## Sheet1
Room by room ventilation heat loss calculation following EN 12831-1:2017 standard calculation method

External temperature			-3

Room name			Livingroom	Hall	Kitchen	Bed 1	Bed 2	Bed 3	Landing	Bathroom	Totals
Room internal temperature		C	20	18	18	18	18	18	18	22		C
Room volume		m3	58.8	17.3	17.3	25.2	20	9.5	15.8	19	182.9	m3
Envelope of the room		m2	54	26.9	27.4	22.3	23.7	13.6	17.2	29.5	214.6	m2
Exhaust air volume flow from the room	qv.exh.i	m3/hr	0	0	0	0	0	0	0	0	0
Effective air change rate		ACH	0.44	0.74	0.75	0.42	0.56	0.68	0.52	0.74		ACH
Effective air change rate		ACH	0.87	1.48	1.50	0.84	1.13	1.36	1.03	1.48		ACH

Effective air volume flow		m3/hr	25.7	12.8	13.0	10.6	11.3	6.5	8.2	14.0	101.9	0.6	ACH
Effective air volume flow		m3/hr	51.3	25.6	26.0	21.2	22.5	12.9	16.3	28.0	203.9	1.1	ACH

6.3.3.3.1 Ventilation heat loss of the building (build) / zone (z) / room (I)

6.3.3.3.1 Building (15)					764	W

6.3.3.3.1 Zone (16)		W	201	91	93	76	80	46	58	119	764	W

6.3.3.3.1 Heated space (17)		W	401	182	186	151	161	92	117	238	1529	W
Density x specific heat	p.cp		0.34	0.34	0.34	0.34	0.34	0.34	0.34	0.34
Internal temperature	O.int.i	C	20	18	18	18	18	18	18	22		C
Outside temperature	O.e	C	-3	-3	-3	-3	-3	-3	-3	-3		C
Rec temperature	O.rec.z	C	0	0	0	0	0	0	0	0		C
Transfer temperature	O.transfer.ij	C	0	0	0	0	0	0	0	0		C
	qv.env.i	m3/h	51.3	25.6	26.0	21.2	22.5	12.9	16.3	28.0		m3/h
	qv.open.i	m3/h	0	0	0	0	0	0	0	0		m3/h
	qv.min.i	m3/h	29.4	8.65	8.65	12.6	10	4.75	0	9.5		m3/h
	n.min.i		0.5	0.5	0.5	0.5	0.5	0.5	0	0.5
	qv.techn.i	m3/h	0	0	0	0	0	0	0	0		m3/h
	qv.sup.i	m3/h	0	0	0	0	0	0	0	0		m3/h
	qv.transfer.ij	m3/h	0	0	0	0	0	0	0	0		m3/h

6.3.3.3.2 External air volume flow into the room (I) through the building envelope	qv,env,i	m3/hr	51.3	25.6	26.0	21.2	22.5	12.9	16.3	28.0		m3/hr
Air volume flow through additional infiltration into the zone (z)	qv,inf-add,z		102	102	102	102	102	102	102	102
External air volume flow into the ventilation zone (z) through the building envelope	qv,env,z		102	102	102	102	102	102	102	102
External air volume flow into the zone (z) through large openings	qv.open.z		0	0	0	0	0	0	0	0
External air volume flow into the room (I) through leakages and ATDs in accordance with Formula (19)	qv,leak+ATD,i		25.7	12.8	13.0	10.6	11.3	6.5	8.2	14.0
Orientation factor (default: 2, B.2.14)	fdir,z		2	2	2	2	2	2	2	2
External air volume flow into the room (I) through large openings	qv,open,i		0	0	0	0	0	0	0	0

Formula 19 (page 35)	qv,leak+ATD,i	m3/hr	25.7	12.8	13.0	10.6	11.3	6.5	8.2	14.0		m3/hr
External air volume flow into the ventilation zone (z) through leakages in accordance with (20)	qv.leak.z	m3/h	102	102	102	102	102	102	102	102		m3/h
Envelope of the room (I)	A.env.i	m2	54	26.9	27.4	22.3	23.7	13.6	17.2	29.5		m2
Envelope of the ventilation zone (z)	A.env.z	m2	214.6	214.6	214.6	214.6	214.6	214.6	214.6	214.6		m2
External air volume flow into the zone (z) through ATDs in accordance with Formula (21)	qv.ATD.z		0	0	0	0	0	0	0	0
Design air volume flow of the ATDs in the ventilation room (I)	qv,ATD,design,i		0	0	0	0	0	0	0	0
Design air volume flow of the ATDs in the ventilation zone (z)	qv,ATD,design,z		0	0	0	0	0	0	0	0

Formula 20 (page 36)	qv.leak.z		102
ATD authority of the ATDs in zone (z) in accordance with Formula (22)	a.ATD.z		0
External air volume flow into the ventilation zone (z) through the building envelope	qv,env,z		102

6.3.3.3.4 External air volume flow into the ventilation zone (z) through the building envelope (page 37)	qv,env,z	m3/hr	102					m3/hr
Exhaust air volume flow from the ventilation zone (z) (Sum of rooms, I)	qv,exh,z	m3/hr	0					m3/hr
Combustion or any other technically required air volume flow into the ventilation zone (z) (Sum of rooms, I)	qv,comb,z	m3/hr	0					m3/hr
Supply air volume flow into the ventilation zone (z) (Sum of rooms, I)	qv,sup,z	m3/hr	0					m3/hr
Air volume flow through additional infiltration into the ventilation zone (z) in accordance with 6.3.3.3.5	qv,inf-add,z	m3/hr	102					m3/hr

6.3.3.3.5 Air volume flow through additional infiltration into the zone (z) (page 37)	qv,inf-add,z	m3/hr	102					m3/hr
Specific air permeability of the envelope at 50pa	qenv50	m3/h/m2	9.5	Corrected upwards as test noted 240 m2 envelope area					m3/h/m2
Envelope of the ventilation zone (z)	Aenvz	m2	214.6					m2
Air volume flow into the ventilation zone (z) through ATDs at a pressure difference of 50 Pa in accordance with Formula (29)	qvATD.50z		0
Volume flow factor	fqv,z		0.05
Adjustment factor taking into account the additional pressure difference due to unbalanced ventilation in accordance with Formula (29)	fe,z		1.00

Formula 29 (fe,z) (page 38)	fe,z		1.00
Adjustment factor for the number of exposed facades	ffac.z		8
Volume flow factor	fqv,z		0.05
Exhaust air volume flow from the ventilation zone (z) (Sum of rooms, I)	qv,exh,z	m3/hr	0					m3/hr
Combustion or any other technically required air volume flow into the ventilation zone (z) (Sum of rooms, I)	qv,comb,z	m3/hr	0					m3/hr
Supply air volume flow into the ventilation zone (z) (Sum of rooms, I)	qv,sup,z	m3/hr	0					m3/hr
Design air volume flow of the ATDs in the ventilation zone (z)	qv,ATD,design,z	m3/hr	0					m3/hr
Specific air permeability of the envelope at 50pa	qenv50	m3/h/m2	9.5					m3/h/m2
Envelope of the ventilation zone (z) This value cancels out in the case of natural ventilation	Aenvz	m2	214.6					m2
Air volume flow into the ventilation zone (z) through ATDs at a pressure difference of 50 Pa	qvATD.50z	m3/hr	0					m3/hr

## Sheet2
Room volume		58.8	m3
Envelope of the room		54	m2
Effective air change rate		0.78	ACH

6.3.3.3.1 Ventilation heat loss of the building (build) / zone (z) / room (I)

6.3.3.3.1 Heated space (17)		359	W
Density x specific heat	p.cp	0.34
Internal temperature	O.int.i	20	C
Outside temperature	O.e	-3	C
Rec temperature	O.rec.z	0	C
Transfer temperature	O.transfer.ij	0	C
External air volume flow into the room (I) through the building envelope	qv.env.i	45.9	m3/h
	qv.min.i	29.4	m3/h

6.3.3.3.2 External air volume flow into the room (I) through the building envelope	qv,env,i	45.9	m3/hr
External air volume flow into the room (I) through leakages and ATDs in accordance with Formula (19)	qv,leak+ATD,i	23.0
Orientation factor (default: 2, B.2.14)	fdir,z	2

Formula 19 (page 35)	qv,leak.i	23.0	m3/hr
External air volume flow into the ventilation zone (z) through leakages in accordance with (20)	qv.leak.z	91	m3/h
Envelope of the room (I)	A.env.i	54	m2
Envelope of the ventilation zone (z)	A.env.z	214	m2		Envelope cancels out!

Formula 20 (page 36)	qv.leak.z	91
External air volume flow into the ventilation zone (z) through the building envelope	qv,env,z	91

6.3.3.3.4 External air volume flow into the ventilation zone (z) through the building envelope (page 37)	qv,env,z	91	m3/hr
Air volume flow through additional infiltration into the ventilation zone (z) in accordance with 6.3.3.3.5	qv,inf-add,z	91	m3/hr

6.3.3.3.5 Air volume flow through additional infiltration into the zone (z) (page 37)	qv,inf-add,z	91	m3/hr
Specific air permeability of the envelope at 50pa	qenv50	8.5	m3/h/m2		2040
Envelope of the ventilation zone (z)	Aenvz	214	m2		Envelope cancels out!
Volume flow factor	fqv,z	0.05
Adjustment factor taking into account the additional pressure difference due to unbalanced ventilation in accordance with Formula (29)	fe,z	1.00