## Outdoor
Time | Model | Compressor | 4Way Valve | Hot Gas Valve | Liquid Valve | EVI Bypass | Operation Mode | Operation Status | Error Code | Capacity ( kW) | Target Frequency1 | Order Frequency1 | Current Frequency1 | High Pressure ( kPa) | Saturated T_Pd | Low Pressure ( kPa) | Saturated T_Ps | Discharge1 ( ℃) | Comp Top1 ( ℃) | Outdoor Temp. ( ℃) | Compressor Current1 (A) | OCT1 ( ℃) | DC Link1 ( ℃) | IPM1 Temp ( ℃) | CondOut Temp. ( ℃) | Suction1 Temp. ( ℃) | Eva In1 ( ℃) | Water In(Tw1) ( ℃) = RWT | Water Out(Tw2) ( ℃) = LWT | Main EEV1 | EVI EEV | EVI SOL EEV | EVI IN ( ℃) | EVI OUT ( ℃) | Fan1 RPM | Base Heater | PHE Heater | Waterout type | Location | Serial Number | Main Micom | Inverter1 Micom | EEPROM Version | Current Limit | Defrost | Fan Calibration | Night Silence | Channel Address | Snow Accumulation Prevention Control | Base Heater(option) | Flow Sensor (lpm) | Gylcol density (kg/m3) | Glycol Sp Ht (J/kg/K) | Glycol mass flow (kg/s) | Heat to glycol (W)
PFD Ref | EHS MONO LOWTEMP | 1 | 2 | 3 | 4 | 5 | AA | [5 empty] | 6 | 7 | BB | 8 | CC | 9 | 10 | 11 | 12 |  |  |  | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M? | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 24
45667.4057 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 8 | 41 | 47 | 41 | 2892.9 | 50 | 372.7 | -15 | 63.8 | 73.1 | -2.4 | 5.7 | 19 | 181 | 47 | -14.8 | -15 | 46 | 45.3 | 48.3 | 168 | 150 | 2000 | 11.6 | 11.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M? | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 28.1 | 1007.7968 | 4091.29 | 0.47198 | 5793.0808
45667.4086 | EHS MONO LOWTEMP | On | On | On | Off | On | Defrost | Heat | 0 | 8 | 22 | 50 | 20 | 1980.9 | 34 | 1578.9 | 26 | 28 | 27.2 | -1.7 | 1.8 | 6 | 180 | 25 | 14.1 | 26.8 | 6.6 | 39.1 | 28.3 | 404 | 0 | 0 | 4.3 | 16.4 | 0 | On | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M? | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 27.7 | 1014.2682 | 4079.1725 | 0.46825 | -20628.9525
45667.4156 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 8 | 49 | 50 | 49 | 2814.5 | 48 | 559 | -5 | 68.1 | 77.5 | -2 | 6.1 | 18 | 177 | 42 | -5 | -5.6 | 40 | 42 | 47.2 | 259 | 90 | 2000 | 12 | 12.1 | 550 | On | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M? | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 27.9 | 1008.9508 | 4089.255 | 0.46916 | 9976.3224