## Global Variables
Global Variable | Value
Room temp (degC) | 20
Radiator derating exponent | 1.33
UFH output W/m^2 | 50
UFH mass (kg/m2) | 15
Rad supply pipe velocity (m/sec) | 1
Pump efficiency | 60%
Annual run hours | 3000

## Pump Energy + Authority
Available head (kPa) | 40 | (lose 10% as headroom)
Peak output (kW) | 9
Flowrate at 45/40C (l/min) | 25.7143
Flowrate at 45/40C (l/hour) | 1542.8571
Flowrate (L/min) | 25.7143
Pressure drop (kPa) | 30
Pump power (W) | 21.0214
Annual Pumping Energy (kWh) | 63.0643
Approx pressure drops @ 45/40
Heat meter dP (kPa) | 1.5
IntaKlean dp (kPa) | 1.5
3-port valve | 1.5 |  | guestimate
Primaries | 7.5 |  | 0.4 L/sec; 0.8 m/sec in 28 mm Cu; 3.7 mbar/metre = 370 Pa/metre. Allow 20 metres for fittings etc? 7.4 kPa
Distribution (index run) | 10
Balance available for control valves | 15 |  | 15 kPa is enough authority to balance
Authority | 0.6

## Heat Pump
Available head (kPa) | 44
Min flowrate (L/hour) | 540
Max flowrate (L/hour) | 1205
Min flowrate (L/min) | 9
Max flowrate (L/min) | 20.0833
Water volume (L) | 2
Max output @ 45/40 -7C (kW) | 7.8
Max output @ 45/40C -2C (kW) | 9
Min output @ 35/30C +12C (kW) | 3.5
Min output @ 35/30C +7C (kW) | 3.2
Min output @ 45/40C -2C (kW) | 2

## Heat Meter
Model | Nominal Flow (m3/hr) | Starting flow (threshold flow) L/hour | Legal dynamic range (min / rated) | Minimum legal flowrate (L/hr) | Rated legal flowrate (L/hour) | Pressure loss at legal flowrate (kPa) | Length (mm) | Thread (-G) | Kv (calculated)
E4 | 3.5 | 7 | 100 | 35 | 3500 | 8 | 260 | G 1 1/4" | 12.3744
Flowrate (L/hour) | Pressure drop (kPa) | Pump power (W) | Annual Pumping Energy (kWh)
750 | 0.36735 | 0.12513 | 0.37538
1250 | 1.0204 | 0.57929 | 1.7379
1500 | 1.4694 | 1.001 | 3.0031

## Emitters
calculated manually - http://www.pressure-drop.online
Link | Emitter | Type | DT50 output (W) | Water Vouume (litres) | Weight (kg) | Area (m^2) | Supply (degC) | Return (degC) | Output (W) | Flowrate (L/min) | Flowrate (m3/hr) | Pipe ID (mm) | Pressure drop Pa/m (15 mm Hep2o) | Reynolds No (15 mm Hep2o) | Velocity (m/sec) (15 mm Hep2o) | Pressure drop Pa/m (10 mm Hep2o) | Reynolds No (10 mm Hep2o) | Velocity (m/sec) (10 mm Hep2o) | Distance (m) [one way] | Pressure Drop (kPa) [supply and return] 15 mm Hep2o | Pressure Drop (kPa) [supply and return] 10 mm Hep2o | Pump power (W) [terminal runs] | Annual Pumping Energy (kWh) [terminal runs]
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1400mm-Type-22-Double-Panel-Premium-Double-Convector-Radiator/p/176251 | Snug | 700x1400 T22 | 2748 | 9.7 | 50.3 |  | 45 | 40 | 962.2967 | 2.7494 | 0.16497 | 7.6384 | 298 | 4922 | 0.426 | 4393 | 8651 | 1.315 | 12 | 7.152 | 105.432 | 0.53584 | 1.6075
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1400mm-Type-22-Double-Panel-Premium-Double-Convector-Radiator/p/176251 | Office | 700x1400 T22 | 3145 | 9.7 | 50.3 |  | 45 | 40 | 1101.3184 | 3.1466 | 0.1888 | 8.1715 | 378 | 5651 | 0.489 | 5607 | 9933 | 1.51 | 12 | 9.072 | 134.568 | 0.77788 | 2.3336
https://www.cityplumbing.co.uk/p/stelrad-halcyon-compact-k2-double-panel-double-convector-radiator-600-mm-x-1800-mm-422618/p/421486?lsft=adtype:pla,productchannel:online,storename:,product_id:421486&gclid=CjwKCAiA3pugBhAwEiwAWFzwdVw2OUL70e5QddJ0NUKGofdIpHDrkM2th3eAt69ZQ2jXt6dXamiuGRoCYuoQAvD_BwE&gclsrc=aw.ds#fo_c=2832&fo_k=1a519e7bf9563a6b02c4dc822e1516f6&fo_s=gplauk | Living Room | 600x1800 T22 | 2748 | 11 | 68 |  | 45 | 40 | 962.2967 | 2.7494 | 0.16497 | 7.6384 | 298 | 4922 | 0.426 | 4393 | 8651 | 1.315 | 10 | 5.96 | 87.86 | 0.44653 | 1.3396
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1600mm-Type-22-Double-Panel-Premium-Double-Convector-Radiator/p/176252 | Hall | 700x1600 T22 | 3141 | 11 | 57.3 |  | 45 | 40 | 1099.9177 | 3.1426 | 0.18856 | 8.1663 | 378 | 5651 | 0.489 | 5607 | 9933 | 1.51 | 6 | 4.536 | 67.284 | 0.38845 | 1.1653
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1400mm-Type-22-Double-Panel-Premium-Double-Convector-Radiator/p/176251 | Kitchen Diner 1 | 700x1400 T22 | 2748 | 9.7 | 50.3 |  | 45 | 40 | 962.2967 | 2.7494 | 0.16497 | 7.6384 | 298 | 4922 | 0.426 | 4393 | 8651 | 1.315 | 15 | 8.94 | 131.79 | 0.6698 | 2.0094
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1600mm-Type-22-Double-Panel-Premium-Double-Convector-Radiator/p/176252 | Kitchen Diner 2 | 700x1600 T22 | 3141 | 11 | 57.3 |  | 45 | 40 | 1099.9177 | 3.1426 | 0.18856 | 8.1663 | 378 | 5651 | 0.489 | 5607 | 9933 | 1.51 | 15 | 11.34 | 168.21 | 0.97112 | 2.9134
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1400mm-Type-22-Double-Panel-Premium-Double-Convector-Radiator/p/176251 | Master bedroom | 700x1400 T22 | 2748 | 9.7 | 50.3 |  | 45 | 40 | 962.2967 | 2.7494 | 0.16497 | 7.6384 | 298 | 4922 | 0.426 | 4393 | 8651 | 1.315 | 12 | 7.152 | 105.432 | 0.53584 | 1.6075
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1400mm-Type-22-Double-Panel-Premium-Double-Convector-Radiator/p/176251 | Guest Bedroom | 700x1400 T22 | 2748 | 9.7 | 50.3 |  | 45 | 40 | 962.2967 | 2.7494 | 0.16497 | 7.6384 | 298 | 4922 | 0.426 | 4393 | 8651 | 1.315 | 12 | 7.152 | 105.432 | 0.53584 | 1.6075
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1400mm-Type-11-Single-Panel-Single-Convector-Radiator/p/176189 | Gym | 700x1400 T11 | 1534 | 5 | 26.6 |  | 45 | 40 | 537.1773 | 1.5348 | 0.092088 | 5.707 | 109 | 2734 | 0.236 | 1955 | 5447 | 0.828 | 20 | 4.36 | 78.2 | 0.18235 | 0.54705
https://www.bestheating.com/milano-nero-straight-black-heated-towel-rail-various-sizes-91121 | Downstairs Bath (towel rail) | Towel 1600x600 | 738 | 6.7 | 9 |  | 45 | 40 | 258.4334 | 0.73838 | 0.044303 | 3.9584 | 26 | 1276 | 0.11 | 250 | 2243 | 0.341 | 3 | 0.156 | 1.5 | 0.0031389 | 0.0094166
| Downstairs Bath (UFH) | Approx 2.5 m^2 |  |  |  | 2.5 | 45 | 22 | 125 | 0.07764 | 0.0046584 | 1.2836 | 4 | 182 | 0.016 | 35 | 320 | 0.049 | 30 | 0.24 | 2.1 | 0.0044429 | 0.013329
https://www.bestheating.com/milano-bow-black-d-bar-central-connection-heated-towel-rail-1269mm-x-600mm-97483 | Upstairs Bath (towel rail) | Towel 1300x600 | 1100 | 10.2 | 27 |  | 45 | 40 | 385.1988 | 1.1006 | 0.066034 | 4.8327 | 41 | 2005 | 0.173 | 921 | 3524 | 0.536 | 3 | 0.246 | 5.526 | 0.0073777 | 0.022133
| Upstairs Bath (UFH) | Approx 4 m^2 |  |  |  | 4 | 45 | 22 | 200 | 0.12422 | 0.0074534 | 1.6236 | 4 | 182 | 0.016 | 35 | 320 | 0.049 | 30 | 0.24 | 2.1 | 0.0071087 | 0.021326
| System Total |  | 26539 | 103.4 | 496.7 | 6.5 |  |  | 9618.4466 | 26.7546 | 1.6053 | [10 empty] | 5.0657 | 15.1971
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1400mm-Type-22-Double-Panel-Premium-Double-Convector-Radiator/p/176251 | Snug | 700x1400 T22 | 2748 | 9.7 | 50.3 |  | 35 | 30 | 434.8586 | 1.2425 | 0.074547 | 5.1348 | 298 | 4922 | 0.426 | 4393 | 8651 | 1.315 | 12 | 7.152 | 105.432 | 0.24214 | 0.72643
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1400mm-Type-22-Double-Panel-Premium-Double-Convector-Radiator/p/176251 | Office | 700x1400 T22 | 3145 | 9.7 | 50.3 |  | 35 | 30 | 497.682 | 1.4219 | 0.085317 | 5.4931 | 378 | 5651 | 0.489 | 5607 | 9933 | 1.51 | 12 | 9.072 | 134.568 | 0.35152 | 1.0546
https://www.cityplumbing.co.uk/p/stelrad-halcyon-compact-k2-double-panel-double-convector-radiator-600-mm-x-1800-mm-422618/p/421486?lsft=adtype:pla,productchannel:online,storename:,product_id:421486&gclid=CjwKCAiA3pugBhAwEiwAWFzwdVw2OUL70e5QddJ0NUKGofdIpHDrkM2th3eAt69ZQ2jXt6dXamiuGRoCYuoQAvD_BwE&gclsrc=aw.ds#fo_c=2832&fo_k=1a519e7bf9563a6b02c4dc822e1516f6&fo_s=gplauk | Living Room | 600x1800 T22 | 2748 | 11 | 68 |  | 35 | 30 | 434.8586 | 1.2425 | 0.074547 | 5.1348 | 298 | 4922 | 0.426 | 4393 | 8651 | 1.315 | 10 | 5.96 | 87.86 | 0.20179 | 0.60536
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1600mm-Type-22-Double-Panel-Premium-Double-Convector-Radiator/p/176252 | Hall | 700x1600 T22 | 3141 | 11 | 57.3 |  | 35 | 30 | 497.049 | 1.4201 | 0.085208 | 5.4897 | 378 | 5651 | 0.489 | 5607 | 9933 | 1.51 | 6 | 4.536 | 67.284 | 0.17554 | 0.52661
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1400mm-Type-22-Double-Panel-Premium-Double-Convector-Radiator/p/176251 | Kitchen Diner 1 | 700x1400 T22 | 2748 | 9.7 | 50.3 |  | 35 | 30 | 434.8586 | 1.2425 | 0.074547 | 5.1348 | 298 | 4922 | 0.426 | 4393 | 8651 | 1.315 | 15 | 8.94 | 131.79 | 0.30268 | 0.90804
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1600mm-Type-22-Double-Panel-Premium-Double-Convector-Radiator/p/176252 | Kitchen Diner 2 | 700x1600 T22 | 3141 | 11 | 57.3 |  | 35 | 30 | 497.049 | 1.4201 | 0.085208 | 5.4897 | 378 | 5651 | 0.489 | 5607 | 9933 | 1.51 | 15 | 11.34 | 168.21 | 0.43884 | 1.3165
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1400mm-Type-22-Double-Panel-Premium-Double-Convector-Radiator/p/176251 | Master bedroom | 700x1400 T22 | 2748 | 9.7 | 50.3 |  | 35 | 30 | 434.8586 | 1.2425 | 0.074547 | 5.1348 | 298 | 4922 | 0.426 | 4393 | 8651 | 1.315 | 12 | 7.152 | 105.432 | 0.24214 | 0.72643
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1400mm-Type-22-Double-Panel-Premium-Double-Convector-Radiator/p/176251 | Guest Bedroom | 700x1400 T22 | 2748 | 9.7 | 50.3 |  | 35 | 30 | 434.8586 | 1.2425 | 0.074547 | 5.1348 | 298 | 4922 | 0.426 | 4393 | 8651 | 1.315 | 12 | 7.152 | 105.432 | 0.24214 | 0.72643
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1400mm-Type-11-Single-Panel-Single-Convector-Radiator/p/176189 | Gym | 700x1400 T11 | 1534 | 5 | 26.6 |  | 35 | 30 | 242.7486 | 0.69357 | 0.041614 | 3.8364 | 109 | 2734 | 0.236 | 1955 | 5447 | 0.828 | 20 | 4.36 | 78.2 | 0.082403 | 0.24721
https://www.bestheating.com/milano-nero-straight-black-heated-towel-rail-various-sizes-91121 | Downstairs Bath (towel rail) | Towel 1600x600 | 738 | 6.7 | 9 |  | 35 | 30 | 116.7852 | 0.33367 | 0.02002 | 2.661 | 26 | 1276 | 0.11 | 250 | 2243 | 0.341 | 3 | 0.156 | 1.5 | 0.0014184 | 0.0042553
| Downstairs Bath (UFH) | Approx 2.5 m^2 |  |  |  | 2.5 | 35 | 22 | 125 | 0.13736 | 0.0082418 | 1.7073 | 4 | 182 | 0.016 | 35 | 320 | 0.049 | 30 | 0.24 | 2.1 | 0.0078606 | 0.023582
https://www.bestheating.com/milano-bow-black-d-bar-central-connection-heated-towel-rail-1269mm-x-600mm-97483 | Upstairs Bath (towel rail) | Towel 1300x600 | 1100 | 10.2 | 27 |  | 35 | 30 | 174.07 | 0.49734 | 0.029841 | 3.2487 | 41 | 2005 | 0.173 | 921 | 3524 | 0.536 | 3 | 0.246 | 5.526 | 0.0033339 | 0.010002
| Upstairs Bath (UFH) | Approx 4 m^2 |  |  |  | 4 | 35 | 22 | 200 | 0.21978 | 0.013187 | 2.1596 | 4 | 182 | 0.016 | 35 | 320 | 0.049 | 30 | 0.24 | 2.1 | 0.012577 | 0.037731
| System Total |  | 26539 | 103.4 | 496.7 | 6.5 |  |  | 4524.6765 | 12.3562 | 0.74137 | [10 empty] | 2.3044 | 6.9132
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1400mm-Type-22-Double-Panel-Premium-Double-Convector-Radiator/p/176251 | Snug | 700x1400 T22 | 2748 | 9.7 | 50.3 |  | 45 | 40 | 962.2967 | 2.7494 | 0.16497 | 7.6384 | 298 | 4922 | 0.426 | 4393 | 8651 | 1.315 | 12 | 7.152 | 105.432 | 0.53584 | 1.6075
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1400mm-Type-22-Double-Panel-Premium-Double-Convector-Radiator/p/176251 | Office | 700x1400 T22 | 3145 | 9.7 | 50.3 |  | 45 | 40 | 1101.3184 | 3.1466 | 0.1888 | 8.1715 | 378 | 5651 | 0.489 | 5607 | 9933 | 1.51 | 12 | 9.072 | 134.568 | 0.77788 | 2.3336
https://www.cityplumbing.co.uk/p/stelrad-halcyon-compact-k2-double-panel-double-convector-radiator-600-mm-x-1800-mm-422618/p/421486?lsft=adtype:pla,productchannel:online,storename:,product_id:421486&gclid=CjwKCAiA3pugBhAwEiwAWFzwdVw2OUL70e5QddJ0NUKGofdIpHDrkM2th3eAt69ZQ2jXt6dXamiuGRoCYuoQAvD_BwE&gclsrc=aw.ds#fo_c=2832&fo_k=1a519e7bf9563a6b02c4dc822e1516f6&fo_s=gplauk | Living Room | 600x1800 T22 | 2748 | 11 | 68 |  | 45 | 40 | 962.2967 | 2.7494 | 0.16497 | 7.6384 | 298 | 4922 | 0.426 | 4393 | 8651 | 1.315 | 10 | 5.96 | 87.86 | 0.44653 | 1.3396
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1600mm-Type-22-Double-Panel-Premium-Double-Convector-Radiator/p/176252 | Hall | 700x1600 T22 | 3141 | 11 | 57.3 |  | 45 | 40 | 1099.9177 | 3.1426 | 0.18856 | 8.1663 | 378 | 5651 | 0.489 | 5607 | 9933 | 1.51 | 6 | 4.536 | 67.284 | 0.38845 | 1.1653
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1400mm-Type-22-Double-Panel-Premium-Double-Convector-Radiator/p/176251 | Kitchen Diner 1 | 700x1400 T22 | 0 | 0 | 50.3 |  | 45 | 40 | 0 | 0 | 0 | 0 | 298 | 4922 | 0.426 | 4393 | 8651 | 1.315 | 15 | 8.94 | 131.79 | 0 | 0
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1600mm-Type-22-Double-Panel-Premium-Double-Convector-Radiator/p/176252 | Kitchen Diner 2 | 700x1600 T22 | 0 | 0 | 57.3 |  | 45 | 40 | 0 | 0 | 0 | 0 | 378 | 5651 | 0.489 | 5607 | 9933 | 1.51 | 15 | 11.34 | 168.21 | 0 | 0
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1400mm-Type-22-Double-Panel-Premium-Double-Convector-Radiator/p/176251 | Master bedroom | 700x1400 T22 | 2748 | 9.7 | 50.3 |  | 45 | 40 | 962.2967 | 2.7494 | 0.16497 | 7.6384 | 298 | 4922 | 0.426 | 4393 | 8651 | 1.315 | 12 | 7.152 | 105.432 | 0.53584 | 1.6075
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1400mm-Type-22-Double-Panel-Premium-Double-Convector-Radiator/p/176251 | Guest Bedroom | 700x1400 T22 | 2748 | 9.7 | 50.3 |  | 45 | 40 | 962.2967 | 2.7494 | 0.16497 | 7.6384 | 298 | 4922 | 0.426 | 4393 | 8651 | 1.315 | 12 | 7.152 | 105.432 | 0.53584 | 1.6075
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1400mm-Type-11-Single-Panel-Single-Convector-Radiator/p/176189 | Gym | 700x1400 T11 | 0 | 0 | 26.6 |  | 45 | 40 | 0 | 0 | 0 | 0 | 109 | 2734 | 0.236 | 1955 | 5447 | 0.828 | 20 | 4.36 | 78.2 | 0 | 0
https://www.bestheating.com/milano-nero-straight-black-heated-towel-rail-various-sizes-91121 | Downstairs Bath (towel rail) | Towel 1600x600 | 0 | 0 | 9 |  | 45 | 40 | 0 | 0 | 0 | 0 | 26 | 1276 | 0.11 | 250 | 2243 | 0.341 | 3 | 0.156 | 1.5 | 0 | 0
| Downstairs Bath (UFH) | Approx 2.5 m^2 | 0 |  |  | 2.5 | 45 | 22 | 0 | 0 | 0 | 0 | 4 | 182 | 0.016 | 35 | 320 | 0.049 | 30 | 0.24 | 2.1 | 0 | 0
https://www.bestheating.com/milano-bow-black-d-bar-central-connection-heated-towel-rail-1269mm-x-600mm-97483 | Upstairs Bath (towel rail) | Towel 1300x600 | 0 | 0 | 27 |  | 45 | 40 | 0 | 0 | 0 | 0 | 41 | 2005 | 0.173 | 921 | 3524 | 0.536 | 3 | 0.246 | 5.526 | 0 | 0
| Upstairs Bath (UFH) | Approx 4 m^2 | 0 |  |  | 4 | 45 | 22 | 0 | 0 | 0 | 0 | 4 | 182 | 0.016 | 35 | 320 | 0.049 | 30 | 0.24 | 2.1 | 0 | 0
| System Total |  | 17278 | 60.8 | 496.7 | 6.5 |  |  | 6050.4228 | 17.2869 | 1.0372 | [10 empty] | 3.2204 | 9.6611
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1400mm-Type-22-Double-Panel-Premium-Double-Convector-Radiator/p/176251 | Snug | 700x1400 T22 | 2748 | 9.7 | 50.3 |  | 35 | 30 | 434.8586 | 1.2425 | 0.074547 | 5.1348 | 298 | 4922 | 0.426 | 4393 | 8651 | 1.315 | 12 | 7.152 | 105.432 | 0.24214 | 0.72643
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1400mm-Type-22-Double-Panel-Premium-Double-Convector-Radiator/p/176251 | Office | 700x1400 T22 | 3145 | 9.7 | 50.3 |  | 35 | 30 | 497.682 | 1.4219 | 0.085317 | 5.4931 | 378 | 5651 | 0.489 | 5607 | 9933 | 1.51 | 12 | 9.072 | 134.568 | 0.35152 | 1.0546
https://www.cityplumbing.co.uk/p/stelrad-halcyon-compact-k2-double-panel-double-convector-radiator-600-mm-x-1800-mm-422618/p/421486?lsft=adtype:pla,productchannel:online,storename:,product_id:421486&gclid=CjwKCAiA3pugBhAwEiwAWFzwdVw2OUL70e5QddJ0NUKGofdIpHDrkM2th3eAt69ZQ2jXt6dXamiuGRoCYuoQAvD_BwE&gclsrc=aw.ds#fo_c=2832&fo_k=1a519e7bf9563a6b02c4dc822e1516f6&fo_s=gplauk | Living Room | 600x1800 T22 | 2748 | 11 | 68 |  | 35 | 30 | 434.8586 | 1.2425 | 0.074547 | 5.1348 | 298 | 4922 | 0.426 | 4393 | 8651 | 1.315 | 10 | 5.96 | 87.86 | 0.20179 | 0.60536
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1600mm-Type-22-Double-Panel-Premium-Double-Convector-Radiator/p/176252 | Hall | 700x1600 T22 | 3141 | 11 | 57.3 |  | 35 | 30 | 497.049 | 1.4201 | 0.085208 | 5.4897 | 378 | 5651 | 0.489 | 5607 | 9933 | 1.51 | 6 | 4.536 | 67.284 | 0.17554 | 0.52661
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1400mm-Type-22-Double-Panel-Premium-Double-Convector-Radiator/p/176251 | Kitchen Diner 1 | 700x1400 T22 | 0 | 0 | 50.3 |  | 35 | 30 | 0 | 0 | 0 | 0 | 298 | 4922 | 0.426 | 4393 | 8651 | 1.315 | 15 | 8.94 | 131.79 | 0 | 0
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1600mm-Type-22-Double-Panel-Premium-Double-Convector-Radiator/p/176252 | Kitchen Diner 2 | 700x1600 T22 | 0 | 0 | 57.3 |  | 35 | 30 | 0 | 0 | 0 | 0 | 378 | 5651 | 0.489 | 5607 | 9933 | 1.51 | 15 | 11.34 | 168.21 | 0 | 0
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1400mm-Type-22-Double-Panel-Premium-Double-Convector-Radiator/p/176251 | Master bedroom | 700x1400 T22 | 2748 | 9.7 | 50.3 |  | 35 | 30 | 434.8586 | 1.2425 | 0.074547 | 5.1348 | 298 | 4922 | 0.426 | 4393 | 8651 | 1.315 | 12 | 7.152 | 105.432 | 0.24214 | 0.72643
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1400mm-Type-22-Double-Panel-Premium-Double-Convector-Radiator/p/176251 | Guest Bedroom | 700x1400 T22 | 2748 | 9.7 | 50.3 |  | 35 | 30 | 434.8586 | 1.2425 | 0.074547 | 5.1348 | 298 | 4922 | 0.426 | 4393 | 8651 | 1.315 | 12 | 7.152 | 105.432 | 0.24214 | 0.72643
https://www.wickes.co.uk/Homeline-by-Stelrad-700-x-1400mm-Type-11-Single-Panel-Single-Convector-Radiator/p/176189 | Gym | 700x1400 T11 | 0 | 0 | 26.6 |  | 35 | 30 | 0 | 0 | 0 | 0 | 109 | 2734 | 0.236 | 1955 | 5447 | 0.828 | 20 | 4.36 | 78.2 | 0 | 0
https://www.bestheating.com/milano-nero-straight-black-heated-towel-rail-various-sizes-91121 | Downstairs Bath (towel rail) | Towel 1600x600 | 0 | 0 | 9 |  | 35 | 30 | 0 | 0 | 0 | 0 | 26 | 1276 | 0.11 | 250 | 2243 | 0.341 | 3 | 0.156 | 1.5 | 0 | 0
| Downstairs Bath (UFH) | Approx 2.5 m^2 | 0 |  |  | 2.5 | 35 | 22 | 0 | 0 | 0 | 0 | 4 | 182 | 0.016 | 35 | 320 | 0.049 | 30 | 0.24 | 2.1 | 0 | 0
https://www.bestheating.com/milano-bow-black-d-bar-central-connection-heated-towel-rail-1269mm-x-600mm-97483 | Upstairs Bath (towel rail) | Towel 1300x600 | 0 | 0 | 27 |  | 35 | 30 | 0 | 0 | 0 | 0 | 41 | 2005 | 0.173 | 921 | 3524 | 0.536 | 3 | 0.246 | 5.526 | 0 | 0
| Upstairs Bath (UFH) | Approx 4 m^2 | 0 |  |  | 4 | 35 | 22 | 0 | 0 | 0 | 0 | 4 | 182 | 0.016 | 35 | 320 | 0.049 | 30 | 0.24 | 2.1 | 0 | 0
| System Total |  | 17278 | 60.8 | 496.7 | 6.5 |  |  | 2734.1652 | 7.8119 | 0.46871 | [10 empty] | 1.4553 | 4.3658

## Pipes
OD (mm) | Material | Wall thickness (mm) | ID (mm) | Roughness k (mm)
10 | Hep2o | 1.7 | 6.6 | 0.007
15 | Hep2o | 1.7 | 11.6 | 0.007
22 | Hep2o | 2.2 | 17.6 | 0.007
10 | Copper | 0.6 | 8.8
15 | Copper | 0.7 | 13.6
22 | Copper | 0.9 | 20.2
28 | Copper | 0.9 | 26.2
35 | Copper | 1.2 | 32.6

## Taps
Fixture | Flowrate (L/min) | Pressure drop Pa/m (15 mm Hep2o) | Reynolds No (15 mm Hep2o) | Velocity (m/sec) (15 mm Hep2o) | Pressure drop Pa/m (10 mm Hep2o) | Reynolds No (10 mm Hep2o) | Velocity (m/sec) (10 mm Hep2o) | 10 or 15 mm? | Run Length (m) | Pressure Drop (bar) | Clearance Volume (L) | Clearance Time (sec)
Downstairs Shower | 12 | 4106 | 21877 | 1.9 |  |  |  | 15 | 2 | 0.08212 | 0.21137 | 1.0568
Downstairs Basin | 6 | 1198 | 10938 | 0.95 | 18262 | 19225 | 2.9 | 10 | 4 | 0.73048 | 0.13685 | 1.3685
Downstairs Toilet | 6 |  |  |  | 18262 | 19225 | 2.9 | 10 | 4 | 0.73048 | 0.13685 | 1.3685
Upstairs Shower | 12 | 4106 | 21877 | 1.9 |  |  |  | 15 | 8 | 0.32848 | 0.84547 | 4.2273
Upstairs Basin | 6 | 1198 | 10938 | 0.95 | 18262 | 19225 | 2.9 | 10 | 4 | 0.73048 | 0.13685 | 1.3685
Upstairs Toilet | 6 |  |  |  | 18262 | 19225 | 2.9 | 10 | 4 | 0.73048 | 0.13685 | 1.3685
Kitchen Tap | 6 | 1198 | 10938 | 0.95 |  |  |  | 15 | 8 | 0.09584 | 0.84547 | 8.4547
Utility Tap | 6 | 1198 | 10938 | 0.95 |  |  |  | 15 | 20 | 0.2396 | 2.1137 | 21.1366
Dishwasher | 3 | 357 | 5469 | 0.47 | 5291 | 9612 | 1.4 | 15 | 15 | 0.05355 | 1.5852 | 31.705
Washing Machine | 3 | 357 | 5469 | 0.47 | 5291 | 9612 | 1.4 | 15 | 20 | 0.0714 | 2.1137 | 42.2733
Upstairs Toilet 2.0 -4.5 | 4.5 |  |  |  | 10885 | 14419 | 2.2 | 10 | 10 | 1.0885 | 0.34212 | 4.5616
Upstairs Toilet 2.0 -6.0 | 6 |  |  |  | 18262 | 19225 | 2.9 | 10 | 10 | 1.8262 | 0.34212 | 3.4212

## Valves
Presetting | Number of Turns | Room temp offset (degK) | Kv | Flowrate (L/min) | Pressure drop (kPa) | Pump power (W) | Annual Pumping Energy (kWh) |  |  | Description 1 | Kv Valve 1 | Description 2 | Kv Valve 2 | Combined Kv | Flowrate (L/min) | Pressure drop (kPa) | Pump power (W) | Annual Pumping Energy (kWh)
[10 empty] | RLV 1.5 turns | 1 | RA-N setting N | 0.73 | 0.58961 | 3.1 | 9.9516 | 0.84066 | 2.522
| 0.25 |  | 0.2 | 3.1 | 86.49 | 7.3062 | 21.9187 | Danfoss RLV 15 | Could probably even use RLV-S here (the | RLV 0.25 turns | 0.2 | RA-N setting 3 | 0.16 | 0.12494 | 0.7 | 11.3006 | 0.21556 | 0.64668
| 0.5 |  | 0.4 | 3.1 | 21.6225 | 1.8266 | 5.4797
| 0.75 |  | 0.5 | 3.1 | 13.8384 | 1.169 | 3.507
| 1 |  | 0.65 | 3.1 | 8.1884 | 0.69172 | 2.0751
| 1.5 |  | 1 | 3.1 | 3.4596 | 0.29225 | 0.87675
| 2 |  | 1.3 | 3.1 | 2.0471 | 0.17293 | 0.51879
| 2.5 |  | 1.7 | 3.1 | 1.1971 | 0.10112 | 0.30337
| 3 |  | 1.9 | 3.1 | 0.95834 | 0.080956 | 0.24287
| 3.5 |  | 2.1 | 3.1 | 0.78449 | 0.06627 | 0.19881
| 4 |  | 2.3 | 3.1 | 0.65399 | 0.055246 | 0.16574
| 0.25 |  | 0.2 | 0.7 | 4.41 | 0.084121 | 0.25236
| 0.5 |  | 0.4 | 0.7 | 1.1025 | 0.02103 | 0.063091
| 0.75 |  | 0.5 | 0.7 | 0.7056 | 0.013459 | 0.040378
| 1 |  | 0.65 | 0.7 | 0.41751 | 0.0079641 | 0.023892
| 1.5 |  | 1 | 0.7 | 0.1764 | 0.0033648 | 0.010094
| 2.5 |  | 1.7 | 0.7 | 0.061038 | 0.0011643 | 0.0034929
| 3 |  | 1.9 | 0.7 | 0.048864 | 0.00093209 | 0.0027963
| 3.5 |  | 2.1 | 0.7 | 0.04 | 0.000763 | 0.002289
| 4 |  | 2.3 | 0.7 | 0.033346 | 0.00063607 | 0.0019082
1 |  | 2 | 0.04 | 3.1 | 2162.25 | 182.6561 | 547.9682 | Danfoss RA-N | Kv values at Xp=2K - this means that the valve is completely closed when room temperature rises 2K above current room temperature
2 |  | 2 | 0.09 | 3.1 | 427.1111 | 36.0802 | 108.2406 |  | Kvs is the max possible valve opening (without an actuator head / with a very high temperature difference)
3 |  | 2 | 0.16 | 3.1 | 135.1406 | 11.416 | 34.248
4 |  | 2 | 0.25 | 3.1 | 55.3536 | 4.676 | 14.028
5 |  | 2 | 0.36 | 3.1 | 26.6944 | 2.255 | 6.765
6 |  | 2 | 0.43 | 3.1 | 18.7107 | 1.5806 | 4.7417
7 |  | 2 | 0.52 | 3.1 | 12.7944 | 1.0808 | 3.2424
N |  | 2 | 0.73 | 3.1 | 6.492 | 0.54841 | 1.6452
1 |  | 2 | 0.04 | 0.7 | 110.25 | 2.103 | 6.3091
2 |  | 2 | 0.09 | 0.7 | 21.7778 | 0.41541 | 1.2462
3 |  | 2 | 0.16 | 0.7 | 6.8906 | 0.13144 | 0.39432
4 |  | 2 | 0.25 | 0.7 | 2.8224 | 0.053837 | 0.16151
5 |  | 2 | 0.36 | 0.7 | 1.3611 | 0.025963 | 0.07789
6 |  | 2 | 0.43 | 0.7 | 0.95403 | 0.018198 | 0.054594
7 |  | 2 | 0.52 | 0.7 | 0.65237 | 0.012444 | 0.037332
N |  | 2 | 0.73 | 0.7 | 0.33102 | 0.0063142 | 0.018943
[8 empty] | Danfoss RAS-C2 TRV | Liquid filled (22 minute reaction time) actuator TRV | Description 1 | Kv Valve 1 | Description 2 | Kv Valve 2 | Combined Kv | Flowrate (L/min) | Pressure drop (kPa) | Pump power (W) | Annual Pumping Energy (kWh)
|  | 0.5 | 0.13 | 3.1 | 204.7101 | 17.2929 | 51.8786 |  |  | RLV 4 turns | 2.3 | RAS-C2 at 2K | 0.5 | 0.48859 | 3.1 | 14.4924 | 1.2242 | 3.6727
|  | 1 | 0.27 | 3.1 | 47.4568 | 4.0089 | 12.0267 |  | Touch small for big rad and too big for towel rail but works ok for gym rad | RLV 0.25 turns | 0.2 | RAS-C2 at 2K | 0.5 | 0.1857 | 1.1 | 12.6324 | 0.37866 | 1.136
|  | 2 | 0.5 | 3.1 | 13.8384 | 1.169 | 3.507
|  | 3 | 0.64 | 3.1 | 8.4463 | 0.7135 | 2.1405
|  | 0.5 | 0.13 | 2.7 | 155.2899 | 11.4255 | 34.2764
|  | 1 | 0.27 | 2.7 | 36 | 2.6487 | 7.9461
|  | 2 | 0.5 | 2.7 | 10.4976 | 0.77236 | 2.3171
|  | 3 | 0.64 | 2.7 | 6.4072 | 0.47141 | 1.4142
|  | 0.5 | 0.13 | 1.5 | 47.929 | 1.9591 | 5.8773
|  | 1 | 0.27 | 1.5 | 11.1111 | 0.45417 | 1.3625
|  | 2 | 0.5 | 1.5 | 3.24 | 0.13244 | 0.39731
|  | 3 | 0.64 | 1.5 | 1.9775 | 0.080832 | 0.2425
|  | 0.5 | 0.13 | 1.1 | 25.7751 | 0.77261 | 2.3178
|  | 1 | 0.27 | 1.1 | 5.9753 | 0.17911 | 0.53733
|  | 2 | 0.5 | 1.1 | 1.7424 | 0.052228 | 0.15669
|  | 3 | 0.64 | 1.1 | 1.0635 | 0.031878 | 0.095633
|  | 0.5 | 0.13 | 0.7 | 10.4379 | 0.1991 | 0.59731
|  | 1 | 0.27 | 0.7 | 2.4198 | 0.046157 | 0.13847
|  | 2 | 0.5 | 0.7 | 0.7056 | 0.013459 | 0.040378
|  | 3 | 0.64 | 0.7 | 0.43066 | 0.0082149 | 0.024645

## Runtime
Scenario | 45/40C @ -2C All emitters | 35/30C @ +12C All emitters | 45/40C @ -2C Kitchen dinner gym bathrooms off | 35/30C @ +12C Kitchen dinner gym bathrooms off
System volume (litres) | 103.4 | 103.4 | 60.8 | 60.8
System supply temperature (dgeC) | 45 | 35 | 45 | 35
System return temperature (degC) | 40 | 30 | 40 | 30
System dt50 Output (W) | 26539 | 26539 | 17278 | 17278
System derated output (W) | 9618.4466 | 4524.6765 | 6050.4228 | 2734.1652
Heat pump miniumum input (W) | 2000 | 3500 | 2000 | 3500
Minimum "net" heat input (W) | -7618.4466 | -1024.6765 | -4050.4228 | 765.8348
Must cycle? | NO | NO | NO | YES
Time per degC increase in water temp (mins) | -0.95006 | -7.0637 | -1.0508 | 5.5573
Additional volume (litres | 100 | 100 | 100 | 100
Time per degC increase in water temp (mins) | -1.8689 | -13.8951 | -2.779 | 14.6977