## BS12831 Example
Room name			Hobby room	Living room	Kitchen	Bed 1	Bed 2	Bed 3	Bathroom	Entrance hall	Hall	WC
Room internal volume	Vi	m3	29	92.3	23.8	27.3	25.6	26.3	11.5	19.6	13.3	4.1	272.8
External temperature	Oe	C	-10	-10	-10	-10	-10	-10	-10	-10
Internal temperature	Oint,i	C	20	20	20	20	20	20	24	20	20	20
Temperature difference	Oint,i-Oe	C	30	30	30	30	30	30	34	30	30	30
Exposed openings		p.u	1	2	1	1	1	2	1	1	0	0
Air exchange rate	n50	h-1	6	6	6	6	6	6	6	6
shielding factor	e	p.u	0.02	0.03	0.02	0.02	0.02	0.03	0.02	0.02	0	0
height correction factor		p.u	1	1	1	1	1	1	1	1
Infiltration air flow rate	Vinf,i	m3/h	7.0	33.2	5.7	6.6	6.1	9.5	2.8	4.7	0.0	0.0
Extracted air	Vex,i	m3/h	0	0	120	0	0	0	30	0	0	30	180
Supplied air	VSU,i	m3/h	0	0	0	0	0	0	0	0
Temperature of supplied air	OSU	C
Reduction factor	fV,i
Air coming from adjacent rooms					104				22			27
Reduction factor	fV,i				0.00				0.12			0.00
Surplus of exhaust air total building		m3/h	180	180	180	180	180	180	180	180	180	180
Surplus of exhaust air room by room		m3/h	19	61	16	18	17	17	8	13	9	3
Total corrected ventilation flow rate		m3/h	26.1	94.1	21.4	24.6	23.0	26.8	13.0	17.6	8.8	2.7
Design ventilation heat loss coef		W/K	8.9	32.0	7.3	8.4	7.8	9.1	4.4	6.0	3.0	0.9
Design ventilation heat loss		W	266	960	218	251	235	274	150	180	90	28	2651

## Midterrace
Room name			Living room	Hall	Kitchen	Bed 1	Bed 2	Bed 3	Landing	Bathroom
Room internal volume	Vi	m3	58.8	17.3	17.3	25.2	20	9.5	15.8	19	182.9
External temperature	Oe	C	-3	-3	-3	-3	-3	-3	-3	-3
Internal temperature	Oint,i	C	20	20	20	20	20	20	20	20
Temperature difference	Oint,i-Oe	C	23	23	23	23	23	23	23	23
Exposed openings		p.u	1	1	1	1	1	1	1	1
Air exchange rate	n50	h-1	10.13	10.13	10.13	10.13	10.13	10.13	10.13	10.13
shielding factor	e	p.u	0.02	0.02	0.02	0.02	0.02	0.02	0.02	0.02
height correction factor		p.u	1	1	1	1	1	1	1	1
Infiltration air flow rate	Vinf,i	m3/h	23.8	7.0	7.0	10.2	8.1	3.8	6.4	7.7	74.11108	0.41
Extracted air	Vex,i	m3/h	0	0	108	0	0	0	0	54	162	0.89
Supplied air	VSU,i	m3/h	0	0	0	0	0	0	0	0
Temperature of supplied air	OSU	C
Reduction factor	fV,i
Air coming from adjacent rooms					93					37
Reduction factor	fV,i				0.00					0.00
Surplus of exhaust air total building		m3/h	162	162	162	162	162	162	162	162
Surplus of exhaust air room by room		m3/h	52	15	15	22	18	8	14	17
Total corrected ventilation flow rate		m3/h	75.9	22.3	22.3	32.5	25.8	12.3	20.4	24.5
Design ventilation heat loss coef		W/K	25.8	7.6	7.6	11.1	8.8	4.2	6.9	8.3
Design ventilation heat loss		W	594	175	175	254	202	96	160	192	1846

			Alternative simplified method based on a single whole house ventilation rate (measured average and part F minimum whole house ventilation rate)
Assumed ACH			0.6	0.6	0.6	0.6	0.6	0.6	0.6	0.6
Room by room heat loss			276	81	81	118	94	45	74	89	858

			Alternative simplified method based on a single whole house ventilation rate (equivalent to minimum continuous part F extraction rate + base infiltration 0.41 + 0.41)
Assumed ACH			0.82	0.82	0.82	0.82	0.82	0.82	0.82	0.82
Room by room heat loss			377	111	111	162	128	61	101	122	1173

			Alternative simplified method based on a single whole house ventilation rate (full intermittent extraction rate, part F)
Assumed ACH			1.3	1.3	1.3	1.3	1.3	1.3	1.3	1.3
Room by room heat loss			598	176	176	256	203	97	161	193	1859