## Sheet1
Water temp ex ASHP (degC) | T1, t1 | 45 | Assumes radiator in temp = ASHP exit temp, measured
Water flow ex ASHP (kg/s) | M | 0.5 | Measured
Radiator OHTC (W/m2/degC) | U | 50 | Previous tests
Radiator area (m2) | A | 1.84 | Measured
Room temperature (degC) | Tr | 21 | Target (assumed fixed)
Radiator flow (kg/s) | m | 0.2 | 0.25 | 0.3 | 0.35 | 0.4 | 0.45 | 0.5 | Different scenarios between 40 and 100% of primary circuit flow
Radiator flow (litre/min) | v | 11.7647 | 14.7059 | 17.6471 | 20.5882 | 23.5294 | 26.4706 | 29.4118 | Glycol density = 1020kg/m3
Trial radiator exit temp (degC) | t2 | 42.3846 | 42.8849 | 43.2245 | 43.4701 | 43.6561 | 43.8017 | 43.9189
Average radiator temp (degC) | tave | 43.6923 | 43.9424 | 44.1122 | 44.2351 | 44.328 | 44.4009 | 44.4594 | (t1 + t2) / 2
Calc radiator duty (W) | Q | 2087.6929 | 2110.7046 | 2126.3266 | 2137.6261 | 2146.179 | 2152.8782 | 2158.2675 | From Q = U * A * (Tave - Tr)
Glycol Sp Ht (kJ/kg/degC) | Cp | 3.9913 | 3.9917 | 3.992 | 3.9922 | 3.9924 | 3.9925 | 3.9926 | 20% glycol solution at Tave
Calc radiator temp drop (degC) | Dt | 2.6153 | 2.1151 | 1.7755 | 1.5299 | 1.3439 | 1.1983 | 1.0811 | From Dt = Q / m / Cp
Error |  | 5.2654e-05 | 2.5975e-05 | 1.4334e-05 | 8.5385e-06 | 5.3726e-06 | 3.5195e-06 | 2.3755e-06 | Use Excel Goal Seek to reset trial t2 so U * A * (Tr -Tave) = m * Cp * Dt
Calc ASHP inlet temp (degC) | T2 | 43.9539 | 43.9424 | 43.9347 | 43.9291 | 43.9249 | 43.9215 | 43.9189 | Blend radiator outlet flow and temp with buffer tank bypass flow (= M - m) and inlet temp t1
Glycol Sp Ht (kJ/kg/degC) | Cp | 3.9926 | 3.9926 | 3.9926 | 3.9926 | 3.9926 | 3.9926 | 3.9926 | 20% glycol solution at average of T1 and T2
Radiator duty imbalance |  | -3.27% | -2.204% | -1.48% | -0.9564% | -0.5601% | -0.2497% | 0% | Reduction in radiator duty compared with m = M case (0.5kg/s)
ASHP electrical power reqt | Php | 535.3059 | 541.2063 | 545.212 | 548.1093 | 550.3023 | 552.0201 | 553.4019 | From Q / CoP where CoP = 3.90 (Samsung data for 45degC exit temp, 7degC ambient)
Est'd pump head (kPa) | H | 15.7079 | 23.2928 | 32.2548 | 42.594 | 54.3104 | 67.4039 | 81.8746 | Curve fit of estimated system curve (H = 0.0796v^2 + 0.4718v -0.86)
CH pump hydraulic power (W) | Phyd | 3.08 | 5.709 | 9.4867 | 14.6156 | 21.2982 | 29.737 | 40.1346 | From P = H * v / 60 (s/min)
Pump shaft power (W) | Pch | 5.1333 | 9.515 | 15.8112 | 24.3593 | 35.497 | 49.5617 | 66.891 | Assuming h = 0.6
Total power (W) | Poa | 540.4392 | 550.7213 | 561.0231 | 572.4686 | 585.7993 | 601.5818 | 620.2929 | Php + Pch
Net power saving |  | 12.87% | 11.22% | 9.555% | 7.71% | 5.561% | 3.017% | 0% | Reduction in overall power compared with m = M case (0.5kg/s)