## NASA Database
Mess # | Type E/V/L/S | NASA .ptc? | SNET? | NASA mon? | Content ("xx" = SNET Field) | Protocol ID | Sign? | Div | F1/F2 Freq (s) | Value (V=variable) | Comments
0025 | E | Y |  |  | Multi tenant no. | ENUM_AD_MULTI_TENANT_NO | N |  | -
0202 | V | Y |  |  | "Error code" | VAR_ad_error_code1 | Y |  | 10 | V | Per listing in User Manual (0 = no error)
0207 | V | Y |  |  | No. of Indoor Units | VAR_ad_install_number_indoor | N |  | 40 | 1
0211 | V | Y |  |  | No. of MCUs (microcontroller units) | VAR_ad_install_number_mcu | N |  | -
0400 | L | Y |  |  | Default address | LVAR_AD_ADDRESS_DEFAULT_MAIN | N |  | -
0401 | L | Y |  |  | Main address | LVAR_AD_ADDRESS_MAIN | N |  | -
0402 | L | Y |  |  | RMC address | LVAR_ad_address_rmc | N |  | 160 | 0x00A00000
0408 | L | Y |  |  | Setup address | LVAR_AD_ADDRESS_SETUP | N |  | -
0409 | L | Y |  |  | Remote level | LVAR_ad_install_level_all | N |  | 160 | 0
040A | L | Y |  |  | Operating power | LVAR_ad_install_level_operation_power | N |  | 160 | 0
040B | L | Y |  |  | Operating mode | LVAR_ad_install_level_operation_mode | N |  | 160 | 0
040C | L | Y |  |  | Fan mode | LVAR_ad_install_level_fan_mode | N |  | 160 | 0
040D | L | Y |  |  | Fan direction | LVAR_ad_install_level_fan_direction | N |  | 160 | 0
040E | L | Y |  |  | Target temperature | LVAR_ad_install_level_temp_target | N |  | 160 | 0
040F | L | Y |  |  | Alternative mode value | LVAR_ad_install_level_keep_individual_control | N |  | -
0410 | L | Y |  |  | Operating mode limit | LVAR_ad_install_level_operation_mode_only | N |  | 10 | 0
0411 | L | Y |  |  | Cooling max temperature | LVAR_AD_INSTALL_LEVEL_COOL_MODE_UPPER | N |  | 160 | 0x012C0000 | MSB = 300 (30degC)
0412 | L | Y |  |  | Cooling min temperature | LVAR_AD_INSTALL_LEVEL_COOL_MODE_LOWER | N |  | 160 | 0x00320000 | MSB = 50 (5degC)
0413 | L | Y |  |  | Heating max temperature | LVAR_AD_INSTALL_LEVEL_HEAT_MODE_UPPER | N |  | 160 | 0x02260000 | MSB = 550 (55degC)
0414 | L | Y |  |  | Heating min temperature | LVAR_AD_INSTALL_LEVEL_HEAT_MODE_LOWER | N |  | 160 | 0x00960000 | MSB = 150 (15degC)
0415 | L | Y |  |  | Contact control | LVAR_ad_install_level_contact_control | N |  | 160 | 0x00500000 | MSB = 80 (8degC)
0416 | L | Y |  |  | Key operating input | LVAR_ad_install_level_key_operation_input | N |  | 160 | 0
041B | L |  |  |  | ? |  | N |  | 10 | 0x0020FFFF
0448 | L | Y |  |  | MCU port setup | LVAR_AD_MCU_PORT_SETUP | N |  | -
0600 | S | Y | Y |  | "Product Option" | STR_ad_option_basic | N |  | SNET | 0x12300000000000000000
0601 | S | Y |  |  | Install option | STR_ad_option_install | N |  | SNET | 0x20010000000000000000
0602 | S | Y |  |  | Install option 2 | STR_ad_option_install_2 | N |  | SNET | 0x50000000000000000000
0603 | S | Y |  |  | Cycle option | STR_ad_option_cycle | N |  | SNET | 0x30000000000000000000
0605 | S | Y | Y |  | "Location" (user input) | STR_ad_info_equip_position | N |  | -
0607 | S | Y | Y |  | "Serial Number" | STR_ad_id_serial_number | N |  | -
0608 | S | Y | Y | Y | "Main Micom" | STR_ad_dbcode_micom_main | N |  | 40 - 135 | V | 0x9102450A220706000000 (outdoor PCB) or 0x9102501A240624090909 (indoor PCB)
060C | S | Y | Y | Y | "EEPROM Version" | STR_ad_dbcode_eeprom | N |  | 135 | 0x8207081A220622
061A | S | Y | Y |  | "Model" (series) | STR_AD_PRODUCT_MODEL_NAME | N |  | SNET | 0x11454853204D4F4E4F204C4F5754454D5000
061C | S | Y |  |  | Wifi Kit MAC address | STR_AD_PRODUCT_MAC_ADDRESS | N |  | -
061F | S | Y |  |  | Model name | STR_AD_ID_MODEL_NAME | N |  | -
0623 | S |  |  |  | ? |  | N |  | 160 | 0x91000000000000090909
200F | E | Y |  |  | Network position layer | ENUM_NM_network_positinon_layer | N |  | - |  | 0 = control layer, 1 = set layer
2010 | E | Y |  |  | Network tracking state | ENUM_NM_network_tracking_state | N |  | -
22F7 | V |  |  |  | ? |  | N |  | 40 | V
22F9 | V |  |  |  | ? |  | N |  | 40 | 0
22FA | V |  |  |  | ? |  | N |  | 90 | 0 or 1
22FB | V |  |  |  | ? |  | N |  | 40 | V
22FC | V |  |  |  | ? |  | N |  | 90 | V
22FD | V |  |  |  | ? |  | N |  | 40 | 0 or 1
22FE | V |  |  |  | ? |  | N |  | 90 | V | 7, 9 or 11
22FF | V |  |  |  | ? |  | N |  | 70 -100 | 3
2400 | L |  |  |  | ? |  | N |  | 20 - 120 | 0xFF02FFFF
2401 | L |  |  |  | ? |  | N |  | 20 - 100 | 0x00010000
24FB | L |  |  |  | ? |  | N |  | 90 | 0
24FC | L |  |  |  | Peak power supply voltage (?) |  | N |  | 160 | V | Possibly RMS x sqrt(2)
4000 | E | Y | Y |  | "Zone 1 Normal Power" | ENUM_in_operation_power | N |  | 3 - 160 | 1 | 0 = off, 1 = on
4001 | E | Y |  |  | Indoor Unit control mode | ENUM_in_operation_mode | N |  | 3 -160 | 4 | See option list in NASA.ptc
4002 | E | Y | Y |  | "Operation Mode" | ENUM_in_operation_mode_real | N |  | 3 -160 | 4 | See option list in NASA.ptc
4003 | E | Y |  |  | Ventilation status | ENUM_IN_OPERATION_VENT_POWER | N |  | - |  | 0 = off, 1 = on
4004 | E | Y |  |  | Ventilation mode | ENUM_IN_OPERATION_VENT_MODE | N |  | - |  | See option list in NASA.ptc
4006 | E | Y |  |  | Fan setting | ENUM_IN_FAN_MODE | N |  | 160 | 3 | See option list in NASA.ptc
4007 | E | Y |  |  | Fan mode | ENUM_in_fan_mode_real | N |  | - |  | See option list in NASA.ptc
4008 | E | Y |  |  | Current Indoor Unit air flow setting | ENUM_IN_FAN_VENT_MODE | N |  | - |  | See option list in NASA.ptc
400F | E |  |  |  | ? |  | N |  | 160 | 0
4010 | E |  |  |  | ? |  | N |  | 160 | 0
4011 | E | Y |  |  | Up/down louvre control | ENUM_IN_LOUVER_HL_SWING | N |  | - |  | 0 = off, 1 = on
4012 | E | Y |  |  | Up/down louvre setting | ENUM_in_louver_hl_part_swing | N |  | - |  | See option list in NASA.ptc
4015 | E |  |  |  | ? |  | N |  | 160 | 1
4019 | E |  |  |  | ? |  | N |  | 160 | 0
401B | E |  |  |  | ? |  | N |  | 160 | 1
4023 | E |  |  |  | ? |  | N |  | 160 | 0
4024 | E |  |  |  | ? |  | N |  | 160 | 1
4027 | E |  |  |  | ? |  | N |  | -
4028 | E | Y | Y |  | "Thermo" (cylstat status) | ENUM_IN_STATE_THERMO | N |  | 3 - 160 | 0 or 1 | 0 = no demand, 1 = demand
4029 | E |  |  |  | ? |  | N |  | 160 | 0
402A | E |  |  |  | Duplicate of 4028? |  | N |  | 160 | 0 or 1
402B | E |  |  |  | ? |  | N |  | 160 | 0
402D | E |  |  |  | ? |  | N |  | 160 | 0
402E | E | Y |  |  | Defrost status | ENUM_in_state_defrost_mode | N |  | 160 | 0 | 0 = clear, 1 = initialise, 2 = run
402F | E | Y |  |  | MTFC (?) | ENUM_IN_MTFC | N |  | -
4031 | E |  |  |  | ? |  | N |  | 160 | 0
4035 | E |  |  |  | ? |  | N |  | 3 - 160 | 0
4038 | E | Y |  |  | Indoor air humidity (%) | ENUM_IN_STATE_HUMIDITY_PERCENT | N |  | -
4043 | E |  |  |  | Purify (?) |  | N |  | 160 | 0 | 0 = off, 1 = on (MIM-B19N manual)
4046 | E | Y | Y | Y | "Silence Mode" | ENUM_IN_SILENCE | N |  | 160 | 0 | 0 = off, 1 = on
4047 | E |  |  |  | ? |  | N |  | 160 | 0 or 1
4048 | E |  |  |  | ? |  | N |  | 160 | 0
404F | E | Y |  |  | SH plus 16 state (?) | ENUM_IN_STATE_SH_PLUS16 | N |  | 160 | -1
4051 | E |  |  |  | ? |  | N |  | 3 - 160 | 0
4059 | E |  |  |  | ? |  | N |  | 3 - 160 | 1
405F | E |  |  |  | ? |  | N |  | 160 | 0
4060 | E | Y |  |  | Alternative mode status | ENUM_IN_ALTERNATIVE_MODE | N |  | 160 | 0 | 0 = off, 9 = on
4065 | E | Y | Y | Y | "DHW power" (DHW heating on/off) | ENUM_IN_WATER_HEATER_POWER | N |  | 3 - 160 | V | 0 = off, 1 = on
4066 | E | Y | Y | Y | "DHW Mode" | ENUM_IN_WATER_HEATER_MODE | N |  | 3 - 160 | V | 0 = eco, 1 = std, 2 = power, 3 = force
4067 | E | Y | Y | Y | "3Way Valve" (position) | ENUM_IN_3WAY_VALVE | N |  | 160 | V | 0 = room, 1 = DHW tank
4068 | E | Y | Y |  | "Solar Pump" (demand) | ENUM_IN_SOLAR_PUMP | N |  | 160 | V | 0 = off, 1 = on
4069 | E | Y | Y |  | "Thermostat1" (ext'l roomstat demand) | ENUM_IN_THERMOSTAT1 | N |  | 160 | V | 0 = off, 1 = cool, 2 = heat
406A | E | Y | Y |  | "Thermostat2" (ext'l roomstat demand) | ENUM_IN_THERMOSTAT2 | N |  | 160 | 0 | 0 = off, 1 = cool, 2 = heat
406B | E |  |  |  | ? |  | N |  | 160 | 0
406C | E | Y | Y | Y | "Backup Heater" (demand) | ENUM_IN_BACKUP_HEATER | N |  | 160 | 0 | 0 = Off, 1 = step 1, 2 = step 2
406D | E | Y | Y | Y | "Outing Operation" | ENUM_IN_OUTING_MODE | N |  | 160 | 0 | 0 = off, 1 = on
406E | E | Y |  |  | Quiet mode | ENUM_IN_QUIET_MODE | N |  | -
406F | E | Y | Y |  | "Ref Temp" (select basis) | ENUM_IN_REFERENCE_EHS_TEMP | N |  | 160 | 1 | 0 = room, 1 = LWT
4070 | E | Y |  |  | Discharge temp enable | ENUM_IN_DISCHAGE_TEMP_CONTROL | N |  | 160 | 0 | 0 = off, 1 = on
4073 | E |  |  |  | ? |  | N |  | 160 | 0
4074 | E |  |  |  | ? |  | N |  | 160 | 0
4076 | E | Y |  |  | Roomstat select | ENUM_IN_ROOM_TEMP_SENSOR | N |  | - |  | 0 = external, 2 = wired remote control
4077 | E |  |  |  | ? |  | N |  | 160 | 0
407B | E |  |  |  | ? |  | N |  | 160 | 0
407D | E |  |  |  | ? |  | N |  | 160 | 0
407E | E | Y |  |  | Left/right louvre control | ENUM_IN_LOUVER_LR_SWING | N |  | 160 | 0 | 0 = off, 1 = on
4085 | E |  |  |  | ? |  | N |  | 160 | 0
4086 | E |  |  |  | ? |  | N |  | 160 | 0
4087 | E | Y | Y | Y | "Boost Heater" (immersion heater status) | ENUM_IN_BOOSTER_HEATER | N |  | 160 | 0 or 1 | 0 = off, 1 = on
4089 | E | Y | Y |  | "Water Pump" (circ'n pump status) | ENUM_IN_STATE_WATER_PUMP | N |  | 160 | 0 or 1 | 0 = off, 1 = on
408A | E | Y |  |  | 2 way valve position | ENUM_IN_2WAY_VALVE | N |  | 160 | 0 or 2
4093 | E | Y | Y | Y | FSV 2041 (heating WL selection) | ENUM_IN_FSV_2041 | N |  | - |  | 1 = WL1, 2= WL2
4094 | E | Y | Y | Y | FSV 2081 (cooling WL selection) | ENUM_IN_FSV_2081 | N |  | - |  | 1 = WL1, 2= WL2
4095 | E | Y | Y | Y | FSV 2091 (WL1 circ'n pump control) | ENUM_IN_FSV_2091 | N |  | 160 | V | Values 0 - 4 (see user manual)
4096 | E | Y | Y | Y | FSV 2092 (WL2 circ'n pump control) | ENUM_IN_FSV_2092 | N |  | 160 | V | Values 0 - 4 (see user manual)
4097 | E | Y | Y | Y | FSV 3011 (enable DHW) | ENUM_IN_FSV_3011 | N |  | 160 | V | 0 = not use, 1 = @thermo on, 2 = @thermo off
4098 | E | Y | Y | Y | FSV 3031 (enable immersion heater) | ENUM_IN_FSV_3031 | N |  | - |  | 0 = disable, 1 = enable
4099 | E | Y | Y | Y | FSV 3041 (enable disinfection) | ENUM_IN_FSV_3041 | N |  | 160 | 0 or 1 | 0 = disable, 1 = enable
409A | E | Y | Y | Y | FSV 3042 (disinfection day) | ENUM_IN_FSV_3042 | N |  | 160 | V | Day of week (0 - 6) or every day (7)
409B | E | Y | Y | Y | FSV 3051 (enable forced DHW) | ENUM_IN_FSV_3051 | N |  | - |  | 0 = disable, 1 = enable
409C | E | Y | Y | Y | FSV 3061 (simultanEus use of HP and PV) | ENUM_IN_FSV_3061 | N |  | 160 | V | 0 = disable, 1 = roomstat, 2 = cylstat
409D | E | Y | Y | Y | FSV 3071 (3 way valve default dir'n) | ENUM_IN_FSV_3071 | N |  | - |  | 0 = room, 1 = DHW tank
409E | E | Y | Y | Y | FSV 4011 (DHW/CH priority) | ENUM_IN_FSV_4011 | N |  | - |  | 0 = DHW, 1 = CH
409F | E | Y | Y | Y | FSV 4021 (enable backup heater) | ENUM_IN_FSV_4021 | N |  | - |  | 0 = disable, 1 = 2 step, 2 = 1 step
40A0 | E | Y | Y | Y | FSV 4022 (backup/immersion heater priority) | ENUM_IN_FSV_4022 | N |  | - |  | 0 = both, 1 = backup, 2 = immersion
40A1 | E | Y | Y | Y | FSV 4023 (enable cold weather compensation) | ENUM_IN_FSV_4023 | N |  | - |  | 0 = disable, 1 = enable
40A2 | E | Y | Y | Y | FSV 4031 (enable backup boiler) | ENUM_IN_FSV_4031 | N |  | - |  | 0 = disable, 1 = enable
40A3 | E | Y | Y | Y | FSV 4032 (boiler priority) | ENUM_IN_FSV_4032 | N |  | - |  | 0 = off, 1 = use
40A4 | E | Y | Y | Y | FSV 5041 (enable power peak control) | ENUM_IN_FSV_5041 | N |  | - |  | 0 = disable, 1 = enable
40A5 | E | Y | Y | Y | FSV 5042 (select devices to disable) | ENUM_IN_FSV_5042 | N |  | - |  | 0 = BUH, 1 = BUH/BSH, 2 = Compr/BUH, 3 = all
40A6 | E | Y | Y | Y | FSV 5043 (select voltage switch) | ENUM_IN_FSV_5043 | N |  | - |  | 0 = on low voltage, 1 = on high voltage
40A7 | E | Y | Y | Y | FSV 5051 (enable frequency ratio control) | ENUM_IN_FSV_5051 | N |  | - |  | 0 = disable, 1 = enable
40B4 | E | Y | Y |  | FSV 5061 (CH/DHW supply ratio) | ENUM_IN_FSV_5061 | N |  | - |  | Values 1 - 7 (see user manual)
40B5 | E |  |  |  | ? |  | N |  | 160 | 0
40BB | E | Y |  |  | Automatic pressure control status | ENUM_IN_STATE_AUTO_STATIC_PRESSURE_RUNNING | N |  | - |  | 0 = off, 1 = complete, 2 = running
40BC | E | Y |  |  | Room occupancy status | ENUM_IN_STATE_KEY_TAG | N |  | - |  | 0 = unoccupied, 1 = occupied
40BD | E | Y |  |  | Vacancy control | ENUM_IN_EMPTY_ROOM_CONTROL_USED | N |  | - |  | 0 = disable, 1 = enable
40C0 | E | Y | Y | Y | FSV 4041 (UFH mixing valve operation) | ENUM_IN_FSV_4041 | N |  | - |  | 0 = not use, 1 = use 4042/3, 2 = use WL1/2
40C1 | E | Y | Y | Y | FSV 4044 (mixing valve control factor) | ENUM_IN_FSV_4044 | N |  | - |  | Values 1 - 5 (see user manual)
40C2 | E | Y | Y | Y | FSV 4051 (circ'n pump PWM control) | ENUM_IN_FSV_4051 | N |  | - |  | 0 = not use, 1 = 100%, 2 = 70%
40C3 | E | Y | Y | Y | FSV 4053 (PWM control factor) | ENUM_IN_FSV_4053 | N |  | - |  | Values 1 - 3 (see user manual)
40C4 | E | Y | Y | Y | "Inverter pump PWM" | ENUM_IN_WATERPUMP_PWM_VALUE | N |  | 80 | V | %
40C5 | E | Y | Y |  | "DHW thermostat" | ENUM_IN_THERMOSTAT_WATER_HEATER | N |  | 160 | V | 0 = off, 1 = on
40C6 | E |  |  |  | ? |  | N |  | 160 | 0
40D5 | E | Y |  |  | Enable room entry control option | ENUM_IN_ENTER_ROOM_CONTROL_USED | N |  | - |  | 0 = disable, 1 = enable
40D6 | E | Y |  |  | Clear error history for HASS (?) | ENUM_IN_ERROR_HISTORY_CLEAR_FOR_HASS | N |  | - |  | HASS = Home Assistant?
40E3 | E |  |  |  | ? |  | N |  | 40 | 255
40E7 | E | Y |  |  | Set chiller WL sensor | ENUM_IN_CHILLER_WATERLAW_SENSOR | N |  | - |  | 0 = LWT, 1 = roomstat
40F7 | E | Y |  |  | Enable chiller WL | ENUM_IN_CHILLER_WATERLAW_ON_OFF | N |  | - |  | 0 = disable, 1 = enable
40FB | E | Y |  |  | Set chiller silence level | ENUM_IN_CHILLLER_SETTING_SILENT_LEVEL | N |  | - |  | Values 0 (= none) to 3
40FC | E | Y |  |  | Set chiller demand level | ENUM_IN_CHILLER_SETTING_DEMAND_LEVEL | N |  | - |  | Values 0 (=100%) to 10 (=50%) or 11 (not use)
4101 | E | Y |  |  | Enable chiller LWT control | ENUM_IN_CHILLER_EXT_WATER_OUT_INPUT | N |  | - |  | 0 = disable, 1 = enable
4102 | E | Y |  |  | Enable state flow check | ENUM_IN_STATE_FLOW_CHECK | N |  | - |  | 0 = disable, 1 = enable
4103 | E | Y |  |  | Set water valve 1 | ENUM_IN_WATER_VALVE_1_ON_OFF | N |  | - |  | 0 = closed, 1 = open
4104 | E | Y |  |  | Set water valve 2 | ENUM_IN_WATER_VALVE_2_ON_OFF | N |  | - |  | 0 = closed, 1 = open
4105 | E | Y |  |  | Set enthalpy control state (?) | ENUM_IN_ENTHALPY_CONTROL_STATE | N |  | -
4107 | E | Y | Y |  | FSV 5033 (set TDM control) | ENUM_IN_FSV_5033 | N |  | - |  | 0 = A2A, 1 = DHW
4108 | E | Y |  |  | Set TDM equipment type | ENUM_IN_TDM_INDOOR_TYPE | N |  | - |  | 0 = A2A, 2 = A2W
410D | E | Y |  |  | Set free cooling state (?) | ENUM_IN_FREE_COOLING_STATE | N |  | -
4113 | E | Y |  |  | Set diverter valve 2 default position | ENUM_IN_3WAY_VALVE_2 | N |  | - |  | 0 = room, 1 = DHW tank
4117 | E |  |  |  | ? |  | N |  | 160 | 0
4118 | E |  |  |  | ? |  | N |  | -
4119 | E | Y |  |  | Zone 1 operating power | ENUM_IN_OPERATION_POWER_ZONE1 | N |  | - |  | 0 = off, 1 = on
411A | E | Y | Y | Y | FSV 4061 (enable separate zone control) | ENUM_IN_FSV_4061 | N |  | 160 | V | 0 = disable, 1 = enable
411B | E | Y | Y | Y | FSV 5081 (enable PV override) | ENUM_IN_FSV_5081 | N |  | - |  | 0 = disable, 1 = enable
411C | E | Y | Y | Y | FSV 5091 (enable smart grid control) | ENUM_IN_FSV_5091 | N |  | - |  | 0 = disable, 1 = enable
411D | E | Y | Y | Y | FSV 5094 (smart grid hot water mode) | ENUM_IN_FSV_5094 | N |  | - |  | 0 = 55degC, 1 = 70degC
411E | E | Y |  |  | Zone 2 operating power | ENUM_IN_OPERATION_POWER_ZONE2 | N |  | 3 - 160 | V | 0 = off, 1 = on
4123 | E | Y | Y |  | "PV control" | ENUM_IN_PV_CONTACT_STATE | N |  | - |  | 0 = disable, 1 = enable
4124 | E | Y | Y |  | "Smart Grid" (readiness) | ENUM_IN_SG_READY_MODE_STATE | N |  | 160 | 0
4125 | E | Y |  |  | FSV load save | ENUM_IN_FSV_LOAD_SAVE | N |  | 160 | 0 | 0 = disable, 1 = enable (dup 0x412D?)
4127 | E | Y | Y | Y | FSV 2093 (WRC circ'n pump control) | ENUM_IN_FSV_2093 | N |  | 160 | V | Values 0 - 4 (see user manual)
4128 | E | Y | Y | Y | FSV 5022 (enable DHW saving mode) | ENUM_IN_FSV_5022 | N |  | 160 | V | 0 = disable, 1 = enable
412A | E | Y | Y |  | (Future) | ENUM_IN_FSV_2094 | N |  | - |  | Values 0 - 4 (see user manual)
412D | E | Y |  |  | FSV load save | ENUM_IN_FSV_LOAD_SAVE | N |  | - |  | 0 = disable, 1 = enable (dup 0x4125?)
4147 | E | Y |  |  | Gas level (refrigerant inventory?) | ENUM_IN_GAS_LEVEL | N |  | - |  | Values 0 - 7
4149 | E | Y |  |  | Diffuser operation | ENUM_IN_DIFFUSER_OPERATION_POWER | N |  | - |  | 0 = off, 1 = on
415D | E | Y |  |  | Set state temperature alarm (?) | ENUM_IN_STATE_TEMP_ALARM | N |  | - |  | 0 = none, 1 = THA, 2 = TLA
415E | E | Y |  |  | Forced defrost status | ENUM_IN_FORCED_DEFROST_KEY_STATUS | N |  | -
415F | E | Y |  |  | Night time settings | ENUM_IN_NIGHT_TIME_USE | N |  | - |  | 0 = off, 1 - 3 = timer settings
4160 | E | Y |  |  | Defrost group (?) | ENUM_IN_DEFROST_GROUP | N |  | -
4161 | E | Y |  |  | Defrost total cycle time | ENUM_IN_DEFROST_CYCLE_TIME | N |  | -
4162 | E | Y |  |  | Defrost elapsed time | ENUM_IN_DEFROST_EXECUTION_TIME | N |  | -
4163 | E | Y |  |  | Set defrost execution type | ENUM_IN_DEFROST_EXECUTION_TYPE | N |  | - |  | 0 = time interval, 1 = actual time
4164 | E |  |  |  | ? |  | N |  | 160 | 0
4167 | E |  |  |  | ? |  | N |  | 160 | 0
4201 | V | Y | Y |  | "Zone 1 room set temp" | VAR_in_temp_target_f | Y | 10 | 160 | V | If WL selected (0x406F), use 0x4247
4202 | V |  |  |  | Duplicate of 427F (?) |  | Y | 10 | 10 - 170 | V
4203 | V | Y | Y |  | "Room Temp degC" (at WRC) | VAR_in_temp_room_f | Y | 10 | 40 | 200
4204 | V | Y |  |  | ? | VAR_IN_TEMP_ROOM_DISPLAY_F | Y | 10 | 40 | V | Tracks 4205 (within 0.3degC)
4205 | V | Y | Y |  | "Eva In1 degC" (Indoor Unit) | VAR_in_temp_eva_in_f | Y | 10 | 40 | V | Duplicate of 82DE?
4206 | V | Y |  |  | Evaporator outlet temp (Indoor Unit)? | VAR_in_temp_eva_out_f | Y | 10 | 40 | -500 | not conn
4207 | V | Y |  |  | Electric heater outlet temp | VAR_IN_TEMP_ELECTRIC_HEATER_F | Y | 10 | -
420B | V | Y |  |  | Discharge temp (duct/AHU) | VAR_in_temp_discharge | Y | 10 | -
420C | V |  |  |  | ? |  | Y | 10 | 40 | V | Duplicate of 8204?
4211 | V | Y |  |  | Indoor unit capacity | VAR_in_capacity_request | N | 8.6 | 3 - 160 | 0 or 68
4212 | V | Y |  |  | Indoor unit absolute capacity | VAR_in_capacity_absolute | N | 8.6 | 160 | 68
4213 | V |  |  |  | ? |  | N |  | 160 | 0
4217 | V | Y |  |  | EEV value real1 | VAR_in_eev_value_real_1 | N |  | 40 | 0 | Range 0 - 3000
4218 | V | Y |  |  | EEV value real2 | VAR_in_eev_value_real_2 | N |  | - |  | Range 0 - 3000
421B | V | Y |  |  | CO2 measurement | VAR_IN_SENSOR_CO2_PPM | N |  | - |  | Range 400 - 5000 ppm
4229 | V | Y |  |  | Indoor unit model information | VAR_in_model_information | N |  | 160 | 115 | Values per NASA.ptc
422A | V | Y |  |  | Cooling target temp | VAR_IN_TEMP_DISCHARGE_COOL_TARGET_F | Y | 10 | -
422B | V | Y |  |  | Heating target temp | VAR_IN_TEMP_DISCHARGE_HEAT_TARGET_F | Y | 10 | -
4235 | V | Y | Y | Y | "DHW Set Temp" (tank target temp) | VAR_IN_TEMP_WATER_HEATER_TARGET_F | Y | 10 | 160 | V
4236 | V | Y | Y |  | "Water In degC" (DHW tank coil inlet temp) | VAR_IN_TEMP_WATER_IN_F | Y | 10 | 40 | V | copy of Tw2 (0x82E0)
4237 | V | Y | Y | Y | "DHW Tank degC" (measured temp) | VAR_IN_TEMP_WATER_TANK_F | Y | 10 | 40 | V
4238 | V | Y | Y |  | "Water Out degC" (DHW tank coil outlet temp) | VAR_IN_TEMP_WATER_OUT_F | Y | 10 | 40 | V | copy of Tw1 (0x82DF)
4239 | V | Y |  |  | DHW tank coil outlet temp 2 | VAR_IN_TEMP_WATER_OUT2_F | Y | 10 | 40 | -500 | not conn
423E | V |  |  |  | ? |  | N |  | 40 | -1
4247 | V | Y | Y |  | "Water Outlet Set Temp" (target LWT if WL not selected) | VAR_IN_TEMP_WATER_OUTLET_TARGET_F | Y | 10 | 160 | V
4248 | V | Y | Y |  | "Water Law Target Value" | VAR_IN_TEMP_WATER_LAW_TARGET_F | Y | 10 | 160 | 0
424A | V | Y | Y | Y | FSV 1011 (max LWT for cooling) | VAR_IN_FSV_1011 | Y | 10 | 160 | V
424B | V | Y | Y | Y | FSV 1012 (min LWT for cooling) | VAR_IN_FSV_1012 | Y | 10 | 160 | V
424C | V | Y | Y | Y | FSV 1021 (max room temp for cooling) | VAR_IN_FSV_1021 | Y | 10 | 160 | V
424D | V | Y | Y | Y | FSV 1022 (min room temp for cooling) | VAR_IN_FSV_1022 | Y | 10 | 160 | V
424E | V | Y | Y | Y | FSV 1031 (max LWT for heating) | VAR_IN_FSV_1031 | Y | 10 | 160 | V
424F | V | Y | Y | Y | FSV 1032 (min LWT for heating) | VAR_IN_FSV_1032 | Y | 10 | 160 | V
4250 | V | Y | Y | Y | FSV 1041 (max room temp for heating) | VAR_IN_FSV_1041 | Y | 10 | 160 | V
4251 | V | Y | Y | Y | FSV 1042 (min room temp for heating) | VAR_IN_FSV_1042 | Y | 10 | 160 | V
4252 | V | Y | Y | Y | FSV 1051 (max DHW tank temp) | VAR_IN_FSV_1051 | Y | 10 | 160 | V
4253 | V | Y | Y | Y | FSV 1052 (min DHW tank temp) | VAR_IN_FSV_1052 | Y | 10 | 160 | V
4254 | V | Y | Y | Y | FSV 2011 (Heating WL low amb temp) | VAR_IN_FSV_2011 | Y | 10 | - |  | With 2021/2031 sets max heating LWT
4255 | V | Y | Y | Y | FSV 2012 (Heating WL high amb temp) | VAR_IN_FSV_2012 | Y | 10 | - |  | With 2022/2032 sets min heating LWT
4256 | V | Y | Y | Y | FSV 2021 (Heating WL1 high LWT temp) | VAR_IN_FSV_2021 | Y | 10 | -
4257 | V | Y | Y | Y | FSV 2022 (Heating WL1 low LWT temp) | VAR_IN_FSV_2022 | Y | 10 | -
4258 | V | Y | Y | Y | FSV 2031 (Heating WL2 high LWT temp) | VAR_IN_FSV_2031 | Y | 10 | -
4259 | V | Y | Y | Y | FSV 2032 (Heating WL2 low LWT temp) | VAR_IN_FSV_2032 | Y | 10 | -
425A | V | Y | Y | Y | FSV 2051 (Cooling WL low amb temp) | VAR_IN_FSV_2051 | Y | 10 | - |  | With 2061/2071 sets max cooling LWT
425B | V | Y | Y | Y | FSV 2052 (Cooling WL high amb temp) | VAR_IN_FSV_2052 | Y | 10 | - |  | With 2061/2071 sets min cooling LWT
425C | V | Y | Y | Y | FSV 2061 (Cooling WL1 high LWT temp) | VAR_IN_FSV_2061 | Y | 10 | -
425D | V | Y | Y | Y | FSV 2062 (Cooling WL1 low LWT temp) | VAR_IN_FSV_2062 | Y | 10 | -
425E | V | Y | Y | Y | FSV 2071 (Cooling WL2 high LWT temp) | VAR_IN_FSV_2071 | Y | 10 | -
425F | V | Y | Y | Y | FSV 2072 (Cooling WL2 low LWT temp) | VAR_IN_FSV_2072 | Y | 10 | -
4260 | V | Y | Y | Y | FSV 3021 (max DHW tank temp from heat pump) | VAR_IN_FSV_3021 | Y | 10 | -
4261 | V | Y | Y | Y | FSV 3022 (set DHW tank "off" temp) | VAR_IN_FSV_3022 | Y | 10 | -
4262 | V | Y | Y | Y | FSV 3023 (set DHW tank "on" temp) | VAR_IN_FSV_3023 | Y | 10 | -
4263 | V | Y | Y | Y | FSV 3024 (min DHW tank heating time) | VAR_IN_FSV_3024 | N |  | - |  | min
4264 | V | Y | Y | Y | FSV 3025 (max DHW tank heating time) | VAR_IN_FSV_3025 | N |  | - |  | min
4265 | V | Y | Y | Y | FSV 3026 (DHW tank heating interval) | VAR_IN_FSV_3026 | N |  | - |  | hours
4266 | V | Y | Y | Y | FSV 3032 (immersion heater delay time) | VAR_IN_FSV_3032 | N |  | - |  | min
4267 | V | Y | Y | Y | FSV 3033 (DHW tank overshoot temp) | VAR_IN_FSV_3033 | Y | 10 | -
4268 | V | Y |  |  | FSV 3034 (future - not used) | VAR_IN_FSV_3034 | Y | 10 | -
4269 | V | Y | Y | Y | FSV 3043 (disinfection start time) | VAR_IN_FSV_3043 | N |  | 160 | V | o'clock (24h)
426A | V | Y | Y | Y | FSV 3044 (target disinfection temp) | VAR_IN_FSV_3044 | Y | 10 | 160 | V
426B | V | Y | Y | Y | FSV 3045 (disinfection duration) | VAR_IN_FSV_3045 | Y |  | 160 | V | min
426C | V | Y | Y | Y | FSV 3052 (forced DHW duration) | VAR_IN_FSV_3052 | Y | 0.1 | -
426D | V | Y | Y | Y | FSV 4012 (amb temp for CH priority) | VAR_IN_FSV_4012 | Y | 10 | -
426E | V | Y | Y | Y | FSV 4013 (CH upper limit temp) | VAR_IN_FSV_4013 | Y | 10 | -
426F | V | Y |  |  | FSV 4014 (future - not used) | VAR_IN_FSV_4014 | Y | 10 | -
4270 | V | Y | Y | Y | FSV 4024 (backup heater threshhold) | VAR_IN_FSV_4024 | Y | 10 | -
4271 | V | Y | Y | Y | FSV 4025 (backup heater defrost temo) | VAR_IN_FSV_4025 | Y | 10 | -
4272 | V | Y | Y | Y | FSV 4033 (backup boiler threshhold) | VAR_IN_FSV_4033 | Y | 10 | -
4273 | V | Y | Y | Y | FSV 5011 (holiday mode cooling LWT) | VAR_IN_FSV_5011 | Y | 10 | 160 | V
4274 | V | Y | Y | Y | FSV 5012 (holiday mode cooling roomstat temp) | VAR_IN_FSV_5012 | Y | 10 | 160 | V
4275 | V | Y | Y | Y | FSV 5013 (holiday mode heating LWT) | VAR_IN_FSV_5013 | Y | 10 | 160 | V
4276 | V | Y | Y | Y | FSV 5014 (holiday mode heating roomstat temp) | VAR_IN_FSV_5014 | Y | 10 | 160 | V
4277 | V | Y | Y | Y | FSV 5015 (holiday mode cooling WL1 temp) | VAR_IN_FSV_5015 | Y | 10 | 160 | V
4278 | V | Y | Y | Y | FSV 5016 (holiday mode cooling WL2 temp) | VAR_IN_FSV_5016 | Y | 10 | 160 | V
4279 | V | Y | Y | Y | FSV 5017 (holiday mode heating WL1 temp) | VAR_IN_FSV_5017 | Y | 10 | 160 | V
427A | V | Y | Y | Y | FSV 5018 (holiday mode heating WL2 temp) | VAR_IN_FSV_5018 | Y | 10 | 160 | V
427B | V | Y | Y | Y | FSV 5019 (holiday mode DHW tank temp) | VAR_IN_FSV_5019 | Y | 10 | 160 | V
427C | V | Y | Y | Y | FSV 5021 (DHW saving temp) | VAR_IN_FSV_5021 | Y | 10 | -
427D | V | Y |  |  | FSV 5032 (TDM non-priority max operation time) | VAR_IN_FSV_5031 | N | 10 | -
427E | V | Y |  |  | FSV 5031 (TDM priority max operation time) | VAR_IN_FSV_5032 | N | 10 | -
427F | V | Y | Y | Y | "Water Law Set Temp" (calc'd target LWT at given ambient temp) | VAR_IN_TEMP_WATER_LAW_F | Y | 10 | 40 | V
4286 | V | Y | Y | Y | FSV 4042 (mixing valve target dT heating) | VAR_IN_FSV_4042 | N | 10 | -
4287 | V | Y | Y | Y | FSV 4043 (mixing valve target dT cooling) | VAR_IN_FSV_4043 | N | 10 | -
4288 | V | Y | Y | Y | FSV 4045 (mixing valve control interval) | VAR_IN_FSV_4045 | N |  | -
4289 | V | Y | Y | Y | FSV 4046 (mixing valve running time) | VAR_IN_FSV_4046 | N | 0.1 | -
428A | V | Y | Y | Y | FSV 4052 (circ'n pump target dT for PWM) | VAR_IN_FSV_4052 | N | 10 | -
428C | V | Y | Y |  | "Mixing valve temp (TW4) degC" | VAR_IN_TEMP_MIXING_VALVE_F | Y | 10 | 40 | -500 | not conn
428D | V |  |  |  | ? |  | N |  | 160 | 0
4297 | V | Y |  |  | AHU supply air temp | VAR_AHU_PANEL_SA_TEMP | Y | 10 | -
4298 | V | Y |  |  | AHU supply air humidity | VAR_AHU_PANEL_SA_HUMIDITY | Y |  | -
429F | V | Y |  |  | Fan current rpm suction1 | VAR_IN_FAN_CURRENT_RPM_SUCTION1 | N |  | -
42A1 | V | Y |  |  | Fan current rpm suction2 | VAR_IN_FAN_CURRENT_RPM_SUCTION2 | N |  | -
42A3 | V | Y |  |  | Fan current rpm suction3 | VAR_IN_FAN_CURRENT_RPM_SUCTION3 | N |  | -
42A5 | V | Y |  |  | Panel air cool1 temp | VAR_IN_TEMP_PANEL_AIR_COOL1_F | Y | 10 | -
42A6 | V | Y |  |  | Panel air cool2 temp | VAR_IN_TEMP_PANEL_AIR_COOL2_F | Y | 10 | -
42A7 | V | Y |  |  | Panel room cool1 temp | VAR_IN_TEMP_PANEL_ROOM_COOL1_F | Y | 10 | -
42A8 | V | Y |  |  | Panel room cool2 temp | VAR_IN_TEMP_PANEL_ROOM_COOL2_F | Y | 10 | -
42A9 | V | Y |  |  | Panel target cool1 temp | VAR_IN_TEMP_PANEL_TARGET_COOL1_F | Y | 10 | -
42AA | V | Y |  |  | Panel target cool2 temp | VAR_IN_TEMP_PANEL_TARGET_COOL2_F | Y | 10 | -
42AB | V | Y |  |  | Panel air heat1 temp | VAR_IN_TEMP_PANEL_AIR_HEAT1_F | Y | 10 | -
42AC | V | Y |  |  | Panel air heat2 temp | VAR_IN_TEMP_PANEL_AIR_HEAT2_F | Y | 10 | -
42AD | V | Y |  |  | Panel room heat1 temp | VAR_IN_TEMP_PANEL_ROOM_HEAT1_F | Y | 10 | -
42AE | V | Y |  |  | Panel room heat2 temp | VAR_IN_TEMP_PANEL_ROOM_HEAT2_F | Y | 10 | -
42AF | V | Y |  |  | Panel target heat1 temp | VAR_IN_TEMP_PANEL_TARGET_HEAT1_F | Y | 10 | -
42B0 | V | Y |  |  | Panel target heat2 temp | VAR_IN_TEMP_PANEL_TARGET_HEAT2_F | Y | 10 | -
42B1 | V | Y |  |  | MCC group module address | VAR_IN_MCC_GROUP_MODULE_ADDRESS | N |  | -
42B2 | V | Y |  |  | MCC group main | VAR_IN_MCC_GROUP_MAIN | N |  | -
42B3 | V | Y |  |  | MCC module main | VAR_IN_MCC_MODULE_MAIN | N |  | -
42C2 | V | Y |  |  | Evaporator2 inlet temp | VAR_IN_TEMP_EVA2_IN_F | Y | 10 | -
42C3 | V | Y |  |  | Evaporator2 outlet temp | VAR_IN_TEMP_EVA2_OUT_F | Y | 10 | -
42C4 | V | Y |  |  | Chiller PHE inlet pressure | VAR_IN_CHILLER_PHE_IN_P | Y | 100 | -
42C5 | V | Y |  |  | Chiller PHE outlet pressure | VAR_IN_CHILLER_PHE_OUT_P | Y | 100 | -
42C9 | V | Y |  |  | Chiller external temp | VAR_IN_CHILLER_EXTERNAL_TEMPERATURE | Y | 10 | -
42CA | V | Y |  |  | Modulating valve 1 | VAR_IN_MODULATING_VALVE_1 | N |  | -
42CB | V | Y |  |  | Modulating valve 2 | VAR_IN_MODULATING_VALVE_2 | N |  | -
42CC | V | Y |  |  | Modulating fan | VAR_IN_MODULATING_FAN | N |  | -
42CD | V | Y |  |  | DHW tank2 coil inlet temp | VAR_IN_TEMP_WATER_IN2_F | Y | 10 | -
42CE | V | Y | Y | Y | FSV 3046 (max allowed disinfection time) | VAR_IN_FSV_3046 | N |  | 160 | 480 | Mins
42CF | V | Y |  |  | Enthalpy sensor output | VAR_IN_ENTHALPY_SENSOR_OUTPUT | N |  | -
42D0 | V | Y |  |  | Variable damper output | VAR_IN_EXT_VARIABLE_DAMPER_OUTPUT | N |  | -
42D1 | V | Y |  |  | Dust sensor PM10 value | VAR_IN_DUST_SENSOR_PM10_0_VALUE | N |  | - |  | Range -1 to 999
42D2 | V | Y |  |  | Dust sensor PM2.5 value | VAR_IN_DUST_SENSOR_PM2_5_VALUE | N |  | - |  | Range -1 to 999
42D3 | V | Y |  |  | Dust sensor PM1 value | VAR_IN_DUST_SENSOR_PM1_0_VALUE | N |  | - |  | Range -1 to 999
42D4 | V | Y | Y | Y | "Zone2 Room Temp degC" | VAR_IN_TEMP_ZONE2_F | Y | 10 | 40 | V
42D6 | V | Y |  | Y | Target Zone 2 temperature | VAR_IN_TEMP_TARGET_ZONE2_F | Y | 10 | 160 | V
42D7 | V | Y | Y | Y | "Zone2 Room Set Temp" | VAR_IN_TEMP_WATER_OUTLET_TARGET_ZONE2_F | Y | 10 | 160 | V
42D8 | V | Y | Y | Y | "Zone1 Water Out Temp degC" | VAR_IN_TEMP_WATER_OUTLET_ZONE1_F | Y | 10 | 40 | -500 | not conn
42D9 | V | Y | Y | Y | "Zone2 Water Out Temp degC" | VAR_IN_TEMP_WATER_OUTLET_ZONE2_F | Y | 10 | 40 | -500 | not conn
42DB | V | Y | Y | Y | FSV 5082 (PV setting cooling shift temp) | VAR_IN_FSV_5082 | N |  | -
42DC | V | Y | Y | Y | FSV 5083 (PV setting heating shift temp) | VAR_IN_FSV_5083 | N |  | -
42DD | V | Y | Y | Y | FSV 5092 (SG setting heating shift temp) | VAR_IN_FSV_5092 | N | 10 | -
42DE | V | Y | Y | Y | FSV 5093 (SG setting DHW shift temp) | VAR_IN_FSV_5093 | N | 10 | -
42E8 | V | Y |  | Y | Flow sensor voltage | VAR_IN_FLOW_SENSOR_VOLTAGE | N | 10 | 40 | V | Range = 0 - 500
42E9 | V | Y | Y | Y | "Flow sensor" (circulating fluid) | VAR_IN_FLOW_SENSOR_CALC | Y | 10 | 40 | V | Range = 0 - 80 lpm
42ED | V | Y | Y | Y | FSV 3081 (backup heater step 1 power for energy metering) | VAR_IN_FSV_3081 | Y |  | - |  | kW
42EE | V | Y | Y | Y | FSV 3082 (backup heater step 2 power for energy metering) | VAR_IN_FSV_3082 | Y |  | - |  | kW
42EF | V | Y | Y | Y | FSV 3083 (immersion heater power for energy metering) | VAR_IN_FSV_3083 | Y |  | - |  | kW
42F0 | V | Y | Y | Y | FSV 5023 (DHW saving thermo on temp) | VAR_IN_FSV_5023 | Y | 10 | -
42F1 | V |  |  |  | Compressor frequency control | VAR_OUT_COMP_FREQ_RATE_CONTROL | N |  | 160 | 0 | See MIM-B19N manual
4302 | V | Y |  |  | Capacity ventilation request | VAR_IN_CAPACITY_VENTILATION_REQUEST | N | 8.6 | - |  | kW
4306 | V | Y |  |  | Thermostat input status | VAR_IN_THERMOSTAT_INPUT_STATUS | N |  | -
4307 | V | Y |  |  | Thermostat output status | VAR_IN_THERMOSTAT_OUTPUT_STATUS | N |  | -
4308 | V | Y |  |  | Defrost target temperature | VAR_IN_TEMP_DEFROST_TARGET_F | Y | 10 | -
4309 | V | Y |  |  | Defrost measured temperature | VAR_IN_TEMP_DEFROST_F | Y | 10 | -
430A | V | Y |  |  | Upper temperature alarm | VAR_IN_TEMP_ALARM_UPPER | Y | 10 | -
430B | V | Y |  |  | Lower temperature alarm | VAR_IN_TEMP_ALARM_LOWER | Y | 10 | -
430C | V | Y |  |  | Room temperature adjustment | VAR_IN_TEMP_ROOM_ADJUST | Y | 10 | -
430D | V | Y |  |  | Defrost schedule 1 | VAR_IN_DEFROST_SCHEDULE_1 | N |  | -
430E | V | Y |  |  | Defrost schedule 2 | VAR_IN_DEFROST_SCHEDULE_2 | N |  | -
430F | V | Y |  |  | Defrost schedule 3 | VAR_IN_DEFROST_SCHEDULE_3 | N |  | -
4310 | V | Y |  |  | Defrost schedule 4 | VAR_IN_DEFROST_SCHEDULE_4 | N |  | -
4311 | V | Y |  |  | Defrost schedule 5 | VAR_IN_DEFROST_SCHEDULE_5 | N |  | -
4312 | V | Y |  |  | Defrost schedule 6 | VAR_IN_DEFROST_SCHEDULE_6 | N |  | -
4313 | V | Y |  |  | Defrost schedule 7 | VAR_IN_DEFROST_SCHEDULE_7 | N |  | -
4314 | V | Y |  |  | Defrost schedule 8 | VAR_IN_DEFROST_SCHEDULE_8 | N |  | -
4317 | V | Y |  |  | Night time start schedule | VAR_IN_NIGHT_START_SCHEDULE | N | 10 | -
4318 | V | Y |  |  | Night time end schedule | VAR_IN_NIGHT_END_SCHEDULE | N | 10 | -
4319 | V | Y |  |  | Current time | VAR_IN_CURRENT_TIME | N |  | -
431E | V | Y | Y | Y | FSV 1061 (LWT hysteresis for heating) | VAR_IN_FSV_1061 | Y | 10 | - |  | Range 1 - 7degC
431F | V | Y | Y | Y | FSV 1062 (LWT hysteresis for cooling) | VAR_IN_FSV_1062 | Y | 10 | - |  | Range 1 - 7degC
4320 | V | Y | Y |  | FSV 1063 (Roomstat hysteresis for heating) | VAR_IN_FSV_1063 | Y | 10 | - |  | Range 1 - 7degC
4321 | V | Y | Y |  | FSV 1064 (Roomstat hysteresis for cooling) | VAR_IN_FSV_1064 | Y | 10 | - |  | Range 1 - 7degC
440A | L | Y | Y |  | Heat pump boiler status | LVAR_In_Device_staus_Heatpump_Boiler | N |  | ? | 0
440E | L |  |  |  | Compressor running? |  | N |  | 3 - 160 | 0x040* | * = 3 (running) or 1 (not running)
440F | L |  |  |  | ? |  | N |  | 160 | 0
4415 | L | Y |  |  | Static pressure | LVAR_IN_AUTO_STATIC_PRESSURE | N |  | -
4418 | L | Y |  |  | Empty room control data | LVAR_IN_EMPTY_ROOM_CONTROL_DATA | N |  | -
441B | L | Y |  |  | Room entry control data | LVAR_IN_ENTER_ROOM_CONTROL_DATA | N |  | -
441F | L | Y |  |  | ETO cooling control data | LVAR_IN_ETO_COOL_CONTROL_DATA | N |  | -
4420 | L | Y |  |  | ETO heating control data | LVAR_IN_ETO_HEAT_CONTROL_DATA | N |  | -
4423 | L |  |  | Y | Minutes since Outdoor Unit installation (cumulative total) |  | N |  | 160 | V | cum total
4424 | L |  |  | Y | Minutes Outdoor Unit online (cumulative total) |  | N |  | 160 | V | cum total
4426 | L |  |  | Y | Generated energy (current rate) |  | N |  | 160 | V | W
4427 | L |  |  | Y | Generated energy (total to date) |  | N |  | 160 | V | cum total Wh
4604 | S | Y |  |  | Indoor Unit setup info | STR_IN_INSTALL_INDOOR_SETUP_INFO | N |  | 160 | 0x1300090040020000200007990000000000000100
4612 | S | Y |  |  | FSV table info | STR_IN_FSV_TABLE_INFORMATION | N |  | SNET | SNET | Appears after FSV update request
461E | S | Y |  |  | Error history for Home Assistant | STR_IN_ERROR_HISTORY_FOR_HASS | N |  | SNET | 0x02020911000000000000
8000 | E | Y |  |  | Defrost steps (Indoor Unit?) | ENUM_OUT_OPERATION_SERVICE_OP | N |  | 10 | V
8001 | E | Y | Y | Y | "Operation Mode" | ENUM_out_operation_odu_mode | N |  | 3 | V | Range 0 - 36 (main ones 0 = stop, 1 = safety start, 3 = normal op, 5 = defrost)
8003 | E | Y | Y |  | "Operation Status" | ENUM_out_operation_heatcool | N |  | 3 | V | Range 0 - 4 (main ones 1 = cool, 2 = heat)
8005 | E |  |  |  | ? |  | N |  | 10 | 255
800D | E |  |  |  | ? |  | N |  | 135 | 0 or 1
8010 | E | Y | Y |  | "Compressor" | ENUM_out_load_comp1 | N |  | 135 | 0 or 1 | 0 = off, 1 = on
8011 | E | Y |  |  | Compressor 2 status | ENUM_out_load_comp2 | N |  | - |  | 0 = off, 1 = on
8012 | E | Y |  |  | Compressor 3 status | ENUM_out_load_comp3 | N |  | - |  | 0 = off, 1 = on
8013 | E | Y |  |  | CCH1 status | ENUM_out_load_cch1 | N |  | - |  | 0 = off, 1 = on
8014 | E | Y |  |  | CCH2 status | ENUM_out_load_cch2 | N |  | - |  | 0 = off, 1 = on
8017 | E | Y | Y |  | "Hot Gas Valve" | ENUM_out_load_hotgas | N |  | 10 | 0 or 1 | 0 = closed, 1 = open
8018 | E | Y |  |  | Hot gas valve 2 status | ENUM_out_load_hotgas2 | N |  | - |  | 0 = closed, 1 = open
8019 | E | Y | Y |  | "Liquid Valve" | ENUM_OUT_LOAD_LIQUID | N |  | 10 | 0 or 1 | 0 = closed, 1 = open
801A | E | Y | Y |  | "4Way Valve" | ENUM_out_load_4way | N |  | 10 | 0 or 1 | 0 = cooling position, 1 = heating position
801F | E | Y |  |  | Main cooling valve status | ENUM_out_load_maincool | N |  | - |  | 0 = closed, 1 = open
8020 | E | Y |  |  | Load EEV status | ENUM_out_load_outeev | N |  | -
8021 | E | Y | Y |  | "EVI Bypass" | ENUM_out_load_evi_bypass | N |  | 10 | 0 or 1 | 0 = closed, 1 = open
8022 | E | Y |  |  | Vapour injection solenoid1 status | ENUM_out_load_evi_sol1 | N |  | - |  | 0 = closed, 1 = open
8023 | E | Y |  |  | Vapour injection solenoid2 status | ENUM_out_load_evi_sol2 | N |  | - |  | 0 = closed, 1 = open
8025 | E | Y |  |  | Gas charge valve status | ENUM_out_load_gascharge | N |  | - |  | 0 = closed, 1 = open
8026 | E | Y |  |  | Water load valve status | ENUM_out_load_water | N |  | - |  | 0 = closed, 1 = open
8027 | E | Y |  |  | Pump out valve status | ENUM_out_load_pumpout | N |  | - |  | 0 = closed, 1 = open
802A | E | Y |  |  | 4Way valve2 status | ENUM_OUT_LOAD_4WAY2 | N |  | - |  | 0 = cooling position, 1 = heating position
8031 | E |  |  |  | ? |  | N |  | 3 | 0
8032 | E |  |  |  | ? |  | N |  | 10 | 255
8033 | E |  |  |  | ? |  | N |  | 10 | 0
8034 | E | Y |  |  | Liquid tube load status | ENUM_out_load_liquidtube | N |  | -
8037 | E | Y |  |  | Accumulator return valve status | ENUM_out_load_accreturn | N |  | - |  | 0 = closed, 1 = open
803B | E | Y |  |  | Flow switch status | ENUM_out_load_flow_switch | N |  | - |  | 0 = deactivated, 1 = activated
803C | E | Y |  |  | Automatic check step | ENUM_out_operation_auto_inspect_step | N |  | 10 | 0 | Range 0 - 13 (see NASA.ptc for list)
803F | E |  |  |  | ? |  | N |  | 3 | 0
8045 | E |  |  |  | ? |  | N |  | 10 | 0
8046 | E | Y |  |  | Automatic check status | ENUM_out_op_test_op_complete | N |  | 135 | 1 | 0 = not complete, 1 = complete
8048 | E |  |  |  | ? |  | N |  | 40 | 0
8049 | E | Y |  |  | MCU A cooling load | ENUM_out_mcu_load_cool_a | N |  | -
804A | E | Y |  |  | MCU A heating load | ENUM_out_mcu_load_heat_a | N |  | -
804B | E | Y |  |  | MCU B cooling load | ENUM_out_mcu_load_cool_b | N |  | -
804C | E | Y |  |  | MCU B heating load | ENUM_out_mcu_load_heat_b | N |  | -
804D | E | Y |  |  | MCU C cooling load | ENUM_out_mcu_load_cool_c | N |  | -
804E | E | Y |  |  | MCU C heating load | ENUM_out_mcu_load_heat_c | N |  | -
804F | E | Y |  |  | MCU D cooling load | ENUM_out_mcu_load_cool_d | N |  | -
8050 | E | Y |  |  | MCU D heating load | ENUM_out_mcu_load_heat_d | N |  | -
8051 | E | Y |  |  | MCU E cooling load | ENUM_out_mcu_load_cool_e | N |  | -
8052 | E | Y |  |  | MCU E heating load | ENUM_out_mcu_load_heat_e | N |  | -
8053 | E | Y |  |  | MCU F cooling load | ENUM_out_mcu_load_cool_f | N |  | -
8054 | E | Y |  |  | MCU F heating load | ENUM_out_mcu_load_heat_f | N |  | -
8055 | E | Y |  |  | MCU liquid load | ENUM_out_mcu_load_liquid | N |  | -
8058 | E | Y |  |  | MCU port 0 address | ENUM_out_mcu_port0_indoor_addr | N |  | -
8059 | E | Y |  |  | MCU port 1 address | ENUM_out_mcu_port1_indoor_addr | N |  | -
805A | E | Y |  |  | MCU port 2 address | ENUM_out_mcu_port2_indoor_addr | N |  | -
805B | E | Y |  |  | MCU port 3 address | ENUM_out_mcu_port3_indoor_addr | N |  | -
805C | E | Y |  |  | MCU port 4 address | ENUM_out_mcu_port4_indoor_addr | N |  | -
805D | E | Y |  |  | MCU port 5 address | ENUM_out_mcu_port5_indoor_addr | N |  | -
805E | E |  |  |  | ? |  | N |  | 3 | 0 or 1
8061 | E | Y |  |  | Defrost operation steps | ENUM_OUT_DEICE_STEP_INDOOR | N |  | 3 | V | Range 0 - 7 (stage 1/2/3, 7 = end, 255 = no defrost
8062 | E |  |  |  | ? |  | N |  | 3 | 0
8063 | E |  |  |  | ? |  | N |  | 10 | 1
8066 | E |  |  |  | ? |  | N |  | 10 | 0
8075 | E |  |  |  | ? |  | N |  | 3 | 255
8077 | E |  |  |  | ? |  | N |  | 10 | 0
8078 | E |  |  |  | ? |  | N |  | 10 | 0
8079 | E |  |  |  | ? |  | N |  | 10 | 0
807A | E |  |  |  | ? |  | N |  | 10 | 0
807B | E |  |  |  | ? |  | N |  | 10 | 0
807C | E |  |  |  | ? |  | N |  | 10 | 0
807D | E |  |  |  | ? |  | N |  | 10 | 0
807E | E |  |  |  | ? |  | N |  | 10 | 0
807F | E |  |  |  | ? |  | N |  | 10 | 255
8081 | E |  |  |  | ? |  | N |  | 40 | 0
8083 | E |  |  |  | ? |  | N |  | 10 | 0
808D | E |  |  |  | ? |  | N |  | 3 | 0
808E | E | Y |  |  | Operation reference step | ENUM_OUT_OP_CHECK_REF_STEP | N |  | 10 | V | Values 0 - 8 (and 255?)
8092 | E | Y |  |  | No. of Outdoor Units | ENUM_OUT_INSTALL_ODU_COUNT | N |  | -
8099 | E | Y |  |  | No. of fans | ENUM_OUT_CONTROL_FAN_NUM | N |  | -
809C | E | Y |  |  | Refrigerant inventory | ENUM_OUT_CHECK_REF_RESULT | N |  | 40 | 0 | Values 0 - 7
809D | E |  |  |  | ? |  | N |  | 40 | 0
809E | E | Y |  |  | Cbox cooling fan status | ENUM_OUT_LOAD_CBOX_COOLING_FAN | N |  | -
80A5 | E | Y |  |  | Backup operation status | ENUM_OUT_STATE_BACKUP_OPER | N |  | -
80A6 | E | Y |  |  | Compressor protection control operation status | ENUM_OUT_STATE_COMP_PROTECT_OPER | N |  | -
80A7 | E |  |  |  | ? |  | N |  | 40 | 0
80A9 | E |  |  |  | ? |  | N |  | 10 | 0
80AA | E |  |  |  | ? |  | N |  | 40 | 1
80AF | E | Y | Y | Y | "Base Heater" | ENUM_OUT_LOAD_BASEHEATER | N |  | 10 | 0 or 1 | 0 = off, 1 = on
80B1 | E |  |  |  | ? |  | N |  | 10 | 0
80B2 | E |  |  |  | ? |  | N |  | 135 | 0xFF80
80B4 | E | Y |  |  | Accumulator valve status | ENUM_OUT_STATE_ACCUM_VALVE_ONOFF | N |  | - |  | 0 = closed, 1 = open
80B6 | E |  |  |  | ? |  | N |  | 40 | 1
80B8 | E | Y |  |  | Oil bypass valve 1 status | ENUM_OUT_LOAD_OIL_BYPASS1 | N |  | - |  | 0 = closed, 1 = open
80B9 | E | Y |  |  | Oil bypass valve 2 status | ENUM_OUT_LOAD_OIL_BYPASS2 | N |  | - |  | 0 = closed, 1 = open
80BC | E |  |  |  | ? |  | N |  | 40 | 0
80BE | E | Y |  |  | A2* current mode | ENUM_OUT_OP_A2_CURRENTMODE | N |  | - |  | 0 = off, 1 = A2W, 3 = A2A
80BF | E |  |  |  | ? |  | N |  | 3 | 0
80C1 | E | Y |  |  | A2A valve status | ENUM_OUT_LOAD_A2A_VALVE | N |  | -
80CE | E |  |  |  | ? |  | N |  | 10 | 0
80CF | E |  |  |  | ? |  | N |  | 160 | 0
80D7 | E | Y | Y |  | "PHE Heater" | ENUM_OUT_LOAD_PHEHEATER | N |  | 10 | 0 | 0 = off, 1 = on
80D8 | E | Y | Y |  | "Waterout Type" | ENUM_OUT_EHS_WATEROUT_TYPE | N |  | 40 | 1 | 0 = default, 1 = 70degC
8200 | V |  |  |  | ? |  | N |  | 40 | 0
8202 | V | Y |  |  | No. outdoor compressors | VAR_out_install_Comp_Num | N |  | 135 | V
8204 | V | Y | Y | Y | "Outdoor Temp" | VAR_out_sensor_airout | Y | 10 | 10 | V
8206 | V | Y | Y |  | "High Pressure" | VAR_out_sensor_highpress | Y | 10 | 10 | V
8208 | V | Y | Y |  | "Low Pressure" | VAR_out_sensor_lowpress | Y | 10 | 10 | V
820A | V | Y | Y |  | "Discharge1" | VAR_out_sensor_discharge1 | Y | 10 | 10 | V
820C | V | Y |  |  | Compressor discharge2 | VAR_out_sensor_discharge2 | Y | 10 | -
820E | V | Y |  |  | Compressor discharge3 | VAR_out_sensor_discharge3 | Y | 10 | -
8217 | V | Y | Y |  | "Compressor Current1" | VAR_out_sensor_ct1 | Y | 10 | 10 | V
8218 | V | Y | Y | Y | "CondOut Temp" | VAR_out_sensor_condout | Y | 10 | 10 | V
821A | V | Y | Y |  | "Suction1 Temp" | VAR_out_sensor_suction | Y | 10 | 10 | V
821C | V | Y |  | Y | Double tube temp | VAR_out_sensor_doubletube | Y | 10 | 10 | V | Duplicate of 0x82DE
821E | V | Y | Y | Y | "EVI IN" | VAR_outcd__sensor_eviin | Y | 10 | 10 | V
8220 | V | Y | Y | Y | "EVI OUT" | VAR_out_sensor_eviout | Y | 10 | 10 | V
8223 | V | Y |  |  | Target compressor discharge pres | VAR_out_control_target_discharge | Y | 10 | -
8224 | V |  |  | Y | ? | VAR_out | Y | 10 | <= 10 | V | Related to compressor motor current?
8225 | V |  |  | Y | Tracks Tw2 (0x82E0) | VAR_out | Y | 10 | 10 | V
8226 | V | Y |  |  | Fan speed step setting | VAR_out_load_fanstep1 | N |  | 10 | V
8227 | V |  |  |  | ? | VAR_out | N |  | 135 | 0
8229 | V | Y | Y |  | "Main EEV1" (opening) | VAR_out_load_outeev1 | N |  | 10 | V | Wide open = 2000, control range ~150-300
822A | V | Y |  |  | EEV2 opening | VAR_out_load_outeev2 | N |  | -
822B | V | Y |  |  | EEV3 opening | VAR_OUT_LOAD_OUTEEV3 | N |  | -
822C | V | Y |  |  | EEV4 opening | VAR_OUT_LOAD_OUTEEV4 | N |  | -
822D | V | Y |  |  | EEV5 opening | VAR_OUT_LOAD_OUTEEV5 | N |  | -
822E | V | Y | Y |  | "EVI EEV" | VAR_out_load_evieev | N |  | 10 | V
8231 | V |  |  |  | Compressor running? |  | N |  | 10 | 0 or 100 | Stopped or running
8233 | V |  |  |  | Compressor running? |  | N |  | 3 | 0 or 68 | Stopped or running
8234 | V |  |  |  | ? |  | N |  | 10 | 300
8235 | V | Y |  |  | Duplicate of 0x0202? | VAR_out_error_code | N |  | 3 | V (0)
8236 | V | Y | Y | Y | "Order Frequency1" | VAR_out_control_order_cfreq_comp1 | N |  | 10 | V
8237 | V | Y | Y | Y | "Target Frequency1" | VAR_out_control_target_cfreq_comp1 | N |  | 10 | V
8238 | V | Y | Y | Y | "Current Frequency1" | VAR_out_control_cfreq_comp1 | N |  | 10 | V
8239 | V |  |  |  | ? |  | N |  | 10 | 45
823B | V | Y | Y |  | "DC Link1" | VAR_out_sensor_dclink_voltage | N |  | 135 | V
823C | V |  |  |  | ? |  | N |  | 135 | 0, 3 or 255 | Likely ENUM rather than VAR
823D | V | Y | Y | Y | "Fan1 RPM" | VAR_out_load_fanrpm1 | N |  | 10 | Y
823E | V | Y |  |  | Fan2 rpm | VAR_out_load_fanrpm2 | N |  | -
823F | V |  |  |  | ? |  | N |  | 3 | 200
8240 | V |  |  | Y | ? |  | N |  | 135 | V | Percent of Outdoor Unit capability used?
8243 | V |  |  |  | ? |  | N |  | 3 | 0
8244 | V |  |  |  | ? |  | N |  | <= 3 | 0
8245 | V |  |  |  | ? |  | N |  | 10 | 255 | Likely ENUM rather than VAR
8247 | V |  |  |  | ? |  | N |  | 3 | 255 | Likely ENUM rather than VAR
8248 | V |  |  |  | ? |  | N |  | <= 3 | 255 | Likely ENUM rather than VAR
8249 | V |  |  |  | ? |  | N |  | 3 | 3 or 255 | Likely ENUM rather than VAR
824B | V |  |  |  | ? |  | N |  | 135 | 0
824C | V |  |  |  | ? |  | N |  | 135 | V
824F | V | Y |  |  | Refrigerant inventory | VAR_out_control_refrigerants_volume | N | 10 | -
8254 | V | Y | Y | Y | "IPM1 Temp" | VAR_out_sensor_IPM1 | Y | 10 | 10 | V
8255 | V | Y |  |  | IPM2 temp | VAR_out_sensor_IPM2 | Y | 10 | -
825A | V |  |  |  | ? |  | N |  | 10 | 255 | Likely ENUM rather than VAR
825B | V |  |  |  | ? |  | N |  | 10 | 0
825C | V |  |  |  | ? |  | N |  | 10 | 3 | Likely ENUM rather than VAR
825D | V |  |  |  | ? |  | N |  | 10 | 0
825E | V | Y |  |  | Water temp sensor | VAR_out_sensor_temp_water | Y | 10 | -
825F | V | Y |  |  | Pipe1 inlet temp | VAR_OUT_SENSOR_PIPEIN1 | Y | 10 | -
8260 | V | Y |  |  | Pipe2 inlet temp | VAR_OUT_SENSOR_PIPEIN2 | Y | 10 | -
8261 | V | Y |  |  | Pipe3 inlet temp | VAR_OUT_SENSOR_PIPEIN3 | Y | 10 | -
8262 | V | Y |  |  | Pipe4 inlet temp | VAR_OUT_SENSOR_PIPEIN4 | Y | 10 | -
8263 | V | Y |  |  | Pipe5 inlet temp | VAR_OUT_SENSOR_PIPEIN5 | Y | 10 | -
8264 | V | Y |  |  | Pipe1 outlet temp | VAR_OUT_SENSOR_PIPEOUT1 | Y | 10 | -
8265 | V | Y |  |  | Pipe2 outlet temp | VAR_OUT_SENSOR_PIPEOUT2 | Y | 10 | -
8266 | V | Y |  |  | Pipe3 outlet temp | VAR_OUT_SENSOR_PIPEOUT3 | Y | 10 | -
8267 | V | Y |  |  | Pipe4 outlet temp | VAR_OUT_SENSOR_PIPEOUT4 | Y | 10 | -
8268 | V | Y |  |  | Pipe5 outlet temp | VAR_OUT_SENSOR_PIPEOUT5 | Y | 10 | -
826B | V | Y |  |  | MCU subcooler inlet temp | VAR_out_mcu_sensor_subcooler_in | Y | 10 | -
826C | V | Y |  |  | MCU subcooler outlet temp | VAR_out_mcu_sensor_subcooler_out | Y | 10 | -
826D | V | Y |  |  | MCU subcooler EEV | VAR_out_mcu_subcooler_eev | N |  | -
826E | V | Y |  |  | MCU changeover EEV1 | VAR_out_mcu_change_over_eev1 | N |  | -
826F | V | Y |  |  | MCU changeover EEV2 | VAR_out_mcu_change_over_eev2 | N |  | -
8270 | V | Y |  |  | MCU changeover EEV3 | VAR_out_mcu_change_over_eev3 | N |  | -
8271 | V | Y |  |  | MCU changeover EEV4 | VAR_out_mcu_change_over_eev4 | N |  | -
8272 | V | Y |  |  | MCU changeover EEV5 | VAR_out_mcu_change_over_eev5 | N |  | -
8273 | V | Y |  |  | MCU changeover EEV6 | VAR_out_mcu_change_over_eev6 | N |  | -
8274 | V | Y |  |  | Compressor 2 order freqency | VAR_out_control_order_cfreq_comp2 | N |  | -
8275 | V | Y |  |  | Compressor 2 target freqency | VAR_out_control_target_cfreq_comp2 | N |  | -
8276 | V | Y |  |  | Compressor 2 current freqency | VAR_out_control_cfreq_comp2 | N |  | -
8277 | V | Y |  |  | Compressor 2 current | VAR_out_sensor_ct2 | N | 10 | -
8278 | V | Y | Y |  | "OCT1" | VAR_OUT_SENSOR_OCT1 | N | 10 | 10 | V
827A | V | Y |  |  | Desuperheater temp | VAR_out_control_dsh1 | Y | 10 | 10 | V
8280 | V | Y | Y |  | "Comp Top1" | VAR_out_sensor_top1 | Y | 10 | 10 | V
8281 | V | Y |  |  | Compressor 2 discharge temp | VAR_out_sensor_top2 | Y | 10 | -
8285 | V | Y |  |  | Condensor mid-point temp | VAR_OUT_SENSOR_CONDMID | Y | 10 | -
8287 | V | Y |  |  | Installed capacity | VAR_out_install_capa | N |  | 135 | 3 | Likely ENUM rather than VAR
8298 | V |  |  |  | ? | VAR_out | N |  | 3 | 0
829A | V | Y |  |  | Compressor 2 suction temp | VAR_out_sensor_suction2_1sec | Y | 10 | 10 | 940
829B | V |  |  |  | ? | VAR_out? | N | 1 | 135 | 255 | Likely ENUM rather than VAR
829F | V | Y | Y | Y | "Saturated T_Pd" | VAR_out_sensor_sat_temp_high_pressure | Y | 10 | 10 | V
82A0 | V | Y | Y | Y | "Saturated T_Ps" | VAR_out_sensor_sat_temp_low_pressure | Y | 10 | 10 | V
82A2 | V |  |  |  | ? | VAR_out | N |  | 135 | 0
82A8 | V | Y |  |  | IDU absolute capacity | VAR_out_control_idu_total_abscapa | Y |  | 3 | 0 or 68
82A9 | V |  |  |  | ? | VAR_out | N |  | 3 | 0 or 68
82AA | V |  |  |  | ? | VAR_out | N |  | 3 | 0
82AF | V | Y |  |  | Condensor installed size | VAR_OUT_INSTALL_COND_SIZE | N |  | -
82B2 | V |  |  |  | ? | VAR_out | Y | 10 | 10 | V | Duplicate of 0x827A?
82B5 | V |  |  |  | ? | VAR_out | N |  | 10 | 0
82B8 | V | Y |  |  | Compressor interstage pressure | VAR_out_sensor_midpress | Y | 10 | 10 | 0
82BC | V | Y |  |  | Project code | VAR_OUT_PROJECT_CODE | Y |  | 10 | 0
82BD | V | Y |  |  | Flux valve load | VAR_OUT_LOAD_FLUX_VARIABLE_VALVE | Y | 10 | -
82BE | V | Y |  |  | Control box temp | VAR_OUT_SENSOR_CONTROL_BOX | Y | 10 | -
82BF | V | Y |  |  | Condenser2 outlet temp | VAR_out_sensor_condout2 | Y | 10 | -
82C8 | V | Y |  |  | Accumulator temp | VAR_OUT_SENSOR_ACCUM_TEMP | Y | 10 | -
82C9 | V | Y |  |  | Engine water temp | VAR_OUT_SENSOR_ENGINE_WATER_TEMP | Y | 10 | -
82CA | V | Y |  |  | Oil bypass valve position | VAR_OUT_OIL_BYPASS_VALVE | N |  | - |  | 0 = closed, 1 = open
82CB | V | Y |  |  | Compressor suction superheat | VAR_OUT_SUCTION_OVER_HEAT | N | 10 | -
82CC | V | Y |  |  | Condenser outlet superheat | VAR_OUT_SUB_COND_OVER_HEAT | N | 10 | -
82CD | V | Y |  |  | Outdoor Unit outlet subcool? | VAR_OUT_OVER_COOL | N | 10 | -
82CE | V | Y |  |  | Condenser outlet subcool | VAR_OUT_COND_OVER_COOL | N | 10 | -
82CF | V | Y |  |  | Engine rpm | VAR_OUT_ENGINE_RPM | N | 10 | -
82D0 | V | Y |  |  | Appearance rpm? | VAR_OUT_APPEARANCE_RPM | N | 10 | -
82D1 | V |  |  |  | ? |  | Y |  | 10 | 0x00FF | Likely ENUM rather than VAR
82D2 | V | Y |  |  | Subcooler EEV step | VAR_OUT_SUB_COND_EEV_STEP | N |  | -
82D5 | V |  |  |  | ? |  | N |  | 170 | 0x7FFF | Likely ENUM rather than VAR
82D6 | V |  |  |  | ? |  | N |  | 170 | 0x7FFF | Likely ENUM rather than VAR
82D7 | V |  |  |  | ? |  | N |  | 170 | 0x7FFF | Likely ENUM rather than VAR
82D8 | V |  |  |  | ? |  | N |  | 170 | 0x7FFF | Likely ENUM rather than VAR
82DB | V | Y |  |  | No. phases | VAR_OUT_PHASE_CURRENT | N |  | -
82DE | V | Y | Y | Y | "Eva In1" | VAR_OUT_SENSOR_EVAIN | Y | 10 | 10 | V
82DF | V | Y | Y | Y | "Water In(Tw1)" | VAR_OUT_SENSOR_TW1 | Y | 10 | 10 | V
82E0 | V | Y | Y | Y | "Water Out(Tw2)" | VAR_OUT_SENSOR_TW2 | Y | 10 | 10 | V
82E3 | V | Y | Y | Y | "Capacity" | VAR_OUT_PRODUCT_OPTION_CAPA | N | 10 | 10 | 80
82E7 | V | Y |  |  | Combined suction temp | VAR_OUT_SENSOR_TOTAL_SUCTION | Y | 10 | -
82E8 | V | Y |  |  | Motor Control Unit bypass EEV position | VAR_OUT_LOAD_MCU_HR_BYPASS_EEV | N |  | 10 | 0 or 480
82E9 | V | Y |  |  | Power factor correction element temp | VAR_OUT_SENSOR_PFCM1 | Y | 10 | -
82ED | V |  |  |  | ? |  | N |  | 10 | V | Approx same as 0x821E?
82F5 | V | Y |  |  | Power factor correction overload detection | VAR_OUT_HIGH_OVERLOAD_DETECT | N |  | -
82F6 | V |  |  |  | ? |  | N |  | 10 | 20
82F9 | V | Y |  |  | Compressor suction3 temp | VAR_OUT_SENSOR_SUCTION3_1SEC | Y | 10 | -
82FC | V | Y | Y |  | "EVI SOL EEV" | VAR_OUT_LOAD_EVI_SOL_EEV | Y |  | 10 | V | 2000 max
8401 | L |  |  |  | ? |  | N |  | 10 - 135 | 0
8404 | L |  |  |  | ? |  | N |  | 3 | 75530752 | 0x04808200
8405 | L | Y |  |  | Compressor running time | LVAR_out_load_comp1_running_time | N |  | 135 | V | cum total hours
8408 | L |  |  |  | ? |  | N |  | 10 | V | multiples of 8
8409 | L |  |  |  | ? |  | N |  | 40 | 0
840B | L | Y |  |  | Inspection result 0 | LVAR_OUT_AUTO_INSPECT_RESULT0 | N |  | 10 | 0
840C | L | Y |  |  | Inspection result 1 | LVAR_OUT_AUTO_INSPECT_RESULT1 | N |  | 10 | 0
8411 | L |  |  | Y | ? |  | N |  | 135 | V | Outdoor Unit (only) power (W) ?
8413 | L | Y | Y | Y | Outdoor + Indoor Unit power | LVAR_OUT_CONTROL_WATTMETER_1W_1MIN_SUM | N | 1000 | 30 | V | kW
8414 | L |  |  | Y | Cumulative Outdoor Unit power |  | N |  | 30 | V | Wh (cum total)
8417 | L |  |  |  | ? |  | N |  | 10 - 135 | 3 | Likely ENUM rather than VAR
841A | L |  |  |  | ? |  | N |  | 10 | 0
841F | L |  |  |  | ? |  | N |  | 170 | 255 | Likely ENUM rather than VAR
8601 | S | Y |  |  | "Inverter1 Micom" | STR_out_install_inverter_and_bootloader_info | N |  | SNET | 0x9102412A0000000010001000000000000000000000000000000000000000000000000000000000000000
8608 | S |  |  |  | ? |  | N |  | 135 | 0
860A | S | Y |  |  | Base option info | STR_out_Base_Option | N |  | SNET | 0x000100000000000000000000007F7F7F10000000000000000000010000000000000000
860C | S |  |  |  | ? |  | N |  | 135 | 0x0800000000
860D | S | Y |  |  | Installed Outdoor Unit model info | STR_OUT_INSTALL_MODEL_INFO | N |  | SNET | 0x0408001233
860F | S | Y |  |  | Installed Outdoor Unit setup info | STR_OUT_INSTALL_OUTDOOR_SETUP_INFO | N |  | SNET | 0x0A00000009148110000000002102000027490017E100C0000000000091738F010000C00A08040100
8613 | S | Y |  |  | Outdoor Unit check info | STR_OUT_REF_CHECK_INFO | N |  | -
Note on A1: NASA message number 0xnnn in alphanumeric order
Note on B1: E = enumeration V = variable (2 bytes) L = long variable (4 bytes) S = structure
Note on C1: Whether the message appears in NASA.ptc (and thus accessible to SNET-Pro2)
Note on D1: Whether reported in default SNET-Pro2 tabulation for an EHS range ASHP
Note on E1: Whether reported in NASAmonitor display
Note on F1: Message payload content description (fields in quotes refer to SNET-Pro2 tabulation entries)
Note on G1: Variable name assigned (“Protocol ID”) by NASA.ptc
Note on H1: Whether 2’s complement applied for payload evaluation (negative numbers)
Note on I1: Divisor to be applied to payload to derive actual value (if any)
Note on J1: Frequency at which message appears on F1/F2 data highway (seconds) (Note - varies for some operations)
Note on K1: Payload value (specifics per Sarah Hanson's heat pump): 0xnn… for enum Integer if constant V if varying SNET = appears on SNET start-up or FSV update request

## Packet Decoder
Samsung NASA Packet Decoder |  | Paste your hex NASA packet (with or without spaces between bytes) into cell B3 for disassembly and message evaluation (if packet is valid).
Raw packet data bytes | FD FD FD FF FD 32 00 3C 10 00 00 B0 00 FF C0 14 E1 0C 80 CE 00 80 D7 00 82 04 00 43 82 06 00 5B 82 08 00 5F 82 0A 01 DB 82 17 00 00 82 18 00 4E 82 1A 00 6D 82 1C 00 F5 82 1E 00 D3 82 20 00 F5 56 EF 34
Raw packet concatenated | FDFDFDFFFD32003C100000B000FFC014E10C80CE0080D700820400438206005B8208005F820A01DB821700008218004E821A006D821C00F5821E00D3822000F556EF34
Packet length (chars) | 134
Data start character | 11
Data string | 32003C100000B000FFC014E10C80CE0080D700820400438206005B8208005F820A01DB821700008218004E821A006D821C00F5821E00D3822000F556EF34
Data length | 124
Header before messages | 32003C100000B000FFC014E1
Packet Decoding:
Preamble | FDFDFDFFFD |  |  |  | Mess | Addr | Payload | [5 empty] | Descr ("x" = SNET display)
Packet start | 32 |  |  |  | 1 | 80CE | 0x00 | [5 empty] | ?
Packet length (hex bytes) | 003C | 60 |  |  | 2 | 80D7 | 0x00 | [5 empty] | "PHE Heater"
Source address class | 10 | Outdoor |  |  | 3 | 8204 | 6.7 | [5 empty] | "Outdoor Temp"
Source channel | 00 | 0 |  |  | 4 | 8206 | 9.1 | [5 empty] | "High Pressure"
Source address | 00 | 0 |  |  | 5 | 8208 | 9.5 | [5 empty] | "Low Pressure"
Destination address class | B0 | Broadcast Self Layer |  |  | 6 | 820A | 47.5 | [5 empty] | "Discharge1"
Destination channel | 00 | 0 |  |  | 7 | 8217 | 0 | [5 empty] | "Compressor Current1"
Destination address | FF | 255 |  |  | 8 | 8218 | 7.8 | [5 empty] | "CondOut Temp"
Packet info, protocol vers, retry count | C0 | Pkt = 1 | Pcl = 2 | Rtr = 0 | 9 | 821A | 10.9 | [5 empty] | "Suction1 Temp"
Packet type | 1 | Normal |  |  | 10 | 821C | 24.5 | [5 empty] | Double tube temp
Data type | 4 | Notification |  |  | 11 | 821E | 21.1 | [5 empty] | "EVI IN"
Packet number | E1 | 225 |  |  | 12 | 8220 | 24.5 | [5 empty] | "EVI OUT"
No. messages | 0C | 12
Message registers/payloads | See above right
CRC bytes | 56EF
Packet end | 34
Message string | 80CE0080D700820400438206005B8208005F820A01DB821700008218004E821A006D821C00F5821E00D3822000F5
Message string length | 92
Message No. | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Start char | 1 | 7 | 13 | 21 | 29 | 37 | 45 | 53 | 61 | 69 | 77 | 85
Register | 80CE | 80D7 | 8204 | 8206 | 8208 | 820A | 8217 | 8218 | 821A | 821C | 821E | 8220
Payload length parameter | 0 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Payload length (chars) | 2 | 2 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Payload (hex) | 00 | 00 | 0043 | 005B | 005F | 01DB | 0000 | 004E | 006D | 00F5 | 00D3 | 00F5
In database? | y | y | y | y | y | y | y | y | y | y | y | y
Type (E/V/L/S) | E | E | V | V | V | V | V | V | V | V | V | V
Raw payload (dec) | 0 | 0 | 67 | 91 | 95 | 475 | 0 | 78 | 109 | 245 | 211 | 245
Signed? | N | N | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y
Signed payload (dec) | 0 | 0 | 67 | 91 | 95 | 475 | 0 | 78 | 109 | 245 | 211 | 245
Selected payload (dec) | 0 | 0 | 67 | 91 | 95 | 475 | 0 | 78 | 109 | 245 | 211 | 245
Divisor (dec) | 1 | 1 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Calc'd payload (dec) | 0 | 0 | 6.7 | 9.1 | 9.5 | 47.5 | 0 | 7.8 | 10.9 | 24.5 | 21.1 | 24.5
Displ payload | 0x00 | 0x00 | 6.7 | 9.1 | 9.5 | 47.5 | 0 | 7.8 | 10.9 | 24.5 | 21.1 | 24.5
Payload description | ? | "PHE Heater" | "Outdoor Temp" | "High Pressure" | "Low Pressure" | "Discharge1" | "Compressor Current1" | "CondOut Temp" | "Suction1 Temp" | Double tube temp | "EVI IN" | "EVI OUT"
0x8001 lookup
0x8003 lookup
16 | Outdoor | [7 empty] | 1 | 80 | 128 | €
17 | HTU | [7 empty] | 2 | CE | 206 | Î
32 | Indoor | [7 empty] | 3 | 00 | 0
48 | ERV | [7 empty] | 4 | 80 | 128 | €
53 | Diffuser | [7 empty] | 5 | D7 | 215 | ×
56 | MCU | [7 empty] | 6 | 00 | 0
64 | RMC | [7 empty] | 7 | 82 | 130 | ‚
80 | Wired Remote | [7 empty] | 8 | 04 | 4
88 | PIM | [7 empty] | 9 | 00 | 0
89 | SIM | [7 empty] | 10 | 43 | 67 | C
90 | Peak | [7 empty] | 11 | 82 | 130 | ‚
91 | Power Divider | [7 empty] | 12 | 06 | 6
96 | On/Off Controller | [7 empty] | 13 | 00 | 0
98 | WiFi Kit | [7 empty] | 14 | 5B | 91 | [
101 | Central Controller | [7 empty] | 15 | 82 | 130 | ‚
106 | DMS | [7 empty] | 16 | 08 | 8
128 | Jig Tester | [7 empty] | 17 | 00 | 0
176 | Broadcast Self Layer | [7 empty] | 18 | 5F | 95 | _
177 | Broadcast Control Layer | [7 empty] | 19 | 82 | 130 | ‚
178 | Broadcast Set Layer | [7 empty] | 20 | 0A | 10
179 | Broadcast Control and Set Layer | [7 empty] | 21 | 01 | 1
180 | Broadcast Module Layer | [7 empty] | 22 | DB | 219 | Û
183 | Broadcast Control, Set and Module Layer | [7 empty] | 23 | 82 | 130 | ‚
184 | Broadcast Local Layer | [7 empty] | 24 | 17 | 23
191 | Broadcast Control Set Module and Local Layer | [7 empty] | 25 | 00 | 0
255 | Undefined | [7 empty] | 26 | 00 | 0
€Î€×‚C‚[‚_‚Û‚
0 | Standby
1 | Normal
2 | Gathering
3 | Install
4 | Download
0 | Undefined
1 | Read
2 | Write
3 | Request
4 | Notification
5 | Response
6 | Acknowledge
7 | Negative Acknowledge
0 | Stop
1 | Safety Start
2 | Normal Op'n
3 | Balance Op'n
4 | Recovery Op'n
5 | Defrost
6 | Comp Down
7 | Prohibit Op'n
8 | Line Jig Op'n
9 | PCB Jig Op'n
10 | Test
11 | Charge
12 | Pumpdown
13 | Pumpout
14 | Vacuum Op'n
15 | Calory Jig Op'n
16 | Pumpdown Stop
17 | Substop Op'n
18 | Checkpipe Op'n
19 | CheckRef Op'n
20 | FPT Jig Op'n
21 | Heat/Cool Chg Op'n
22 | Auto Inspect Op'n
23 | Elec Disch Op'n
24 | Split Defrost
25 | Inverter Check
26 | Nonstop Defrost
27 | Rem Test Op'n
28 | Rating Op'n
29 | PC Test Op'n
30 | ThermoOff Op'n
31 | 3Phase Test Op'n
32 | SmartInstall Test
33 | Defrost Perf Test
34 | Inv Fan PBA Check
35 | Auto Pipe Pairing
36 | Auto Charge
1 | Cool
2 | Heat
3 | CoolMain
4 | HeatMain