## Outdoor 10.00.00
Time | Compressor | 4Way Valve | Hot Gas Valve | Liquid Valve | EVI Bypass | Operation Mode | Target Frequency1 | Order Frequency1 | Current Frequency1 | High Pressure ( kgf/cm²) | Saturated T_Pd | Low Pressure ( kgf/cm²) | Saturated T_Ps | Discharge1 ( ℃) | Comp Top1 ( ℃) | Outdoor Temp. ( ℃) | Compressor Current1 ( ℃) | OCT1 ( ℃) | DC Link1 ( ℃) | IPM1 Temp ( ℃) | CondOut Temp. ( ℃) | Suction1 Temp. ( ℃) | Eva In1 ( ℃) | Water In(Tw1) ( ℃) | Water Out(Tw2) ( ℃) | Main EEV1 | EVI EEV | EVI SOL EEV | EVI IN ( ℃) | EVI OUT ( ℃) | Fan1 RPM | Water Law Set Temp. ( ℃) | 3Way Valve | Water Pump | Flow Sensor | Water In ( ℃) | Water Out ( ℃)
| A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S | T | U | V | W | X | Y | Z | a | b | c | d | e | f | g | h | i | j | k | ave water t | density | sp ht | water dt | duty | tA-tevap | %speed | Ttarget-tw2 |  | Pres | Temp | Enth in | Temp | Enth out | DH | R32 flow | flow/n | Pr ratio
45618.292 | - | Off | Off | Off | Off | Stop | 0 | 0 | 0 | 7.6 | 2 | 7.8 | 3 | 18.3 | 29.4 | 1.9 | 0 | 0 | - | 31 | 2.3 | 8.2 | 7.1 | 18.9 | 20.4 | 2000 | 0 | 0 | 4.9 | 6.5 | 0 | 50.3 | Tank | On | 28.7 | 18.9 | 20.4 | 19.65 | 1020.1409 | 3960.0396 | 1.5 | 2898.5552 | -0.4 | 0% | 29.9 | 0 | 7.6 | 18.3 | 538.4086 | 7.1 | 213.1752 | 325.2334 | 0.53473 | #DIV/0! | 0.97436
45618.2921 | - | Off | Off | Off | Off | Stop | 0 | 0 | 0 | 7.6 | 2 | 7.8 | 3 | 18.3 | 29.6 | 1.9 | 0 | 0 | - | 31 | 2.3 | 8.2 | 7.1 | 19 | 18.9 | 2000 | 0 | 0 | 4.9 | 6.5 | 0 | 50.3 | Tank | On | 28.7 | 18.9 | 20.4 | 18.95 | 1020.4045 | 3960.0396 | -0.1 | -193.287 | -0.4 | 0% | 31.4 | 0 | 7.6 | 18.3 | 538.4086 | 7.1 | 213.1752 | 325.2334 | -0.035658 | #DIV/0! | 0.97436
45618.2922 | - | Off | On | Off | Off | Safety Start | 0 | 0 | 0 | 7.6 | 2 | 7.8 | 3 | 18.3 | 29.6 | 1.8 | 0 | 0 | - | 31 | 2.2 | 8.2 | 7.1 | 20.4 | 20.5 | 2000 | 0 | 0 | 4.9 | 6.5 | 0 | 50.3 | Tank | On | 28.7 | 18.9 | 20.4 | 20.45 | 1019.8362 | 3960.0396 | 0.1 | 193.1793 | -0.4 | 0% | 29.8 | 0 | 7.6 | 18.3 | 538.4086 | 7.1 | 213.1752 | 325.2334 | 0.035638 | #DIV/0! | 0.97436
45618.2923 | - | Off | On | Off | On | Safety Start | 20 | 40 | 0 | 7.6 | 2 | 7.8 | 3 | 18.3 | 29.6 | 1.8 | 0 | 0 | - | 31 | 2.2 | 8.2 | 7.1 | 20.2 | 20.8 | 125 | 0 | 0 | 4.9 | 6.5 | 0 | 50.3 | Tank | On | 28.7 | 18.9 | 20.4 | 20.5 | 1019.817 | 3960.0396 | 0.6 | 1159.054 | -0.4 | 0% | 29.5 | 0 | 7.6 | 18.3 | 538.4086 | 7.1 | 213.1752 | 325.2334 | 0.21383 | #DIV/0! | 0.97436
45618.2925 | - | Off | On | Off | On | Safety Start | 20 | 40 | 15 | 7.8 | 3 | 7.7 | 3 | 18.3 | 29.6 | 1.8 | 0 | 0 | - | 31 | 2.2 | 8.2 | 7.1 | 19.4 | 19.9 | 125 | 0 | 0 | 4.9 | 6.5 | 280 | 50.3 | Tank | On | 27.9 | 20.2 | 20.8 | 19.65 | 1020.1409 | 3963.0963 | 0.5 | 939.9781 | -0.4 | 30% | 30.4 | 0 | 7.8 | 18.3 | 537.9102 | 7.1 | 213.142 | 324.7682 | 0.17366 | 0.57886 | 1.013
45618.2926 | - | Off | On | Off | On | Safety Start | 27 | 40 | 25 | 11.2 | 14 | 7.5 | 2 | 18.6 | 29.6 | 1.8 | 1.1 | 5 | - | 31 | 2.1 | 7 | 7.5 | 19.2 | 19.6 | 125 | 0 | 0 | 4.9 | 6.5 | 490 | 50.3 | Tank | On | 27.9 | 20.2 | 20.8 | 19.4 | 1020.2354 | 3963.0963 | 0.4 | 752.0521 | -0.3 | 50% | 30.7 | 1100 | 11.2 | 18.6 | 529.1306 | 7.5 | 213.322 | 315.8086 | 0.14288 | 0.28576 | 1.4933
45618.2927 | - | Off | On | Off | On | Safety Start | 38 | 40 | 36 | 14 | 21 | 7.2 | 1 | 21 | 29.6 | 1.8 | 2.1 | 7 | - | 31 | 1.6 | 3.5 | 10.4 | 19.1 | 19.7 | 125 | 0 | 0 | 4.8 | 6.5 | 530 | 50.3 | Tank | On | 27.9 | 20.2 | 20.8 | 19.4 | 1020.2354 | 3963.0963 | 0.6 | 1128.0782 | 0.2 | 72% | 30.6 | 2100 | 14 | 21 | 523.5788 | 10.4 | 218.3177 | 305.2611 | 0.22173 | 0.30795 | 1.9444
45618.2928 | - | Off | On | Off | On | Safety Start | 40 | 40 | 40 | 14 | 21 | 7.2 | 1 | 21 | 29.6 | 1.8 | 2.1 | 7 | - | 31 | 1.6 | 3.5 | 10.4 | 19.1 | 19.7 | 125 | 0 | 0 | 4.8 | 6.5 | 520 | 50.3 | Tank | On | 27.9 | 20.2 | 20.8 | 19.4 | 1020.2354 | 3963.0963 | 0.6 | 1128.0782 | 0.2 | 80% | 30.6 | 2100 | 14 | 21 | 523.5788 | 10.4 | 218.3177 | 305.2611 | 0.22173 | 0.27716 | 1.9444
45618.2929 | On | Off | On | Off | On | Safety Start | 40 | 40 | 40 | 14.3 | 22 | 7.1 | 0 | 25.7 | 29.8 | 1.8 | 2.4 | 8 | - | 32 | 0.5 | 1 | 14 | 18.8 | 21 | 125 | 0 | 0 | 4.8 | 6.5 | 540 | 50.3 | Tank | On | 27.7 | 18.8 | 21 | 19.9 | 1020.046 | 3959.8044 | 2.2 | 4102.4633 | 1.3 | 80% | 29.3 | 2400 | 14.3 | 25.7 | 528.2357 | 14 | 225.0507 | 303.185 | 0.81187 | 1.0148 | 2.0141
45618.293 | On | Off | On | Off | On | Safety Start | 40 | 40 | 40 | 14.2 | 22 | 7 | 0 | 28.2 | 30.2 | 1.7 | 2.4 | 7 | 180 | 33 | 0.3 | 0.6 | 16.7 | 18.3 | 21 | 425 | 0 | 0 | 4.8 | 6.5 | 560 | 50.3 | Tank | On | 27.7 | 18.8 | 21 | 19.65 | 1020.1409 | 3959.8044 | 2.7 | 5035.3095 | 1.4 | 80% | 29.3 | 2400 | 14.2 | 28.2 | 531.4894 | 16.7 | 230.1414 | 301.348 | 1.0026 | 1.2532 | 2.0286
45618.2931 | On | Off | On | Off | On | Safety Start | 40 | 40 | 40 | 14.2 | 22 | 7 | 0 | 30.5 | 31 | 1.7 | 2.4 | 8 | 180 | 33 | 0 | 0 | 17.3 | 18.4 | 21.1 | 425 | 0 | 0 | 4.8 | 6.5 | 540 | 50.3 | Tank | On | 27.7 | 18.8 | 21 | 19.75 | 1020.103 | 3959.8044 | 2.7 | 5035.1224 | 1.7 | 80% | 29.2 | 2400 | 14.2 | 30.5 | 534.2126 | 17.3 | 231.2702 | 302.9425 | 0.99724 | 1.2466 | 2.0286
45618.2933 | On | Off | On | Off | On | Safety Start | 40 | 40 | 40 | 14.1 | 22 | 7 | 0 | 31.7 | 31.5 | 1.7 | 2.4 | 7 | 180 | 33 | -0.3 | -0.2 | 17.7 | 18.3 | 21.1 | 425 | 0 | 0 | 4.9 | 6.6 | 550 | 50.3 | Tank | On | 27.7 | 18.8 | 21 | 19.7 | 1020.1219 | 3959.8044 | 2.8 | 5221.7055 | 2 | 80% | 29.2 | 2400 | 14.1 | 31.7 | 535.9072 | 17.7 | 232.0312 | 303.8759 | 1.031 | 1.2888 | 2.0143
45618.2934 | On | Off | On | Off | On | Safety Start | 40 | 40 | 40 | 14 | 21 | 7 | 0 | 32.2 | 32 | 1.7 | 2.4 | 7 | 180 | 34 | -0.4 | -0.3 | 18.3 | 18.2 | 20.7 | 425 | 0 | 0 | 5 | 6.7 | 550 | 50.4 | Tank | On | 27.5 | 18.2 | 20.7 | 19.45 | 1020.2165 | 3958.3937 | 2.5 | 4627.3545 | 2.1 | 80% | 29.7 | 2400 | 14 | 32.2 | 536.7688 | 18.3 | 233.1676 | 303.6012 | 0.91449 | 1.1431 | 2
45618.2935 | On | Off | Off | Off | On | Safety Start | 46 | 50 | 45 | 14.2 | 22 | 6.9 | 0 | 32.2 | 32.2 | 1.8 | 2.5 | 8 | 180 | 34 | -0.5 | -0.5 | 18.6 | 18.1 | 20.6 | 500 | 0 | 0 | 5 | 6.8 | 550 | 50.4 | Tank | On | 27.5 | 18.2 | 20.7 | 19.35 | 1020.2542 | 3958.3937 | 2.5 | 4627.5256 | 2.3 | 90% | 29.8 | 2500 | 14.2 | 32.2 | 536.2255 | 18.6 | 233.7158 | 302.5097 | 0.91783 | 1.0198 | 2.058
45618.2936 | On | Off | Off | Off | On | Safety Start | 50 | 50 | 50 | 14.8 | 23 | 6.6 | -1 | 32.2 | 32.2 | 1.8 | 3.2 | 9 | 180 | 34 | -0.8 | -0.9 | 19 | 18.1 | 21.5 | 500 | 0 | 0 | 5.2 | 6.9 | 550 | 50.4 | Tank | On | 27.5 | 18.2 | 20.7 | 19.8 | 1020.084 | 3958.3937 | 3.4 | 6292.3849 | 2.6 | 100% | 28.9 | 3200 | 14.8 | 32.2 | 534.575 | 19 | 234.4229 | 300.1522 | 1.2578 | 1.2578 | 2.2424
45618.2937 | On | Off | Off | Off | On | Safety Start | 50 | 50 | 50 | 14.8 | 23 | 6.5 | -2 | 31.5 | 32.2 | 1.8 | 3.2 | 9 | 180 | 34 | -1.5 | -1.8 | 19.6 | 18.1 | 22.4 | 500 | 0 | 0 | 5.4 | 7 | 540 | 50.4 | Tank | On | 27.5 | 18.2 | 20.7 | 20.25 | 1019.9127 | 3958.3937 | 4.3 | 7956.6796 | 3.3 | 100% | 28 | 3200 | 14.8 | 31.5 | 533.7327 | 19.6 | 235.5543 | 298.1784 | 1.6011 | 1.6011 | 2.2769
45618.2938 | On | Off | Off | Off | On | Safety Start | 50 | 50 | 50 | 15 | 24 | 6.4 | -2 | 31.2 | 32.2 | 1.8 | 3.2 | 9 | 180 | 35 | -1.9 | -2.2 | 20 | 18.3 | 22.6 | 500 | 0 | 0 | 5.7 | 7.1 | 540 | 50.4 | Tank | On | 27.5 | 18.2 | 20.7 | 20.45 | 1019.8362 | 3958.3937 | 4.3 | 7956.0827 | 3.7 | 100% | 27.8 | 3200 | 15 | 31.2 | 532.8082 | 20 | 236.295 | 296.5132 | 1.6099 | 1.6099 | 2.3438
45618.294 | On | Off | Off | Off | On | Safety Start | 50 | 50 | 50 | 15 | 24 | 6.4 | -2 | 30.7 | 32 | 1.8 | 3.2 | 9 | 180 | 35 | -2.2 | -2.6 | 20.3 | 18.3 | 22.6 | 500 | 0 | 0 | 5.9 | 7.2 | 550 | 50.3 | Tank | On | 27.5 | 18.3 | 22.6 | 20.45 | 1019.8362 | 3958.6288 | 4.3 | 7956.5553 | 4 | 100% | 27.7 | 3200 | 15 | 30.7 | 532.2032 | 20.3 | 236.8612 | 295.342 | 1.6164 | 1.6164 | 2.3438
45618.2941 | On | Off | Off | Off | On | Safety Start | 50 | 50 | 50 | 15 | 24 | 6.4 | -2 | 30.7 | 32 | 1.8 | 3.3 | 9 | 180 | 35 | -2.3 | -2.9 | 20.5 | 18.4 | 22.8 | 500 | 0 | 0 | 6.2 | 7.3 | 550 | 50.3 | Tank | On | 27.5 | 18.3 | 22.6 | 20.6 | 1019.7786 | 3958.6288 | 4.4 | 8141.1322 | 4.1 | 100% | 27.5 | 3300 | 15 | 30.7 | 532.2032 | 20.5 | 237.2387 | 294.9646 | 1.656 | 1.656 | 2.3438
45618.2942 | On | Off | Off | Off | On | Safety Start | 50 | 50 | 50 | 15.1 | 24 | 6.3 | -3 | 30.2 | 32 | 1.8 | 3.3 | 9 | 180 | 36 | -2.4 | -3 | 20.5 | 18.4 | 22.8 | 500 | 0 | 0 | 6.5 | 7.5 | 550 | 50.3 | Tank | On | 27.5 | 18.3 | 22.6 | 20.6 | 1019.7786 | 3958.6288 | 4.4 | 8141.1322 | 4.2 | 100% | 27.5 | 3300 | 15.1 | 30.2 | 531.3119 | 20.5 | 237.2322 | 294.0797 | 1.661 | 1.661 | 2.3968
45618.2943 | On | Off | Off | Off | On | Safety Start | 50 | 50 | 50 | 15.1 | 24 | 6.3 | -3 | 30.2 | 32 | 1.8 | 3.3 | 9 | 180 | 36 | -2.4 | -3 | 20.7 | 18.5 | 23 | 500 | 0 | 0 | 6.5 | 7.5 | 550 | 50.3 | Tank | On | 27.5 | 18.3 | 22.6 | 20.75 | 1019.721 | 3958.6288 | 4.5 | 8325.6872 | 4.2 | 100% | 27.3 | 3300 | 15.1 | 30.2 | 531.3119 | 20.7 | 237.6098 | 293.7021 | 1.7008 | 1.7008 | 2.3968
45618.2944 | On | Off | Off | Off | On | Safety Start | 50 | 50 | 50 | 15.2 | 24 | 6.3 | -3 | 30 | 32 | 1.8 | 3.3 | 9 | 180 | 36 | -2.5 | -3.1 | 20.8 | 18.5 | 23.1 | 500 | 0 | 0 | 6.8 | 7.7 | 550 | 50.3 | Tank | On | 27.5 | 18.5 | 23 | 20.8 | 1019.7017 | 3959.099 | 4.6 | 8511.5528 | 4.3 | 100% | 27.2 | 3300 | 15.2 | 30 | 530.7814 | 20.8 | 237.7924 | 292.989 | 1.743 | 1.743 | 2.4127
45618.2945 | On | Off | Off | Off | On | Safety Start | 50 | 50 | 50 | 15.2 | 24 | 6.4 | -2 | 29.8 | 32 | 1.8 | 3.3 | 9 | 181 | 36 | -2.5 | -3.1 | 21 | 18.5 | 23.1 | 500 | 0 | 0 | 7.1 | 7.9 | 540 | 50.3 | Tank | On | 27.5 | 18.5 | 23 | 20.8 | 1019.7017 | 3959.099 | 4.6 | 8511.5528 | 4.3 | 100% | 27.2 | 3300 | 15.2 | 29.8 | 530.5381 | 21 | 238.1702 | 292.3679 | 1.7467 | 1.7467 | 2.375
45618.2947 | On | Off | Off | Off | On | Safety Start | 50 | 50 | 50 | 15.2 | 24 | 6.4 | -2 | 29.6 | 32 | 1.8 | 3.3 | 9 | 181 | 36 | -2.5 | -3.1 | 21.1 | 18.6 | 23.2 | 500 | 0 | 0 | 7.3 | 8 | 540 | 50.3 | Tank | On | 27.5 | 18.5 | 23 | 20.9 | 1019.6632 | 3959.099 | 4.6 | 8511.2311 | 4.3 | 100% | 27.1 | 3300 | 15.2 | 29.6 | 530.2948 | 21.1 | 238.3591 | 291.9358 | 1.7493 | 1.7493 | 2.375
45618.2948 | On | Off | Off | Off | On | Safety Start | 50 | 50 | 50 | 15.2 | 24 | 6.4 | -2 | 29.6 | 32 | 1.8 | 3.3 | 9 | 181 | 36 | -2.4 | -3.1 | 21.1 | 18.7 | 23.2 | 500 | 0 | 0 | 7.6 | 8.1 | 550 | 50.3 | Tank | On | 27.5 | 18.5 | 23 | 20.95 | 1019.6439 | 3959.099 | 4.5 | 8326.0469 | 4.2 | 100% | 27.1 | 3300 | 15.2 | 29.6 | 530.2948 | 21.1 | 238.3591 | 291.9358 | 1.7112 | 1.7112 | 2.375
45618.2949 | On | Off | Off | Off | On | Safety Start | 50 | 50 | 50 | 15.3 | 24 | 6.4 | -2 | 29.4 | 32 | 1.8 | 3.3 | 9 | 181 | 36 | -2.4 | -3.1 | 21.2 | 19 | 23.5 | 500 | 0 | 0 | 7.9 | 8.3 | 550 | 50.3 | Tank | On | 27.5 | 18.7 | 23.2 | 21.25 | 1019.5279 | 3959.5693 | 4.5 | 8326.0883 | 4.2 | 100% | 26.8 | 3300 | 15.3 | 29.4 | 529.7608 | 21.2 | 238.542 | 291.2187 | 1.7154 | 1.7154 | 2.3906
45618.295 | On | Off | Off | Off | On | Safety Start | 50 | 50 | 50 | 15.4 | 25 | 6.4 | -2 | 29.4 | 32 | 1.8 | 3.3 | 9 | 181 | 37 | -2.4 | -3 | 21.4 | 19 | 23.6 | 500 | 0 | 0 | 8.2 | 8.4 | 550 | 50.3 | Tank | On | 27.5 | 18.7 | 23.2 | 21.3 | 1019.5085 | 3959.5693 | 4.6 | 8510.9506 | 4.2 | 100% | 26.7 | 3300 | 15.4 | 29.4 | 529.4691 | 21.4 | 238.9142 | 290.5549 | 1.7575 | 1.7575 | 2.4062
45618.2951 | On | Off | Off | Off | On | Safety Start | 50 | 50 | 50 | 15.4 | 25 | 6.4 | -2 | 29.2 | 32 | 1.8 | 3.3 | 9 | 181 | 37 | -2.3 | -3 | 21.5 | 19 | 23.6 | 500 | 0 | 0 | 8.4 | 8.6 | 550 | 50.3 | Tank | On | 27.5 | 18.7 | 23.2 | 21.3 | 1019.5085 | 3959.5693 | 4.6 | 8510.9506 | 4.1 | 100% | 26.7 | 3300 | 15.4 | 29.2 | 529.2245 | 21.5 | 239.1032 | 290.1213 | 1.7602 | 1.7602 | 2.4062
45618.2952 | On | Off | Off | Off | On | Safety Start | 50 | 50 | 50 | 15.5 | 25 | 6.4 | -2 | 29.2 | 32 | 1.8 | 3.3 | 9 | 181 | 37 | -2.3 | -3 | 21.6 | 19.2 | 23.7 | 500 | 0 | 0 | 8.7 | 8.8 | 550 | 50.3 | Tank | On | 27.5 | 18.7 | 23.2 | 21.45 | 1019.4502 | 3959.5693 | 4.5 | 8325.4543 | 4.1 | 100% | 26.6 | 3300 | 15.5 | 29.2 | 528.9313 | 21.6 | 239.2866 | 289.6446 | 1.7246 | 1.7246 | 2.4219
45618.2953 | On | Off | Off | Off | On | Safety Start | 50 | 50 | 50 | 15.6 | 25 | 6.4 | -2 | 29.2 | 32 | 1.8 | 3.4 | 9 | 181 | 37 | -2.3 | -3 | 21.7 | 19.4 | 24 | 500 | 0 | 0 | 8.9 | 8.9 | 550 | 50.3 | Tank | On | 27.7 | 19.2 | 23.7 | 21.7 | 1019.3529 | 3960.745 | 4.6 | 8574.085 | 4.1 | 100% | 26.3 | 3400 | 15.6 | 29.2 | 528.6372 | 21.7 | 239.4702 | 289.167 | 1.7791 | 1.7791 | 2.4375
45618.2955 | On | Off | Off | Off | On | Safety Start | 50 | 50 | 50 | 15.6 | 25 | 6.4 | -2 | 29.2 | 32.2 | 1.8 | 3.4 | 9 | 181 | 37 | -2.3 | -3 | 21.8 | 19.5 | 24.1 | 500 | 0 | 0 | 9 | 9 | 550 | 50.3 | Tank | On | 27.7 | 19.2 | 23.7 | 21.8 | 1019.3138 | 3960.745 | 4.6 | 8573.7567 | 4.1 | 100% | 26.2 | 3400 | 15.6 | 29.2 | 528.6372 | 21.8 | 239.6594 | 288.9778 | 1.7802 | 1.7802 | 2.4375
45618.2956 | On | Off | Off | Off | On | Safety Start | 50 | 50 | 50 | 15.6 | 25 | 6.4 | -2 | 29.4 | 32.4 | 1.8 | 3.4 | 9 | 181 | 37 | -2.3 | -3 | 22 | 19.7 | 24.2 | 500 | 0 | 0 | 9.3 | 9.1 | 550 | 50.3 | Tank | On | 27.7 | 19.2 | 23.7 | 21.95 | 1019.2552 | 3960.745 | 4.5 | 8386.8879 | 4.1 | 100% | 26.1 | 3400 | 15.6 | 29.4 | 528.8832 | 22 | 240.0378 | 288.8454 | 1.7422 | 1.7422 | 2.4375
45618.2957 | On | Off | Off | Off | On | Safety Start | 50 | 50 | 50 | 15.6 | 25 | 6.4 | -2 | 29.4 | 32.6 | 1.8 | 3.4 | 9 | 181 | 37 | -2.4 | -3.2 | 22.2 | 19.7 | 24.3 | 500 | 0 | 0 | 9.5 | 9.2 | 550 | 50.3 | Tank | On | 27.7 | 19.2 | 23.7 | 22 | 1019.2356 | 3960.745 | 4.6 | 8573.0985 | 4.2 | 100% | 26 | 3400 | 15.6 | 29.4 | 528.8832 | 22.2 | 240.4161 | 288.467 | 1.7832 | 1.7832 | 2.4375
45618.2958 | On | Off | Off | Off | On | Safety Start | 50 | 50 | 50 | 15.6 | 25 | 6.4 | -2 | 29.6 | 32.8 | 1.8 | 3.4 | 9 | 181 | 37 | -2.5 | -3.2 | 22.2 | 19.6 | 24.3 | 500 | 0 | 0 | 9.7 | 9.3 | 550 | 50.3 | Tank | On | 27.7 | 19.7 | 24.3 | 21.95 | 1019.2552 | 3961.9206 | 4.7 | 8762.2386 | 4.3 | 100% | 26 | 3400 | 15.6 | 29.6 | 529.1291 | 22.2 | 240.4161 | 288.713 | 1.821 | 1.821 | 2.4375
45618.2959 | On | Off | Off | Off | On | Safety Start | 50 | 50 | 50 | 15.8 | 25 | 6.4 | -2 | 29.6 | 32.8 | 1.8 | 3.4 | 9 | 181 | 37 | -2.5 | -3.2 | 22.2 | 19.6 | 24.3 | 500 | 0 | 0 | 9.9 | 9.5 | 550 | 50.3 | Tank | On | 27.7 | 19.7 | 24.3 | 21.95 | 1019.2552 | 3961.9206 | 4.7 | 8762.2386 | 4.3 | 100% | 26 | 3400 | 15.8 | 29.6 | 528.541 | 22.2 | 240.4058 | 288.1352 | 1.8246 | 1.8246 | 2.4688
45618.296 | On | Off | Off | Off | On | Safety Start | 50 | 50 | 50 | 15.8 | 25 | 6.4 | -2 | 29.6 | 33 | 1.8 | 3.4 | 9 | 181 | 38 | -2.4 | -3.2 | 22.2 | 19.9 | 24.4 | 500 | 0 | 0 | 10 | 9.6 | 540 | 50.3 | Tank | On | 27.7 | 19.7 | 24.3 | 22.15 | 1019.1768 | 3961.9206 | 4.5 | 8388.7319 | 4.2 | 100% | 25.9 | 3400 | 15.8 | 29.6 | 528.541 | 22.2 | 240.4058 | 288.1352 | 1.7468 | 1.7468 | 2.4688
45618.2962 | On | Off | Off | Off | On | Safety Start | 50 | 50 | 50 | 15.8 | 25 | 6.4 | -2 | 29.6 | 33.5 | 1.8 | 3.4 | 9 | 180 | 38 | -2.4 | -3.2 | 22.5 | 20.1 | 24.7 | 500 | 0 | 0 | 10.1 | 9.6 | 550 | 50.3 | Room | On | 27.7 | 19.7 | 24.3 | 22.4 | 1019.0784 | 3961.9206 | 4.6 | 8574.3208 | 4.2 | 100% | 25.6 | 3400 | 15.8 | 29.6 | 528.541 | 22.5 | 240.9738 | 287.5672 | 1.789 | 1.789 | 2.4688
45618.2963 | On | Off | Off | Off | On | Safety Start | 50 | 50 | 50 | 15.9 | 26 | 6.3 | -3 | 29.8 | 33.7 | 1.8 | 3.4 | 9 | 180 | 38 | -2.4 | -3.2 | 22.5 | 20.2 | 24.7 | 500 | 0 | 0 | 10.3 | 9.8 | 550 | 50.3 | Room | On | 27.5 | 20.2 | 24.7 | 22.45 | 1019.0587 | 3963.0963 | 4.5 | 8329.6699 | 4.2 | 100% | 25.6 | 3400 | 15.9 | 29.8 | 528.4936 | 22.5 | 240.9689 | 287.5247 | 1.7382 | 1.7382 | 2.5238
45618.2964 | On | Off | Off | Off | On | Safety Start | 50 | 50 | 50 | 15.9 | 26 | 6.3 | -3 | 29.8 | 33.7 | 1.8 | 3.4 | 9 | 180 | 38 | -2.5 | -3.2 | 22.7 | 20.2 | 24.8 | 500 | 0 | 0 | 10.4 | 9.9 | 550 | 50.3 | Room | On | 27.5 | 20.2 | 24.7 | 22.5 | 1019.039 | 3963.0963 | 4.6 | 8514.6088 | 4.3 | 100% | 25.5 | 3400 | 15.9 | 29.8 | 528.4936 | 22.7 | 241.3477 | 287.1459 | 1.7792 | 1.7792 | 2.5238
45618.2965 | On | Off | Off | Off | On | Safety Start | 50 | 50 | 50 | 16 | 26 | 6.3 | -3 | 30 | 34.2 | 1.8 | 3.4 | 9 | 180 | 38 | -2.5 | -3.2 | 22.7 | 20.4 | 24.8 | 500 | 0 | 0 | 10.6 | 10 | 550 | 50.3 | Room | On | 27.5 | 20.2 | 24.7 | 22.6 | 1018.9995 | 3963.0963 | 4.4 | 8144.0929 | 4.3 | 100% | 25.5 | 3400 | 16 | 30 | 528.4467 | 22.7 | 241.3429 | 287.1038 | 1.702 | 1.702 | 2.5397
45618.2966 | On | Off | Off | Off | On | Normal Operation | 50 | 50 | 50 | 16.1 | 26 | 6.4 | -2 | 30.2 | 34.4 | 1.8 | 3.5 | 9 | 180 | 38 | -2.4 | -3.2 | 22.8 | 20.6 | 25.2 | 500 | 0 | 0 | 10.7 | 10.1 | 550 | 50.3 | Room | On | 27.5 | 20.2 | 24.7 | 22.9 | 1018.8807 | 3963.0963 | 4.6 | 8513.2863 | 4.2 | 100% | 25.1 | 3500 | 16.1 | 30.2 | 528.4003 | 22.8 | 241.5277 | 286.8726 | 1.7806 | 1.7806 | 2.5156
45618.2967 | On | Off | Off | Off | On | Normal Operation | 50 | 50 | 50 | 16.1 | 26 | 6.4 | -2 | 30.2 | 34.6 | 1.9 | 3.5 | 9 | 180 | 38 | -2.4 | -3.2 | 23.1 | 20.7 | 25.3 | 500 | 0 | 0 | 10.8 | 10.2 | 550 | 50.3 | Room | On | 27.5 | 20.6 | 25.2 | 23 | 1018.841 | 3964.0368 | 4.6 | 8514.9747 | 4.3 | 100% | 25 | 3500 | 16.1 | 30.2 | 528.4003 | 23.1 | 242.0964 | 286.3039 | 1.7845 | 1.7845 | 2.5156
45618.2969 | On | Off | Off | Off | On | Normal Operation | 50 | 50 | 50 | 16.2 | 26 | 6.4 | -2 | 30.5 | 34.8 | 1.9 | 3.5 | 9 | 180 | 38 | -2.4 | -3.2 | 23.2 | 20.8 | 25.4 | 500 | 0 | 0 | 11 | 10.3 | 550 | 50.3 | Room | On | 27.5 | 20.6 | 25.2 | 23.1 | 1018.8012 | 3964.0368 | 4.6 | 8514.6424 | 4.3 | 100% | 24.9 | 3500 | 16.2 | 30.5 | 528.4794 | 23.2 | 242.2816 | 286.1979 | 1.7851 | 1.7851 | 2.5312
45618.297 | On | Off | Off | Off | On | Normal Operation | 50 | 50 | 50 | 16.3 | 27 | 6.4 | -2 | 30.5 | 35 | 1.9 | 3.5 | 9 | 180 | 38 | -2.4 | -3.2 | 23.3 | 21.1 | 25.5 | 500 | 0 | 0 | 11.1 | 10.4 | 550 | 50.3 | Room | On | 27.5 | 20.6 | 25.2 | 23.3 | 1018.7215 | 3964.0368 | 4.4 | 8143.8034 | 4.3 | 100% | 24.8 | 3500 | 16.3 | 30.5 | 528.1836 | 23.3 | 242.4669 | 285.7168 | 1.7102 | 1.7102 | 2.5469
45618.2971 | On | Off | Off | Off | On | Normal Operation | 50 | 50 | 50 | 16.3 | 27 | 6.4 | -2 | 30.7 | 35.2 | 1.9 | 3.5 | 9 | 180 | 39 | -2.4 | -3.2 | 23.5 | 21.2 | 25.7 | 500 | 0 | 0 | 11.2 | 10.5 | 550 | 50.3 | Room | On | 27.5 | 20.6 | 25.2 | 23.45 | 1018.6616 | 3964.0368 | 4.5 | 8328.3999 | 4.3 | 100% | 24.6 | 3500 | 16.3 | 30.7 | 528.4344 | 23.5 | 242.8463 | 285.5881 | 1.7497 | 1.7497 | 2.5469
45618.2972 | On | Off | Off | Off | On | Normal Operation | 50 | 50 | 50 | 16.3 | 27 | 6.4 | -2 | 30.7 | 35.6 | 1.9 | 3.5 | 9 | 180 | 39 | -2.4 | -3.2 | 23.6 | 21.2 | 25.7 | 500 | 0 | 0 | 11.4 | 10.7 | 550 | 50.3 | Room | On | 27.7 | 21.2 | 25.7 | 23.45 | 1018.6616 | 3965.4476 | 4.5 | 8391.9556 | 4.3 | 100% | 24.6 | 3500 | 16.3 | 30.7 | 528.4344 | 23.6 | 243.036 | 285.3984 | 1.7643 | 1.7643 | 2.5469
45618.2973 | On | Off | Off | Off | On | Normal Operation | 52 | 52 | 52 | 16.4 | 27 | 6.3 | -3 | 30.7 | 35.8 | 1.9 | 3.6 | 10 | 180 | 39 | -2.4 | -3.2 | 23.6 | 21.2 | 25.7 | 498 | 0 | 0 | 11.5 | 10.7 | 540 | 50.3 | Room | On | 27.7 | 21.2 | 25.7 | 23.45 | 1018.6616 | 3965.4476 | 4.5 | 8391.9556 | 4.3 | 104% | 24.6 | 3600 | 16.4 | 30.7 | 528.1384 | 23.6 | 243.0319 | 285.1065 | 1.7661 | 1.6981 | 2.6032
45618.2974 | On | Off | Off | Off | On | Normal Operation | 52 | 52 | 52 | 16.6 | 27 | 6.3 | -3 | 31 | 36 | 2 | 3.7 | 10 | 180 | 39 | -2.4 | -3.2 | 23.7 | 21.5 | 26.1 | 498 | 0 | 0 | 11.6 | 10.8 | 550 | 50.3 | Room | On | 27.7 | 21.2 | 25.7 | 23.8 | 1018.5213 | 3965.4476 | 4.6 | 8577.2619 | 4.4 | 104% | 24.2 | 3700 | 16.6 | 31 | 527.9231 | 23.7 | 243.2136 | 284.7094 | 1.8076 | 1.7381 | 2.6349
45618.2975 | On | Off | Off | Off | On | Normal Operation | 52 | 52 | 52 | 16.7 | 27 | 6.3 | -3 | 31 | 36.2 | 2 | 3.7 | 10 | 180 | 39 | -2.5 | -3.3 | 24 | 21.7 | 26.3 | 498 | 0 | 0 | 11.7 | 10.9 | 550 | 50.3 | Room | On | 27.7 | 21.2 | 25.7 | 24 | 1018.4408 | 3965.4476 | 4.6 | 8576.5841 | 4.5 | 104% | 24 | 3700 | 16.7 | 31 | 527.6255 | 24 | 243.7797 | 283.8458 | 1.8129 | 1.7432 | 2.6508
45618.2977 | On | Off | Off | Off | On | Normal Operation | 52 | 52 | 52 | 16.7 | 27 | 6.3 | -3 | 31.2 | 36.2 | 2 | 3.7 | 10 | 180 | 39 | -2.5 | -3.4 | 24 | 21.7 | 26.3 | 498 | 0 | 0 | 11.7 | 11 | 550 | 50.2 | Room | On | 27.5 | 21.7 | 26.3 | 24 | 1018.4408 | 3966.6232 | 4.6 | 8517.1837 | 4.5 | 104% | 23.9 | 3700 | 16.7 | 31.2 | 527.8791 | 24 | 243.7797 | 284.0994 | 1.7988 | 1.7296 | 2.6508
45618.2978 | On | Off | Off | Off | On | Normal Operation | 52 | 52 | 52 | 16.8 | 28 | 6.3 | -3 | 31.5 | 36.5 | 2 | 3.8 | 10 | 180 | 39 | -2.6 | -3.4 | 24.3 | 22 | 26.6 | 498 | 0 | 0 | 11.8 | 11 | 550 | 50.2 | Room | On | 27.5 | 21.7 | 26.3 | 24.3 | 1018.3196 | 3966.6232 | 4.6 | 8516.1705 | 4.6 | 104% | 23.6 | 3800 | 16.8 | 31.5 | 527.9628 | 24.3 | 244.3461 | 283.6166 | 1.8016 | 1.7323 | 2.6667
45618.2979 | On | Off | Off | Off | On | Normal Operation | 52 | 52 | 52 | 16.8 | 28 | 6.3 | -3 | 31.5 | 36.7 | 2 | 3.7 | 10 | 180 | 39 | -2.6 | -3.4 | 24.3 | 21.8 | 26.6 | 498 | 0 | 0 | 11.9 | 11.1 | 550 | 50.2 | Room | On | 27.5 | 21.7 | 26.3 | 24.2 | 1018.3601 | 3966.6232 | 4.8 | 8886.7917 | 4.6 | 104% | 23.6 | 3700 | 16.8 | 31.5 | 527.9628 | 24.3 | 244.3461 | 283.6166 | 1.88 | 1.8077 | 2.6667
45618.298 | On | Off | Off | Off | On | Normal Operation | 54 | 54 | 54 | 16.8 | 28 | 6.3 | -3 | 31.7 | 37.2 | 2 | 3.8 | 10 | 180 | 40 | -2.6 | -3.5 | 24.4 | 22.1 | 26.6 | 497 | 0 | 0 | 11.9 | 11.2 | 540 | 50.2 | Room | On | 27.5 | 21.7 | 26.3 | 24.35 | 1018.2994 | 3966.6232 | 4.5 | 8330.8708 | 4.6 | 108% | 23.6 | 3800 | 16.8 | 31.7 | 528.217 | 24.4 | 244.5362 | 283.6808 | 1.762 | 1.6315 | 2.6667
45618.2981 | On | Off | Off | Off | On | Normal Operation | 54 | 54 | 54 | 16.9 | 28 | 6.2 | -3 | 32 | 37.4 | 2 | 4 | 10 | 180 | 40 | -2.6 | -3.5 | 24.6 | 22.3 | 26.8 | 497 | 0 | 0 | 12 | 11.3 | 550 | 50.2 | Room | On | 27.5 | 22.3 | 26.8 | 24.55 | 1018.2183 | 3968.034 | 4.5 | 8333.17 | 4.6 | 108% | 23.4 | 4000 | 16.9 | 32 | 528.3027 | 24.6 | 244.9131 | 283.3896 | 1.7643 | 1.6336 | 2.7258
45618.2982 | On | Off | Off | Off | On | Normal Operation | 54 | 54 | 54 | 16.9 | 28 | 6.2 | -3 | 32.4 | 37.8 | 2 | 4 | 10 | 180 | 40 | -2.7 | -3.6 | 24.7 | 22.3 | 27 | 497 | 0 | 0 | 12 | 11.4 | 550 | 50.2 | Room | On | 27.5 | 22.3 | 26.8 | 24.65 | 1018.1777 | 3968.034 | 4.7 | 8703.1857 | 4.7 | 108% | 23.2 | 4000 | 16.9 | 32.4 | 528.8127 | 24.7 | 245.1032 | 283.7094 | 1.8406 | 1.7042 | 2.7258
45618.2984 | On | Off | Off | Off | On | Normal Operation | 54 | 54 | 54 | 17.1 | 28 | 6.2 | -3 | 32.6 | 38 | 1.9 | 4 | 10 | 180 | 40 | -2.8 | -3.7 | 24.8 | 22.4 | 27.1 | 497 | 0 | 0 | 12.1 | 11.5 | 550 | 50.2 | Room | On | 27.5 | 22.3 | 26.8 | 24.75 | 1018.137 | 3968.034 | 4.7 | 8702.8379 | 4.7 | 108% | 23.1 | 4000 | 17.1 | 32.6 | 528.4779 | 24.8 | 245.287 | 283.1909 | 1.8439 | 1.7073 | 2.7581
45618.2985 | On | Off | Off | Off | On | Normal Operation | 54 | 54 | 54 | 17.1 | 28 | 6.2 | -3 | 32.8 | 38.4 | 1.9 | 4 | 10 | 180 | 40 | -2.9 | -3.8 | 25.1 | 22.5 | 27.3 | 497 | 0 | 0 | 12.2 | 11.5 | 550 | 50.2 | Room | On | 27.5 | 22.3 | 26.8 | 24.9 | 1018.0758 | 3968.034 | 4.8 | 8887.4709 | 4.8 | 108% | 22.9 | 4000 | 17.1 | 32.8 | 528.7343 | 25.1 | 245.858 | 282.8763 | 1.8851 | 1.7455 | 2.7581
45618.2986 | On | Off | Off | Off | On | Normal Operation | 54 | 54 | 54 | 17.3 | 29 | 6.2 | -3 | 33.2 | 38.8 | 1.9 | 4 | 10 | 180 | 40 | -2.9 | -3.8 | 25.2 | 22.7 | 27.5 | 497 | 0 | 0 | 12.3 | 11.6 | 550 | 50.3 | Room | On | 27.9 | 22.5 | 27.3 | 25.1 | 1017.9941 | 3968.5042 | 4.8 | 9017.088 | 4.8 | 108% | 22.8 | 4000 | 17.3 | 33.2 | 528.6583 | 25.2 | 246.0425 | 282.6158 | 1.9143 | 1.7725 | 2.7903
45618.2987 | On | Off | Off | Off | On | Normal Operation | 56 | 56 | 56 | 17.3 | 29 | 6.2 | -3 | 33.5 | 39 | 1.9 | 4 | 10 | 180 | 40 | -2.9 | -3.8 | 25.3 | 22.7 | 27.6 | 447 | 0 | 0 | 12.4 | 11.7 | 550 | 50.3 | Room | On | 27.9 | 22.5 | 27.3 | 25.15 | 1017.9736 | 3968.5042 | 4.9 | 9204.7589 | 4.8 | 112% | 22.7 | 4000 | 17.3 | 33.5 | 529.045 | 25.3 | 246.233 | 282.8121 | 1.9528 | 1.7436 | 2.7903
45618.2988 | On | Off | Off | Off | On | Normal Operation | 56 | 56 | 56 | 17.4 | 29 | 6.1 | -4 | 33.7 | 39.6 | 1.9 | 4.2 | 10 | 180 | 41 | -3 | -3.9 | 25.4 | 23 | 27.7 | 447 | 0 | 0 | 12.4 | 11.8 | 550 | 50.3 | Room | On | 27.9 | 22.5 | 27.3 | 25.35 | 1017.8916 | 3968.5042 | 4.7 | 8828.3433 | 4.9 | 112% | 22.6 | 4200 | 17.4 | 33.7 | 529.009 | 25.4 | 246.4207 | 282.5883 | 1.8745 | 1.6736 | 2.8525
45618.2989 | On | Off | Off | Off | On | Normal Operation | 56 | 56 | 56 | 17.5 | 29 | 6.1 | -4 | 34 | 39.8 | 1.8 | 4.2 | 10 | 180 | 41 | -3 | -4 | 25.5 | 23.2 | 28.1 | 447 | 0 | 0 | 12.5 | 11.8 | 550 | 50.3 | Room | On | 27.9 | 22.5 | 27.3 | 25.65 | 1017.7682 | 3968.5042 | 4.9 | 9202.9015 | 4.8 | 112% | 22.2 | 4200 | 17.5 | 34 | 529.1033 | 25.5 | 246.6086 | 282.4947 | 1.9546 | 1.7452 | 2.8689
45618.2991 | On | Off | Off | Off | On | Normal Operation | 56 | 56 | 56 | 17.6 | 29 | 6.1 | -4 | 34.2 | 40 | 1.8 | 4.2 | 10 | 180 | 41 | -3.1 | -4 | 25.6 | 23.3 | 28.2 | 447 | 0 | 0 | 12.6 | 11.9 | 550 | 50.3 | Room | On | 27.9 | 23.2 | 28.1 | 25.75 | 1017.727 | 3970.1502 | 4.9 | 9206.3451 | 4.9 | 112% | 22.1 | 4200 | 17.6 | 34.2 | 529.0689 | 25.6 | 246.7966 | 282.2722 | 1.9569 | 1.7472 | 2.8852
45618.2992 | On | Off | Off | Off | On | Normal Operation | 56 | 56 | 56 | 17.7 | 30 | 6.1 | -4 | 34.4 | 40.3 | 1.8 | 4.3 | 10 | 180 | 41 | -3.1 | -4 | 25.8 | 23.5 | 28.5 | 447 | 0 | 0 | 12.6 | 12 | 550 | 50.3 | Room | On | 27.9 | 23.2 | 28.1 | 26 | 1017.6236 | 3970.1502 | 5 | 9393.2755 | 4.9 | 112% | 21.8 | 4300 | 17.7 | 34.4 | 529.0351 | 25.8 | 247.1756 | 281.8595 | 1.9996 | 1.7853 | 2.9016
45618.2993 | On | Off | Off | Off | On | Normal Operation | 56 | 56 | 56 | 17.7 | 30 | 6.1 | -4 | 34.4 | 40.6 | 1.8 | 4.3 | 11 | 183 | 41 | -3.1 | -4 | 26 | 23.6 | 28.6 | 447 | 0 | 0 | 12.6 | 12 | 550 | 50.3 | Room | On | 27.9 | 23.2 | 28.1 | 26.1 | 1017.5822 | 3970.1502 | 5 | 9392.8929 | 4.9 | 112% | 21.7 | 4300 | 17.7 | 34.4 | 529.0351 | 26 | 247.5571 | 281.4779 | 2.0022 | 1.7877 | 2.9016
45618.2994 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 17.8 | 30 | 6.1 | -4 | 34.6 | 40.8 | 1.8 | 4.3 | 10 | 183 | 41 | -3.1 | -4 | 26 | 23.6 | 28.6 | 437 | 0 | 0 | 12.7 | 12 | 540 | 50.3 | Room | On | 27.9 | 23.2 | 28.1 | 26.1 | 1017.5822 | 3970.1502 | 5 | 9392.8929 | 4.9 | 114% | 21.7 | 4300 | 17.8 | 34.6 | 529.002 | 26 | 247.5548 | 281.4471 | 2.0024 | 1.7565 | 2.918
45618.2995 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 17.8 | 30 | 6.1 | -4 | 34.8 | 41.2 | 1.8 | 4.4 | 11 | 183 | 41 | -3.2 | -4.1 | 26.1 | 23.7 | 28.7 | 437 | 0 | 0 | 12.8 | 12 | 550 | 50.3 | Room | On | 27.7 | 23.7 | 28.7 | 26.2 | 1017.5406 | 3971.3258 | 5 | 9327.9414 | 5 | 114% | 21.6 | 4400 | 17.8 | 34.8 | 529.2634 | 26.1 | 247.7457 | 281.5177 | 1.9881 | 1.7439 | 2.918
45618.2996 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 17.8 | 30 | 6.1 | -4 | 35 | 41.6 | 1.8 | 4.4 | 11 | 183 | 42 | -3.2 | -4.2 | 26.3 | 23.8 | 28.8 | 437 | 0 | 0 | 12.8 | 12.1 | 550 | 50.3 | Room | On | 27.7 | 23.7 | 28.7 | 26.3 | 1017.4991 | 3971.3258 | 5 | 9327.5604 | 5 | 114% | 21.5 | 4400 | 17.8 | 35 | 529.5249 | 26.3 | 248.1274 | 281.3975 | 1.9888 | 1.7446 | 2.918
45618.2997 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 17.9 | 30 | 6.1 | -4 | 35.2 | 42 | 1.8 | 4.4 | 11 | 183 | 42 | -3.2 | -4.2 | 26.3 | 24.1 | 29.1 | 437 | 0 | 0 | 12.9 | 12.2 | 550 | 50.3 | Room | On | 27.7 | 23.7 | 28.7 | 26.6 | 1017.3741 | 3971.3258 | 5 | 9326.4144 | 5 | 114% | 21.2 | 4400 | 17.9 | 35.2 | 529.4939 | 26.3 | 248.1253 | 281.3686 | 1.9888 | 1.7446 | 2.9344
45618.2999 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 18.1 | 30 | 6.1 | -4 | 35.4 | 42.2 | 1.8 | 4.4 | 11 | 183 | 42 | -3.2 | -4.2 | 26.5 | 24.3 | 29.3 | 437 | 0 | 0 | 12.9 | 12.2 | 540 | 50.3 | Room | On | 27.7 | 23.7 | 28.7 | 26.8 | 1017.2904 | 3971.3258 | 5 | 9325.6478 | 5 | 114% | 21 | 4400 | 18.1 | 35.4 | 529.1702 | 26.5 | 248.5034 | 280.6669 | 1.9936 | 1.7488 | 2.9672
45618.3 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 18.1 | 30 | 6.1 | -4 | 35.6 | 42.8 | 1.8 | 4.4 | 11 | 183 | 42 | -3.2 | -4.2 | 26.7 | 24.4 | 29.5 | 437 | 0 | 0 | 13 | 12.3 | 550 | 50.3 | Room | On | 27.9 | 24.4 | 29.5 | 26.95 | 1017.2276 | 3972.9717 | 5.1 | 9584.219 | 5 | 114% | 20.8 | 4400 | 18.1 | 35.6 | 529.4339 | 26.7 | 248.8855 | 280.5484 | 2.0497 | 1.798 | 2.9672
45618.3001 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 18.1 | 30 | 6.1 | -4 | 35.8 | 43.1 | 1.8 | 4.4 | 11 | 183 | 42 | -3.1 | -4.1 | 26.7 | 24.4 | 29.6 | 423 | 0 | 0 | 13.1 | 12.4 | 550 | 50.3 | Room | On | 27.9 | 24.4 | 29.5 | 27 | 1017.2066 | 3972.9717 | 5.2 | 9771.9433 | 4.9 | 114% | 20.7 | 4400 | 18.1 | 35.8 | 529.6976 | 26.7 | 248.8855 | 280.8121 | 2.0879 | 1.8315 | 2.9672
45618.3002 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 18.2 | 31 | 6.1 | -4 | 35.8 | 43.3 | 1.8 | 4.4 | 11 | 183 | 42 | -3.2 | -4.1 | 26.8 | 24.5 | 29.7 | 423 | 0 | 0 | 13.2 | 12.5 | 550 | 50.3 | Room | On | 27.9 | 24.4 | 29.5 | 27.1 | 1017.1646 | 3972.9717 | 5.2 | 9771.5398 | 5 | 114% | 20.6 | 4400 | 18.2 | 35.8 | 529.4049 | 26.8 | 249.0749 | 280.33 | 2.0914 | 1.8346 | 2.9836
45618.3003 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 18.3 | 31 | 6.1 | -4 | 36.2 | 43.8 | 1.8 | 4.5 | 11 | 183 | 42 | -3.2 | -4.1 | 27 | 24.6 | 29.7 | 423 | 0 | 0 | 13.2 | 12.6 | 550 | 50.3 | Room | On | 27.9 | 24.4 | 29.5 | 27.15 | 1017.1436 | 3972.9717 | 5.1 | 9583.4274 | 5 | 114% | 20.6 | 4500 | 18.3 | 36.2 | 529.6418 | 27 | 249.4557 | 280.1862 | 2.0522 | 1.8002 | 3
45618.3004 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 18.4 | 31 | 6.1 | -4 | 36.2 | 44 | 1.8 | 4.5 | 11 | 183 | 43 | -3.2 | -4.1 | 27.1 | 24.8 | 30 | 423 | 0 | 0 | 13.3 | 12.6 | 550 | 50.3 | Room | On | 27.7 | 24.6 | 29.7 | 27.4 | 1017.0382 | 3973.442 | 5.2 | 9701.4359 | 5 | 114% | 20.3 | 4500 | 18.4 | 36.2 | 529.3491 | 27.1 | 249.6454 | 279.7036 | 2.0811 | 1.8255 | 3.0164
45618.3006 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 18.4 | 31 | 6.1 | -4 | 36.5 | 44.4 | 1.8 | 4.5 | 11 | 183 | 43 | -3.2 | -4.2 | 27.3 | 25 | 30.1 | 423 | 0 | 0 | 13.3 | 12.7 | 550 | 50.3 | Room | On | 27.7 | 24.6 | 29.7 | 27.55 | 1016.9749 | 3973.442 | 5.1 | 9514.2769 | 5 | 114% | 20.2 | 4500 | 18.4 | 36.5 | 529.748 | 27.3 | 250.028 | 279.7199 | 2.0408 | 1.7902 | 3.0164
45618.3007 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 18.6 | 31 | 6.1 | -4 | 37 | 44.8 | 1.8 | 4.5 | 11 | 183 | 43 | -3.2 | -4.2 | 27.5 | 25.1 | 30.2 | 423 | 0 | 0 | 13.4 | 12.7 | 550 | 50.3 | Room | On | 27.7 | 24.6 | 29.7 | 27.65 | 1016.9325 | 3973.442 | 5.1 | 9513.8811 | 5 | 114% | 20.1 | 4500 | 18.6 | 37 | 529.8309 | 27.5 | 250.4084 | 279.4226 | 2.0429 | 1.792 | 3.0492
45618.3008 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 18.6 | 31 | 6.1 | -4 | 37.2 | 45.1 | 1.8 | 4.5 | 11 | 183 | 43 | -3.2 | -4.1 | 27.6 | 25.3 | 30.4 | 416 | 0 | 0 | 13.4 | 12.8 | 550 | 50.3 | Room | On | 27.7 | 24.6 | 29.7 | 27.85 | 1016.8477 | 3973.442 | 5.1 | 9513.0877 | 5 | 114% | 19.9 | 4500 | 18.6 | 37.2 | 530.0984 | 27.6 | 250.5998 | 279.4986 | 2.0422 | 1.7914 | 3.0492
45618.3009 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 18.6 | 31 | 6.1 | -4 | 37.4 | 45.1 | 1.8 | 4.5 | 11 | 182 | 43 | -3.1 | -4.1 | 27.7 | 25.3 | 30.4 | 416 | 0 | 0 | 13.5 | 12.9 | 550 | 50.3 | Room | On | 27.7 | 25.3 | 30.4 | 27.85 | 1016.8477 | 3975.0879 | 5.1 | 9517.0283 | 4.9 | 114% | 19.9 | 4500 | 18.6 | 37.4 | 530.3658 | 27.7 | 250.7913 | 279.5746 | 2.0425 | 1.7916 | 3.0492
45618.301 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 18.6 | 31 | 6.1 | -4 | 37.4 | 45.5 | 1.8 | 4.5 | 11 | 182 | 43 | -3.1 | -4.1 | 27.7 | 25.3 | 30.4 | 416 | 0 | 0 | 13.5 | 12.9 | 550 | 50.3 | Room | On | 27.7 | 25.3 | 30.4 | 27.85 | 1016.8477 | 3975.0879 | 5.1 | 9517.0283 | 4.9 | 114% | 19.9 | 4500 | 18.6 | 37.4 | 530.3658 | 27.7 | 250.7913 | 279.5746 | 2.0425 | 1.7916 | 3.0492
45618.3011 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 18.7 | 32 | 6.1 | -4 | 37.6 | 45.6 | 1.8 | 4.6 | 11 | 182 | 43 | -3.1 | -4.1 | 27.8 | 25.6 | 30.6 | 416 | 0 | 0 | 13.5 | 12.9 | 550 | 50.3 | Room | On | 27.7 | 25.3 | 30.4 | 28.1 | 1016.7414 | 3975.0879 | 5 | 9329.4444 | 4.9 | 114% | 19.7 | 4600 | 18.7 | 37.6 | 530.3434 | 27.8 | 250.9818 | 279.3616 | 2.0037 | 1.7577 | 3.0656
45618.3012 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 18.9 | 32 | 6.1 | -4 | 37.8 | 46 | 1.8 | 4.6 | 11 | 182 | 43 | -3.1 | -4.1 | 28 | 25.8 | 30.8 | 416 | 0 | 0 | 13.6 | 13 | 550 | 50.3 | Room | On | 27.7 | 25.3 | 30.4 | 28.3 | 1016.6561 | 3975.0879 | 5 | 9328.6616 | 4.9 | 114% | 19.5 | 4600 | 18.9 | 37.8 | 530.0311 | 28 | 251.3633 | 278.6678 | 2.0086 | 1.7619 | 3.0984
45618.3014 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 18.9 | 32 | 6 | -4 | 38 | 46.2 | 1.8 | 4.6 | 11 | 182 | 44 | -3.1 | -4.1 | 28.2 | 26 | 31 | 416 | 0 | 0 | 13.6 | 13.1 | 550 | 50.3 | Room | On | 28.1 | 26 | 31 | 28.5 | 1016.5706 | 3976.7338 | 5 | 9466.4935 | 4.9 | 114% | 19.3 | 4600 | 18.9 | 38 | 530.3008 | 28.2 | 251.7466 | 278.5542 | 2.0391 | 1.7887 | 3.15
45618.3015 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 18.9 | 32 | 6 | -4 | 38.2 | 46.4 | 1.8 | 4.6 | 11 | 182 | 44 | -3.1 | -4.1 | 28.3 | 25.8 | 31 | 403 | 0 | 0 | 13.7 | 13.2 | 550 | 50.3 | Room | On | 28.1 | 26 | 31 | 28.4 | 1016.6134 | 3976.7338 | 5.2 | 9845.5676 | 4.9 | 114% | 19.3 | 4600 | 18.9 | 38.2 | 530.5706 | 28.3 | 251.9383 | 278.6322 | 2.1201 | 1.8598 | 3.15
45618.3016 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 19.1 | 32 | 6 | -4 | 38.4 | 46.8 | 1.8 | 4.6 | 11 | 182 | 44 | -3.1 | -4.1 | 28.3 | 26 | 31 | 403 | 0 | 0 | 13.8 | 13.2 | 540 | 50.3 | Room | On | 28.1 | 26 | 31 | 28.5 | 1016.5706 | 3976.7338 | 5 | 9466.4935 | 4.9 | 114% | 19.3 | 4600 | 19.1 | 38.4 | 530.2613 | 28.3 | 251.9372 | 278.324 | 2.0407 | 1.7901 | 3.1833
45618.3017 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 19.2 | 33 | 6.1 | -4 | 38.6 | 47.1 | 1.8 | 4.6 | 11 | 182 | 44 | -3.2 | -4.1 | 28.5 | 26.4 | 31.5 | 403 | 0 | 0 | 13.8 | 13.3 | 540 | 50.3 | Room | On | 28.1 | 26 | 31 | 28.95 | 1016.3773 | 3976.7338 | 5.1 | 9653.9877 | 5 | 114% | 18.8 | 4600 | 19.2 | 38.6 | 530.2427 | 28.5 | 252.3205 | 277.9222 | 2.0842 | 1.8282 | 3.1475
45618.3018 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 19.2 | 33 | 6.1 | -4 | 39 | 47.3 | 1.8 | 4.6 | 11 | 182 | 44 | -3.2 | -4.2 | 28.7 | 26.4 | 31.5 | 403 | 0 | 0 | 13.9 | 13.4 | 550 | 50.3 | Room | On | 27.9 | 26.4 | 31.5 | 28.95 | 1016.3773 | 3977.6743 | 5.1 | 9587.543 | 5 | 114% | 18.8 | 4600 | 19.2 | 39 | 530.7868 | 28.7 | 252.7043 | 278.0824 | 2.0686 | 1.8146 | 3.1475
45618.3019 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 19.2 | 33 | 6.1 | -4 | 39.2 | 47.6 | 1.8 | 4.6 | 11 | 182 | 44 | -3.1 | -4.1 | 28.8 | 26.4 | 31.7 | 403 | 0 | 0 | 13.9 | 13.4 | 540 | 50.3 | Room | On | 27.9 | 26.4 | 31.5 | 29.05 | 1016.3342 | 3977.6743 | 5.3 | 9963.1026 | 4.9 | 114% | 18.6 | 4600 | 19.2 | 39.2 | 531.0588 | 28.8 | 252.8962 | 278.1626 | 2.1491 | 1.8851 | 3.1475
45618.3021 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 19.4 | 33 | 6.1 | -4 | 39.4 | 47.8 | 1.8 | 4.7 | 11 | 182 | 44 | -3.1 | -4.1 | 28.8 | 26.7 | 31.8 | 403 | 0 | 0 | 14 | 13.5 | 550 | 50.3 | Room | On | 27.9 | 26.4 | 31.5 | 29.25 | 1016.2479 | 3977.6743 | 5.1 | 9586.3217 | 4.9 | 114% | 18.5 | 4700 | 19.4 | 39.4 | 530.755 | 28.8 | 252.8959 | 277.8591 | 2.07 | 1.8158 | 3.1803
45618.3022 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 19.4 | 33 | 6.1 | -4 | 39.6 | 48.1 | 1.8 | 4.7 | 11 | 182 | 44 | -3 | -4.1 | 29.1 | 26.7 | 32 | 392 | 0 | 0 | 14 | 13.6 | 550 | 50.3 | Room | On | 27.9 | 26.4 | 31.5 | 29.35 | 1016.2046 | 3977.6743 | 5.3 | 9961.8318 | 4.8 | 114% | 18.3 | 4700 | 19.4 | 39.6 | 531.0286 | 29.1 | 253.4721 | 277.5565 | 2.1535 | 1.889 | 3.1803
45618.3023 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 19.4 | 33 | 6.1 | -4 | 39.8 | 48.3 | 1.9 | 4.7 | 11 | 182 | 45 | -3 | -4 | 29.1 | 26.7 | 32 | 392 | 0 | 0 | 14.1 | 13.7 | 550 | 50.3 | Room | On | 27.9 | 26.7 | 32 | 29.35 | 1016.2046 | 3978.3797 | 5.3 | 9963.5984 | 4.9 | 114% | 18.3 | 4700 | 19.4 | 39.8 | 531.3022 | 29.1 | 253.4721 | 277.8301 | 2.1517 | 1.8875 | 3.1803
45618.3024 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 19.6 | 33 | 6.1 | -4 | 40 | 48.6 | 1.9 | 4.7 | 11 | 182 | 45 | -3 | -4 | 29.1 | 27.1 | 32.2 | 392 | 0 | 0 | 14.2 | 13.7 | 550 | 50.3 | Room | On | 27.9 | 26.7 | 32 | 29.65 | 1016.0745 | 3978.3797 | 5.1 | 9586.3857 | 4.9 | 114% | 18.1 | 4700 | 19.6 | 40 | 531.0016 | 29.1 | 253.4722 | 277.5294 | 2.0725 | 1.818 | 3.2131
45618.3025 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 19.7 | 33 | 6.1 | -4 | 40.1 | 49 | 2 | 4.7 | 12 | 182 | 45 | -3 | -4 | 29.1 | 27.1 | 32.3 | 392 | 0 | 0 | 14.2 | 13.8 | 550 | 50.3 | Room | On | 27.9 | 26.7 | 32 | 29.7 | 1016.0527 | 3978.3797 | 5.2 | 9774.1449 | 5 | 114% | 18 | 4700 | 19.7 | 40.1 | 530.8514 | 29.1 | 253.4722 | 277.3792 | 2.1142 | 1.8546 | 3.2295
45618.3026 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 19.7 | 33 | 6.1 | -4 | 40.1 | 49 | 2 | 4.7 | 12 | 182 | 45 | -3 | -4 | 29.1 | 27.1 | 32.3 | 392 | 0 | 0 | 14.2 | 13.8 | 550 | 50.3 | Room | On | 27.9 | 26.7 | 32 | 29.7 | 1016.0527 | 3978.3797 | 5.2 | 9774.1449 | 5 | 114% | 18 | 4700 | 19.7 | 40.1 | 530.8514 | 29.1 | 253.4722 | 277.3792 | 2.1142 | 1.8546 | 3.2295
45618.3028 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 19.8 | 34 | 6.1 | -4 | 40.3 | 49.1 | 2 | 4.8 | 12 | 182 | 45 | -3 | -4.1 | 29.1 | 27.6 | 32.6 | 392 | 0 | 0 | 14.3 | 13.8 | 550 | 50.3 | Room | On | 27.9 | 27.6 | 32.6 | 30.1 | 1015.8783 | 3980.4959 | 5 | 9401.6012 | 5 | 114% | 17.7 | 4800 | 19.8 | 40.3 | 530.8396 | 29.1 | 253.4723 | 277.3673 | 2.0338 | 1.784 | 3.2459
45618.3029 | On | Off | Off | Off | On | Normal Operation | 54 | 54 | 54 | 19.8 | 34 | 6.1 | -4 | 40.6 | 49.3 | 2 | 4.8 | 12 | 182 | 45 | -3 | -4.1 | 29.2 | 27.6 | 32.7 | 383 | 0 | 0 | 14.3 | 13.9 | 550 | 50.2 | Room | On | 27.7 | 27.6 | 32.6 | 30.15 | 1015.8564 | 3980.4959 | 5.1 | 9520.6854 | 5 | 108% | 17.5 | 4800 | 19.8 | 40.6 | 531.2547 | 29.2 | 253.6646 | 277.59 | 2.0579 | 1.9054 | 3.2459
45618.303 | On | Off | Off | Off | On | Normal Operation | 54 | 54 | 54 | 19.7 | 33 | 6.1 | -4 | 40.8 | 49.6 | 2 | 4.5 | 11 | 182 | 45 | -3 | -4.1 | 29.3 | 27.6 | 32.8 | 383 | 0 | 0 | 14.4 | 14 | 540 | 50.2 | Room | On | 27.7 | 27.6 | 32.6 | 30.2 | 1015.8346 | 3980.4959 | 5.2 | 9707.1564 | 5 | 108% | 17.4 | 4500 | 19.7 | 40.8 | 531.8172 | 29.3 | 253.8568 | 277.9604 | 2.0954 | 1.9402 | 3.2295
45618.3031 | On | Off | Off | Off | On | Normal Operation | 54 | 54 | 54 | 19.7 | 33 | 6.1 | -4 | 41 | 50 | 2 | 4.5 | 11 | 182 | 45 | -3 | -4 | 29.5 | 27.5 | 32.7 | 383 | 0 | 0 | 14.4 | 14 | 550 | 50.2 | Room | On | 27.7 | 27.6 | 32.6 | 30.1 | 1015.8783 | 3980.4959 | 5.2 | 9707.5744 | 5 | 108% | 17.5 | 4500 | 19.7 | 41 | 532.0931 | 29.5 | 254.2414 | 277.8518 | 2.0963 | 1.941 | 3.2295
45618.3032 | On | Off | Off | Off | On | Normal Operation | 54 | 54 | 54 | 19.7 | 33 | 6.2 | -3 | 41.2 | 50.1 | 2 | 4.5 | 11 | 182 | 45 | -2.9 | -3.9 | 29.5 | 27.7 | 32.7 | 383 | 0 | 0 | 14.5 | 14.1 | 550 | 50.2 | Room | On | 27.7 | 27.6 | 32.6 | 30.2 | 1015.8346 | 3980.4959 | 5 | 9333.8043 | 4.9 | 108% | 17.5 | 4500 | 19.7 | 41.2 | 532.3691 | 29.5 | 254.2414 | 278.1277 | 2.0136 | 1.8644 | 3.1774
45618.3033 | On | Off | Off | Off | On | Normal Operation | 54 | 54 | 54 | 19.8 | 34 | 6.2 | -3 | 41.4 | 50.2 | 2 | 4.5 | 12 | 182 | 45 | -2.9 | -3.9 | 29.5 | 27.7 | 32.7 | 383 | 0 | 0 | 14.5 | 14.1 | 550 | 50.2 | Room | On | 27.7 | 27.7 | 32.7 | 30.2 | 1015.8346 | 3980.731 | 5 | 9334.3556 | 4.9 | 108% | 17.5 | 4500 | 19.8 | 41.4 | 532.3616 | 29.5 | 254.2417 | 278.1199 | 2.0137 | 1.8646 | 3.1935
45618.3034 | On | Off | Off | Off | On | Normal Operation | 54 | 54 | 54 | 20 | 34 | 6.2 | -3 | 41.6 | 50.3 | 2 | 4.5 | 12 | 182 | 45 | -2.8 | -3.9 | 29.7 | 28.1 | 33 | 383 | 0 | 0 | 14.6 | 14.2 | 550 | 50.2 | Room | On | 27.7 | 27.7 | 32.7 | 30.55 | 1015.681 | 3980.731 | 4.9 | 9146.2858 | 4.8 | 108% | 17.2 | 4500 | 20 | 41.6 | 532.0709 | 29.7 | 254.6275 | 277.4434 | 1.978 | 1.8315 | 3.2258
45618.3036 | On | Off | Off | Off | On | Normal Operation | 54 | 54 | 54 | 20 | 34 | 6.2 | -3 | 41.8 | 50.5 | 2 | 4.5 | 12 | 182 | 45 | -2.8 | -3.8 | 30 | 28.2 | 33.1 | 371 | 0 | 0 | 14.6 | 14.3 | 550 | 50.2 | Room | On | 27.7 | 27.7 | 32.7 | 30.65 | 1015.637 | 3980.731 | 4.9 | 9145.8896 | 4.8 | 108% | 17.1 | 4500 | 20 | 41.8 | 532.3492 | 30 | 255.205 | 277.1442 | 1.98 | 1.8334 | 3.2258
45618.3037 | On | Off | Off | Off | On | Normal Operation | 54 | 54 | 54 | 20 | 34 | 6.2 | -3 | 41.8 | 50.7 | 1.9 | 4.5 | 12 | 182 | 45 | -2.8 | -3.8 | 30.2 | 28.3 | 33.1 | 371 | 0 | 0 | 14.7 | 14.3 | 550 | 50.2 | Room | On | 27.7 | 27.7 | 32.7 | 30.7 | 1015.615 | 3980.731 | 4.8 | 8959.0446 | 4.7 | 108% | 17.1 | 4500 | 20 | 41.8 | 532.3492 | 30.2 | 255.59 | 276.7592 | 1.9423 | 1.7984 | 3.2258
45618.3038 | On | Off | Off | Off | On | Normal Operation | 54 | 54 | 54 | 20.2 | 34 | 6.2 | -3 | 42 | 50.7 | 1.9 | 4.5 | 12 | 182 | 46 | -2.8 | -3.8 | 30.3 | 28.6 | 33.3 | 371 | 0 | 0 | 14.7 | 14.3 | 550 | 50.3 | Room | On | 27.9 | 28.3 | 33.1 | 30.95 | 1015.5047 | 3982.1418 | 4.7 | 8837.9079 | 4.7 | 108% | 17 | 4500 | 20.2 | 42 | 532.0604 | 30.3 | 255.7845 | 276.2759 | 1.9194 | 1.7772 | 3.2581
45618.3039 | On | Off | Off | Off | On | Normal Operation | 54 | 54 | 54 | 20.2 | 34 | 6.2 | -3 | 42.2 | 50.8 | 1.9 | 4.5 | 12 | 182 | 46 | -2.8 | -3.8 | 30.5 | 28.7 | 33.5 | 371 | 0 | 0 | 14.7 | 14.4 | 550 | 50.3 | Room | On | 27.9 | 28.3 | 33.1 | 31.1 | 1015.4384 | 3982.1418 | 4.8 | 9025.3587 | 4.7 | 108% | 16.8 | 4500 | 20.2 | 42.2 | 532.3403 | 30.5 | 256.1698 | 276.1705 | 1.9608 | 1.8156 | 3.2581
45618.304 | On | Off | Off | Off | On | Normal Operation | 54 | 54 | 54 | 20.3 | 35 | 6.2 | -3 | 42.4 | 51 | 1.9 | 4.5 | 12 | 182 | 46 | -2.8 | -3.8 | 30.6 | 28.7 | 33.6 | 371 | 0 | 0 | 14.8 | 14.4 | 550 | 50.3 | Room | On | 27.9 | 28.3 | 33.1 | 31.15 | 1015.4162 | 3982.1418 | 4.9 | 9213.1861 | 4.7 | 108% | 16.7 | 4500 | 20.3 | 42.4 | 532.3372 | 30.6 | 256.3636 | 275.9736 | 2.0031 | 1.8547 | 3.2742
45618.3041 | On | Off | Off | Off | On | Normal Operation | 54 | 54 | 54 | 20.4 | 35 | 6.2 | -3 | 42.4 | 51.2 | 1.9 | 4.5 | 12 | 182 | 46 | -2.8 | -3.8 | 30.6 | 28.8 | 33.6 | 371 | 0 | 700 | 14.8 | 14.5 | 550 | 50.3 | Room | On | 27.9 | 28.3 | 33.1 | 31.2 | 1015.394 | 3982.1418 | 4.8 | 9024.9649 | 4.7 | 108% | 16.7 | 4500 | 20.4 | 42.4 | 532.0535 | 30.6 | 256.3648 | 275.6886 | 1.9642 | 1.8187 | 3.2903
45618.3043 | On | Off | Off | Off | On | Normal Operation | 56 | 56 | 56 | 20.5 | 35 | 6.2 | -3 | 42.6 | 51.5 | 1.9 | 4.9 | 12 | 182 | 46 | -2.8 | -3.8 | 30.6 | 28.8 | 33.6 | 364 | 80 | 700 | 14.8 | 14.5 | 550 | 50.3 | Room | On | 27.9 | 28.8 | 33.6 | 31.2 | 1015.394 | 3983.3174 | 4.8 | 9027.6294 | 4.7 | 112% | 16.7 | 4900 | 20.5 | 42.6 | 532.0513 | 30.6 | 256.366 | 275.6853 | 1.9648 | 1.7543 | 3.3065
45618.3044 | On | Off | Off | Off | On | Normal Operation | 56 | 56 | 56 | 20.5 | 35 | 6.2 | -3 | 42.6 | 51.5 | 1.9 | 4.9 | 12 | 182 | 46 | -2.8 | -3.8 | 30.7 | 29.1 | 33.7 | 364 | 80 | 2000 | 14.8 | 14.5 | 550 | 50.3 | Room | On | 27.9 | 28.8 | 33.6 | 31.4 | 1015.3053 | 3983.3174 | 4.6 | 8650.7218 | 4.7 | 112% | 16.6 | 4900 | 20.5 | 42.6 | 532.0513 | 30.7 | 256.5589 | 275.4924 | 1.8841 | 1.6822 | 3.3065
45618.3045 | On | Off | Off | Off | On | Normal Operation | 56 | 56 | 56 | 20.9 | 36 | 6.2 | -3 | 42.8 | 51.7 | 1.9 | 5.2 | 13 | 182 | 46 | -2.8 | -3.8 | 31 | 29.2 | 34.2 | 364 | 150 | 2000 | 11.4 | 16.4 | 550 | 50.3 | Room | On | 27.9 | 28.8 | 33.6 | 31.7 | 1015.1717 | 3983.3174 | 5 | 9401.7213 | 4.7 | 112% | 16.1 | 5200 | 20.9 | 42.8 | 531.1953 | 31 | 257.1436 | 274.0517 | 2.0584 | 1.8378 | 3.371
45618.3046 | On | Off | Off | Off | On | Normal Operation | 56 | 56 | 56 | 20.9 | 36 | 6.1 | -4 | 43.3 | 52.1 | 1.9 | 5.3 | 14 | 182 | 46 | -2.9 | -3.8 | 31.7 | 29.3 | 34.7 | 364 | 150 | 2000 | 9.6 | 20.8 | 550 | 50.3 | Room | On | 27.9 | 28.8 | 33.6 | 32 | 1015.0376 | 3983.3174 | 5.4 | 10152.5178 | 4.8 | 112% | 15.6 | 5300 | 20.9 | 43.3 | 531.9092 | 31.7 | 258.4959 | 273.4133 | 2.2279 | 1.9892 | 3.4262
45618.3047 | On | Off | Off | Off | On | Normal Operation | 56 | 56 | 56 | 20.9 | 36 | 6.1 | -4 | 43.8 | 52.6 | 1.9 | 5.4 | 14 | 182 | 46 | -3.1 | -3.9 | 32.2 | 29.3 | 34.7 | 364 | 150 | 2000 | 10 | 24.1 | 550 | 50.3 | Room | On | 27.7 | 29.3 | 34.7 | 32 | 1015.0376 | 3984.4931 | 5.4 | 10082.7149 | 5 | 112% | 15.6 | 5400 | 20.9 | 43.8 | 532.6232 | 32.2 | 259.4618 | 273.1613 | 2.2147 | 1.9774 | 3.4262
45618.3048 | On | Off | Off | Off | On | Normal Operation | 56 | 56 | 56 | 20.9 | 36 | 6.1 | -4 | 44.4 | 53 | 1.9 | 5.5 | 14 | 182 | 45 | -3.1 | -4 | 32.5 | 29.5 | 34.8 | 364 | 150 | 2000 | 11 | 24.5 | 550 | 50.3 | Room | On | 27.7 | 29.3 | 34.7 | 32.15 | 1014.9704 | 3984.4931 | 5.3 | 9895.3425 | 5 | 112% | 15.5 | 5500 | 20.9 | 44.4 | 533.4799 | 32.5 | 260.0414 | 273.4385 | 2.1713 | 1.9387 | 3.4262
45618.305 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 21 | 36 | 6.1 | -4 | 45 | 53.4 | 1.9 | 5.5 | 14 | 182 | 44 | -3.1 | -4 | 32.7 | 29.7 | 34.8 | 353 | 150 | 2000 | 11.7 | 24.7 | 550 | 50.3 | Room | On | 27.7 | 29.3 | 34.7 | 32.25 | 1014.9255 | 3984.4931 | 5.1 | 9521.5122 | 5 | 114% | 15.5 | 5500 | 21 | 45 | 534.0593 | 32.7 | 260.4306 | 273.6287 | 2.0878 | 1.8314 | 3.4426
45618.3051 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 21 | 36 | 6.1 | -4 | 45.6 | 54 | 1.9 | 5.5 | 14 | 182 | 44 | -3 | -4 | 32.8 | 29.7 | 35 | 353 | 150 | 2000 | 11.8 | 25.6 | 550 | 50.3 | Room | On | 27.7 | 29.3 | 34.7 | 32.35 | 1014.8805 | 3984.4931 | 5.3 | 9894.4666 | 4.9 | 114% | 15.3 | 5500 | 21 | 45.6 | 534.9185 | 32.8 | 260.6238 | 274.2947 | 2.1643 | 1.8985 | 3.4426
45618.3052 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 21.2 | 36 | 6.1 | -4 | 46.2 | 54.5 | 1.8 | 5.5 | 14 | 182 | 44 | -3 | -4 | 33.1 | 30 | 35.1 | 353 | 150 | 2000 | 11.7 | 26.7 | 540 | 50.3 | Room | On | 28.1 | 29.7 | 35 | 32.55 | 1014.7905 | 3985.4336 | 5.1 | 9660.0017 | 4.8 | 114% | 15.2 | 5500 | 21.2 | 46.2 | 535.231 | 33.1 | 261.2098 | 274.0211 | 2.1152 | 1.8554 | 3.4754
45618.3053 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 21.2 | 36 | 6.1 | -4 | 46.8 | 55.1 | 1.8 | 5.5 | 14 | 182 | 43 | -3 | -4 | 33.2 | 30 | 35.2 | 353 | 150 | 2000 | 11.7 | 27.7 | 550 | 50.3 | Room | On | 28.1 | 29.7 | 35 | 32.6 | 1014.7679 | 3985.4336 | 5.2 | 9849.1946 | 4.8 | 114% | 15.1 | 5500 | 21.2 | 46.8 | 536.0951 | 33.2 | 261.4032 | 274.6919 | 2.1513 | 1.8871 | 3.4754
45618.3054 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 21.3 | 36 | 6.1 | -4 | 47.3 | 55.6 | 1.8 | 5.5 | 14 | 182 | 43 | -3 | -4 | 33.3 | 30.2 | 35.4 | 353 | 150 | 2000 | 11.7 | 28.5 | 550 | 50.3 | Room | On | 28.1 | 29.7 | 35 | 32.8 | 1014.6776 | 3985.4336 | 5.2 | 9848.3177 | 4.8 | 114% | 14.9 | 5500 | 21.3 | 47.3 | 536.5454 | 33.3 | 261.5999 | 274.9455 | 2.1491 | 1.8852 | 3.4918
45618.3055 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 21.4 | 37 | 6.1 | -4 | 47.6 | 56.1 | 1.7 | 5.6 | 14 | 182 | 43 | -3 | -4 | 33.5 | 30.3 | 35.5 | 353 | 150 | 2000 | 11.7 | 29 | 550 | 50.3 | Room | On | 28.1 | 29.7 | 35 | 32.9 | 1014.6323 | 3985.4336 | 5.2 | 9847.8785 | 4.7 | 114% | 14.8 | 5600 | 21.4 | 47.6 | 536.7095 | 33.5 | 261.9903 | 274.7193 | 2.1508 | 1.8867 | 3.5082
45618.3056 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 21.4 | 37 | 6.1 | -4 | 48.1 | 56.5 | 1.7 | 5.6 | 14 | 179 | 43 | -3.1 | -4 | 33.6 | 30.4 | 35.7 | 353 | 150 | 2000 | 11.7 | 29.5 | 550 | 50.4 | Room | On | 27.7 | 30.3 | 35.5 | 33.05 | 1014.5643 | 3986.8444 | 5.3 | 9897.2208 | 4.8 | 114% | 14.7 | 5600 | 21.4 | 48.1 | 537.4338 | 33.6 | 262.1838 | 275.25 | 2.1574 | 1.8925 | 3.5082
45618.3058 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 21.4 | 37 | 6.1 | -4 | 48.5 | 57 | 1.7 | 5.6 | 14 | 179 | 43 | -3.1 | -4 | 33.6 | 30.5 | 35.7 | 353 | 150 | 2000 | 11.6 | 29.8 | 550 | 50.4 | Room | On | 27.7 | 30.3 | 35.5 | 33.1 | 1014.5416 | 3986.8444 | 5.2 | 9710.2636 | 4.8 | 114% | 14.7 | 5600 | 21.4 | 48.5 | 538.0132 | 33.6 | 262.1838 | 275.8294 | 2.1122 | 1.8528 | 3.5082
45618.3059 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 21.4 | 37 | 6.1 | -4 | 48.5 | 57 | 1.7 | 5.6 | 14 | 179 | 43 | -3.1 | -4 | 33.6 | 30.5 | 35.7 | 353 | 150 | 2000 | 11.6 | 29.8 | 550 | 50.4 | Room | On | 27.7 | 30.3 | 35.5 | 33.1 | 1014.5416 | 3986.8444 | 5.2 | 9710.2636 | 4.8 | 114% | 14.7 | 5600 | 21.4 | 48.5 | 538.0132 | 33.6 | 262.1838 | 275.8294 | 2.1122 | 1.8528 | 3.5082
45618.306 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 21.5 | 37 | 6.1 | -4 | 49 | 57.5 | 1.7 | 5.6 | 14 | 179 | 44 | -3.1 | -4 | 33.7 | 30.6 | 35.8 | 353 | 150 | 2000 | 11.6 | 30.1 | 550 | 50.4 | Room | On | 27.7 | 30.3 | 35.5 | 33.2 | 1014.4962 | 3986.8444 | 5.2 | 9709.8289 | 4.8 | 114% | 14.6 | 5600 | 21.5 | 49 | 538.4735 | 33.7 | 262.3809 | 276.0926 | 2.1101 | 1.851 | 3.5246
45618.3061 | On | Off | Off | Off | On | Normal Operation | 57 | 57 | 57 | 21.5 | 37 | 6.1 | -4 | 49.1 | 57.8 | 1.7 | 5.6 | 14 | 179 | 44 | -3 | -4 | 33.8 | 30.6 | 36 | 353 | 150 | 2000 | 11.6 | 30.3 | 550 | 50.4 | Room | On | 27.9 | 30.6 | 36 | 33.3 | 1014.4507 | 3987.5498 | 5.4 | 10157.4288 | 4.7 | 114% | 14.4 | 5600 | 21.5 | 49.1 | 538.6188 | 33.8 | 262.5746 | 276.0442 | 2.2078 | 1.9367 | 3.5246
45618.3062 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 21.6 | 37 | 6.1 | -4 | 49.5 | 58.2 | 1.7 | 5.6 | 14 | 179 | 44 | -3 | -4 | 34 | 30.8 | 36.1 | 353 | 150 | 2000 | 11.7 | 30.5 | 550 | 50.4 | Room | On | 27.9 | 30.6 | 36 | 33.45 | 1014.3824 | 3987.5498 | 5.3 | 9968.6569 | 4.7 | 114% | 14.3 | 5600 | 21.6 | 49.5 | 538.9373 | 34 | 262.9656 | 275.9717 | 2.1673 | 1.9012 | 3.541
45618.3063 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 21.7 | 37 | 6.1 | -4 | 49.8 | 58.5 | 1.7 | 5.7 | 14 | 179 | 44 | -3 | -4 | 34.1 | 31 | 36.2 | 353 | 150 | 2000 | 11.9 | 30.7 | 550 | 50.4 | Room | On | 27.9 | 30.6 | 36 | 33.6 | 1014.314 | 3987.5498 | 5.2 | 9779.909 | 4.7 | 114% | 14.2 | 5700 | 21.7 | 49.8 | 539.1125 | 34.1 | 263.1632 | 275.9493 | 2.1265 | 1.8653 | 3.5574
45618.3065 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 21.8 | 37 | 6.1 | -4 | 50.1 | 58.8 | 1.7 | 5.7 | 15 | 179 | 45 | -3 | -4 | 34.2 | 31.1 | 36.4 | 353 | 150 | 2000 | 12.2 | 31 | 550 | 50.4 | Room | On | 27.9 | 30.6 | 36 | 33.75 | 1014.2454 | 3987.5498 | 5.3 | 9967.3102 | 4.7 | 114% | 14 | 5700 | 21.8 | 50.1 | 539.2896 | 34.2 | 263.3609 | 275.9287 | 2.1674 | 1.9012 | 3.5738
45618.3066 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 21.9 | 38 | 6.1 | -4 | 50.3 | 59.1 | 1.7 | 5.7 | 14 | 179 | 45 | -3 | -4 | 34.4 | 31.4 | 36.7 | 353 | 150 | 2000 | 12.4 | 31.2 | 550 | 50.4 | Room | On | 27.7 | 31.1 | 36.4 | 34.05 | 1014.1078 | 3988.7254 | 5.3 | 9897.4353 | 4.7 | 114% | 13.7 | 5700 | 21.9 | 50.3 | 539.3217 | 34.4 | 263.7527 | 275.569 | 2.155 | 1.8903 | 3.5902
45618.3067 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 21.9 | 38 | 6.1 | -4 | 50.6 | 59.5 | 1.7 | 5.7 | 15 | 179 | 45 | -3 | -4 | 34.5 | 31.4 | 36.7 | 353 | 150 | 2000 | 12.5 | 31.5 | 550 | 50.4 | Room | On | 27.7 | 31.1 | 36.4 | 34.05 | 1014.1078 | 3988.7254 | 5.3 | 9897.4353 | 4.7 | 114% | 13.7 | 5700 | 21.9 | 50.6 | 539.7626 | 34.5 | 263.9466 | 275.8159 | 2.1531 | 1.8886 | 3.5902
45618.3068 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 22.1 | 38 | 6.1 | -4 | 50.8 | 59.8 | 1.6 | 5.8 | 15 | 179 | 45 | -3.1 | -4 | 34.7 | 31.7 | 37 | 353 | 150 | 2000 | 12.6 | 31.5 | 550 | 50.4 | Room | On | 27.7 | 31.1 | 36.4 | 34.35 | 1013.9698 | 3988.7254 | 5.3 | 9896.0881 | 4.7 | 114% | 13.4 | 5800 | 22.1 | 50.8 | 539.537 | 34.7 | 264.3431 | 275.1939 | 2.1576 | 1.8927 | 3.623
45618.3069 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 22 | 38 | 6.1 | -4 | 51.2 | 60.1 | 1.6 | 5.7 | 15 | 179 | 46 | -3.1 | -4.1 | 34.8 | 31.7 | 37 | 353 | 150 | 2000 | 12.7 | 31.8 | 550 | 50.4 | Room | On | 27.7 | 31.1 | 36.4 | 34.35 | 1013.9698 | 3988.7254 | 5.3 | 9896.0881 | 4.7 | 114% | 13.4 | 5700 | 22 | 51.2 | 540.3866 | 34.8 | 264.5329 | 275.8537 | 2.1525 | 1.8881 | 3.6066
45618.307 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 22.1 | 38 | 6.1 | -4 | 51.5 | 60.3 | 1.6 | 5.7 | 15 | 179 | 46 | -3.1 | -4.1 | 34.8 | 31.7 | 37 | 349 | 150 | 2000 | 12.7 | 31.8 | 540 | 50.4 | Room | On | 27.9 | 31.7 | 37 | 34.35 | 1013.9698 | 3990.1362 | 5.3 | 9971.0655 | 4.7 | 114% | 13.4 | 5700 | 22.1 | 51.5 | 540.5716 | 34.8 | 264.5372 | 276.0344 | 2.1674 | 1.9012 | 3.623
45618.3072 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 22.2 | 38 | 6.1 | -4 | 52 | 60.6 | 1.6 | 5.8 | 15 | 179 | 46 | -3.1 | -4.1 | 35 | 31.8 | 37.1 | 349 | 159 | 2000 | 12.7 | 32 | 560 | 50.4 | Room | On | 27.9 | 31.7 | 37 | 34.45 | 1013.9237 | 3990.1362 | 5.3 | 9970.6119 | 4.7 | 114% | 13.3 | 5800 | 22.2 | 52 | 541.0551 | 35 | 264.9299 | 276.1252 | 2.1665 | 1.9005 | 3.6393
45618.3073 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 22.3 | 38 | 6.1 | -4 | 52.3 | 61 | 1.6 | 5.8 | 15 | 181 | 46 | -3.1 | -4 | 35.1 | 32.1 | 37.2 | 349 | 159 | 2000 | 13 | 32.1 | 540 | 50.4 | Room | On | 27.9 | 31.7 | 37 | 34.65 | 1013.8313 | 3990.1362 | 5.1 | 9593.4879 | 4.7 | 114% | 13.2 | 5800 | 22.3 | 52.3 | 541.245 | 35.1 | 265.1287 | 276.1163 | 2.0847 | 1.8287 | 3.6557
45618.3074 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 22.3 | 38 | 6.1 | -4 | 52.3 | 61 | 1.6 | 5.8 | 15 | 181 | 46 | -3.1 | -4 | 35.1 | 32.1 | 37.2 | 349 | 159 | 2000 | 13 | 32.1 | 540 | 50.4 | Room | On | 27.9 | 31.7 | 37 | 34.65 | 1013.8313 | 3990.1362 | 5.1 | 9593.4879 | 4.7 | 114% | 13.2 | 5800 | 22.3 | 52.3 | 541.245 | 35.1 | 265.1287 | 276.1163 | 2.0847 | 1.8287 | 3.6557
45618.3075 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 22.4 | 38 | 6.1 | -4 | 52.5 | 61.1 | 1.6 | 5.8 | 15 | 181 | 46 | -3.1 | -4 | 35.2 | 32.2 | 37.4 | 349 | 159 | 2000 | 13.2 | 32.1 | 550 | 50.4 | Room | On | 27.9 | 32.2 | 37.4 | 34.8 | 1013.7618 | 3991.3119 | 5.2 | 9783.8072 | 4.7 | 114% | 13 | 5800 | 22.4 | 52.5 | 541.2878 | 35.2 | 265.3276 | 275.9601 | 2.1272 | 1.866 | 3.6721
45618.3076 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 22.5 | 39 | 6.1 | -4 | 52.8 | 61.4 | 1.6 | 5.9 | 15 | 181 | 46 | -3.1 | -4 | 35.4 | 32.3 | 37.5 | 349 | 166 | 2000 | 13.4 | 32.1 | 550 | 50.4 | Room | On | 27.9 | 32.2 | 37.4 | 34.9 | 1013.7154 | 3991.3119 | 5.2 | 9783.3596 | 4.7 | 114% | 12.9 | 5900 | 22.5 | 52.8 | 541.4812 | 35.4 | 265.7211 | 275.7601 | 2.1287 | 1.8673 | 3.6885
45618.3077 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 22.7 | 39 | 6.1 | -4 | 53 | 61.7 | 1.6 | 5.9 | 15 | 181 | 47 | -3 | -4 | 35.5 | 32.7 | 37.8 | 349 | 166 | 2000 | 13.5 | 32.2 | 550 | 50.4 | Room | On | 27.9 | 32.2 | 37.4 | 35.25 | 1013.5527 | 3991.3119 | 5.1 | 9593.6775 | 4.6 | 114% | 12.6 | 5900 | 22.7 | 53 | 541.2726 | 35.5 | 265.9253 | 275.3474 | 2.0905 | 1.8338 | 3.7213
45618.3078 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 22.6 | 39 | 6.1 | -4 | 53.2 | 61.8 | 1.6 | 5.9 | 15 | 181 | 47 | -3 | -4 | 35.7 | 32.6 | 38 | 349 | 166 | 2000 | 13.7 | 32.3 | 550 | 50.4 | Room | On | 27.9 | 32.2 | 37.4 | 35.3 | 1013.5294 | 3991.3119 | 5.4 | 10157.7779 | 4.6 | 114% | 12.4 | 5900 | 22.6 | 53.2 | 541.8266 | 35.7 | 266.3093 | 275.5173 | 2.2121 | 1.9404 | 3.7049
45618.308 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 22.6 | 39 | 6.1 | -4 | 53.5 | 62.1 | 1.7 | 5.9 | 15 | 181 | 47 | -3 | -4 | 35.8 | 32.6 | 38 | 349 | 166 | 2000 | 13.8 | 32.3 | 550 | 50.4 | Room | On | 28.1 | 32.6 | 38 | 35.3 | 1013.5294 | 3992.2524 | 5.4 | 10233.0043 | 4.7 | 114% | 12.4 | 5900 | 22.6 | 53.5 | 542.2765 | 35.8 | 266.5038 | 275.7727 | 2.2264 | 1.953 | 3.7049
45618.3081 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 22.6 | 39 | 6.1 | -4 | 53.7 | 62.4 | 1.6 | 5.9 | 15 | 181 | 47 | -3 | -4 | 35.8 | 32.6 | 38 | 349 | 174 | 2000 | 13.8 | 32.3 | 550 | 50.4 | Room | On | 28.1 | 32.6 | 38 | 35.3 | 1013.5294 | 3992.2524 | 5.4 | 10233.0043 | 4.6 | 114% | 12.4 | 5900 | 22.6 | 53.7 | 542.5764 | 35.8 | 266.5038 | 276.0726 | 2.224 | 1.9509 | 3.7049
45618.3082 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 22.7 | 39 | 6.1 | -4 | 54.1 | 62.5 | 1.6 | 6 | 15 | 181 | 47 | -3.1 | -4 | 35.8 | 32.8 | 38 | 349 | 174 | 2000 | 13.9 | 32.3 | 550 | 50.4 | Room | On | 28.1 | 32.6 | 38 | 35.4 | 1013.4827 | 3992.2524 | 5.2 | 9853.5505 | 4.7 | 114% | 12.4 | 6000 | 22.7 | 54.1 | 542.9269 | 35.8 | 266.5089 | 276.418 | 2.1388 | 1.8762 | 3.7213
45618.3083 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 22.8 | 39 | 6.1 | -4 | 54.3 | 62.7 | 1.6 | 6 | 15 | 181 | 47 | -3 | -4 | 36 | 33.1 | 38.2 | 349 | 174 | 2000 | 14.2 | 32.3 | 550 | 50.4 | Room | On | 28.1 | 32.6 | 38 | 35.65 | 1013.3658 | 3992.2524 | 5.1 | 9662.9446 | 4.6 | 114% | 12.2 | 6000 | 22.8 | 54.3 | 542.9787 | 36 | 266.9033 | 276.0754 | 2.1001 | 1.8422 | 3.7377
45618.3084 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 23 | 39 | 6.1 | -4 | 54.5 | 63 | 1.6 | 6 | 15 | 181 | 48 | -3 | -4 | 36.1 | 33.3 | 38.4 | 349 | 174 | 2000 | 14.3 | 32.5 | 550 | 50.4 | Room | On | 28.1 | 33.1 | 38.2 | 35.85 | 1013.2721 | 3993.428 | 5.1 | 9664.8958 | 4.6 | 114% | 12 | 6000 | 23 | 54.5 | 542.7824 | 36.1 | 267.1087 | 275.6738 | 2.1036 | 1.8452 | 3.7705
45618.3085 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 23 | 39 | 6.1 | -4 | 54.8 | 63.2 | 1.6 | 6 | 15 | 181 | 48 | -2.9 | -3.9 | 36.2 | 33.3 | 38.5 | 349 | 181 | 2000 | 14.4 | 32.7 | 550 | 50.4 | Room | On | 28.1 | 33.1 | 38.2 | 35.9 | 1013.2486 | 3993.428 | 5.2 | 9854.1753 | 4.5 | 114% | 11.9 | 6000 | 23 | 54.8 | 543.2375 | 36.2 | 267.3034 | 275.9341 | 2.1427 | 1.8796 | 3.7705
45618.3087 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 23 | 39 | 6.1 | -4 | 55.1 | 63.4 | 1.6 | 6 | 15 | 181 | 48 | -2.9 | -3.9 | 36.4 | 33.3 | 38.5 | 349 | 181 | 2000 | 14.5 | 32.8 | 550 | 50.4 | Room | On | 28.1 | 33.1 | 38.2 | 35.9 | 1013.2486 | 3993.428 | 5.2 | 9854.1753 | 4.5 | 114% | 11.9 | 6000 | 23 | 55.1 | 543.6926 | 36.4 | 267.693 | 275.9996 | 2.1422 | 1.8791 | 3.7705
45618.3088 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 23.1 | 40 | 6.1 | -4 | 55.3 | 63.5 | 1.6 | 6.1 | 16 | 180 | 48 | -2.9 | -4 | 36.5 | 33.6 | 38.7 | 349 | 181 | 2000 | 14.6 | 32.8 | 550 | 50.4 | Room | On | 28.1 | 33.1 | 38.2 | 36.15 | 1013.131 | 3993.428 | 5.1 | 9663.5504 | 4.5 | 114% | 11.7 | 6100 | 23.1 | 55.3 | 543.7498 | 36.5 | 267.8934 | 275.8564 | 2.1019 | 1.8437 | 3.7869
45618.3089 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 23.2 | 40 | 6.1 | -4 | 55.6 | 63.8 | 1.5 | 6.1 | 16 | 180 | 49 | -2.9 | -4 | 36.5 | 33.7 | 39 | 349 | 181 | 2000 | 14.7 | 32.8 | 550 | 50.4 | Room | On | 28.1 | 33.6 | 38.7 | 36.35 | 1013.0367 | 3994.6037 | 5.3 | 10044.5344 | 4.4 | 114% | 11.4 | 6100 | 23.2 | 55.6 | 543.9607 | 36.5 | 267.8991 | 276.0616 | 2.1831 | 1.915 | 3.8033
45618.309 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 23.2 | 40 | 6.1 | -4 | 55.6 | 63.8 | 1.5 | 6.1 | 16 | 180 | 49 | -2.9 | -4 | 36.5 | 33.7 | 39 | 349 | 189 | 2000 | 14.7 | 32.8 | 550 | 50.4 | Room | On | 28.1 | 33.6 | 38.7 | 36.35 | 1013.0367 | 3994.6037 | 5.3 | 10044.5344 | 4.4 | 114% | 11.4 | 6100 | 23.2 | 55.6 | 543.9607 | 36.5 | 267.8991 | 276.0616 | 2.1831 | 1.915 | 3.8033
45618.3091 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 23.1 | 40 | 6.1 | -4 | 56 | 64.1 | 1.5 | 6.1 | 15 | 180 | 49 | -2.9 | -4 | 36.7 | 33.7 | 39 | 345 | 189 | 2000 | 14.7 | 33.1 | 550 | 50.4 | Room | On | 28.1 | 33.6 | 38.7 | 36.35 | 1013.0367 | 3994.6037 | 5.3 | 10044.5344 | 4.4 | 114% | 11.4 | 6100 | 23.1 | 56 | 544.8147 | 36.7 | 268.2831 | 276.5316 | 2.1794 | 1.9118 | 3.7869
45618.3092 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 23.2 | 40 | 6.2 | -3 | 56.1 | 64.2 | 1.5 | 6.1 | 15 | 180 | 49 | -2.9 | -3.9 | 36.7 | 33.7 | 38.8 | 345 | 189 | 2000 | 14.8 | 33.1 | 550 | 50.4 | Room | On | 28.1 | 33.6 | 38.7 | 36.25 | 1013.0839 | 3994.6037 | 5.1 | 9665.9456 | 4.4 | 114% | 11.6 | 6100 | 23.2 | 56.1 | 544.7236 | 36.7 | 268.2889 | 276.4347 | 2.098 | 1.8403 | 3.7419
45618.3094 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 23.3 | 40 | 6.1 | -4 | 56.2 | 64.5 | 1.5 | 6.1 | 16 | 180 | 50 | -2.9 | -3.9 | 36.8 | 33.8 | 39.1 | 345 | 189 | 2000 | 15 | 33.1 | 550 | 50.5 | Room | On | 28.1 | 33.8 | 39.1 | 36.45 | 1012.9894 | 3995.0739 | 5.3 | 10045.2484 | 4.4 | 114% | 11.4 | 6100 | 23.3 | 56.2 | 544.6329 | 36.8 | 268.4897 | 276.1431 | 2.1826 | 1.9146 | 3.8197
45618.3095 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 23.5 | 40 | 6.1 | -4 | 56.5 | 64.7 | 1.5 | 6.1 | 16 | 180 | 50 | -2.9 | -3.9 | 37 | 34.1 | 39.1 | 345 | 196 | 2000 | 15.1 | 33.1 | 540 | 50.5 | Room | On | 28.1 | 33.8 | 39.1 | 36.6 | 1012.9185 | 3995.0739 | 5 | 9475.9855 | 4.4 | 114% | 11.4 | 6100 | 23.5 | 56.5 | 544.6063 | 37 | 268.8918 | 275.7145 | 2.0621 | 1.8089 | 3.8525
45618.3096 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 23.5 | 40 | 6.1 | -4 | 56.7 | 64.8 | 1.5 | 6.1 | 16 | 180 | 50 | -2.9 | -3.9 | 37.1 | 34.2 | 39.4 | 345 | 196 | 2000 | 15.3 | 33.1 | 550 | 50.5 | Room | On | 28.1 | 33.8 | 39.1 | 36.8 | 1012.8236 | 3995.0739 | 5.2 | 9854.1023 | 4.4 | 114% | 11.1 | 6100 | 23.5 | 56.7 | 544.9142 | 37.1 | 269.087 | 275.8272 | 2.1435 | 1.8803 | 3.8525
45618.3097 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 23.5 | 40 | 6.1 | -4 | 57 | 65.1 | 1.5 | 6.1 | 16 | 180 | 50 | -2.8 | -3.9 | 37.2 | 34.2 | 39.4 | 345 | 196 | 2000 | 15.4 | 33.1 | 550 | 50.5 | Room | On | 28.1 | 33.8 | 39.1 | 36.8 | 1012.8236 | 3995.0739 | 5.2 | 9854.1023 | 4.3 | 114% | 11.1 | 6100 | 23.5 | 57 | 545.3759 | 37.2 | 269.2821 | 276.0937 | 2.1415 | 1.8785 | 3.8525
45618.3098 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 23.6 | 40 | 6.1 | -4 | 57.3 | 65.2 | 1.5 | 6.2 | 16 | 180 | 50 | -2.8 | -3.9 | 37.2 | 34.2 | 39.4 | 347 | 196 | 2000 | 15.5 | 33.1 | 550 | 50.5 | Room | On | 28.1 | 34.2 | 39.4 | 36.8 | 1012.8236 | 3996.0145 | 5.2 | 9856.4222 | 4.3 | 114% | 11.1 | 6200 | 23.6 | 57.3 | 545.5976 | 37.2 | 269.2883 | 276.3093 | 2.1403 | 1.8775 | 3.8689
45618.3099 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 23.7 | 41 | 6.2 | -3 | 57.5 | 65.4 | 1.6 | 6.2 | 16 | 180 | 50 | -2.8 | -3.9 | 37.4 | 34.5 | 39.7 | 347 | 203 | 2000 | 15.6 | 33.1 | 550 | 50.5 | Room | On | 28.1 | 34.2 | 39.4 | 37.1 | 1012.681 | 3996.0145 | 5.2 | 9855.0339 | 4.4 | 114% | 10.8 | 6200 | 23.7 | 57.5 | 545.6667 | 37.4 | 269.6851 | 275.9816 | 2.1425 | 1.8794 | 3.8226
45618.31 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 23.8 | 41 | 6.2 | -3 | 57.6 | 65.7 | 1.6 | 6.2 | 16 | 180 | 51 | -2.8 | -3.9 | 37.5 | 34.7 | 39.8 | 347 | 203 | 2000 | 15.8 | 33.1 | 550 | 50.5 | Room | On | 28.1 | 34.2 | 39.4 | 37.25 | 1012.6095 | 3996.0145 | 5.1 | 9664.8314 | 4.4 | 114% | 10.7 | 6200 | 23.8 | 57.6 | 545.5818 | 37.5 | 269.8868 | 275.695 | 2.1034 | 1.8451 | 3.8387
45618.3102 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 23.9 | 41 | 6.2 | -3 | 58 | 65.8 | 1.6 | 6.2 | 16 | 180 | 51 | -2.8 | -3.8 | 37.5 | 35 | 39.8 | 347 | 203 | 2000 | 15.9 | 33.2 | 550 | 50.5 | Room | On | 28.1 | 34.2 | 39.4 | 37.4 | 1012.5378 | 3996.0145 | 4.8 | 9095.6684 | 4.4 | 114% | 10.7 | 6200 | 23.9 | 58 | 545.9645 | 37.5 | 269.8932 | 276.0712 | 1.9768 | 1.734 | 3.8548
45618.3103 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 24 | 41 | 6.2 | -3 | 58.1 | 66.1 | 1.6 | 6.3 | 16 | 180 | 51 | -2.7 | -3.8 | 37.8 | 35.1 | 40.1 | 347 | 203 | 2000 | 16.1 | 33.3 | 550 | 50.4 | Room | On | 28.1 | 35.1 | 40.1 | 37.6 | 1012.4421 | 3998.1306 | 5 | 9478.7759 | 4.3 | 114% | 10.3 | 6300 | 24 | 58.1 | 545.8818 | 37.8 | 270.4863 | 275.3955 | 2.0651 | 1.8115 | 3.871
45618.3104 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 24 | 41 | 6.2 | -3 | 58.2 | 66.2 | 1.6 | 6.3 | 16 | 179 | 51 | -2.7 | -3.8 | 38 | 35.1 | 40.1 | 347 | 210 | 2000 | 16.1 | 33.5 | 550 | 50.4 | Room | On | 28.1 | 35.1 | 40.1 | 37.6 | 1012.4421 | 3998.1306 | 5 | 9478.7759 | 4.3 | 114% | 10.3 | 6300 | 24 | 58.2 | 546.0379 | 38 | 270.8773 | 275.1606 | 2.0669 | 1.8131 | 3.871
45618.3105 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 24 | 41 | 6.2 | -3 | 58.5 | 66.4 | 1.6 | 6.3 | 16 | 179 | 51 | -2.7 | -3.8 | 38 | 35.1 | 40.1 | 347 | 210 | 2000 | 16.2 | 33.6 | 550 | 50.4 | Room | On | 28.1 | 35.1 | 40.1 | 37.6 | 1012.4421 | 3998.1306 | 5 | 9478.7759 | 4.3 | 114% | 10.3 | 6300 | 24 | 58.5 | 546.5064 | 38 | 270.8773 | 275.6291 | 2.0634 | 1.81 | 3.871
45618.3106 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 24.1 | 41 | 6.2 | -3 | 58.7 | 66.7 | 1.6 | 6.3 | 16 | 179 | 52 | -2.7 | -3.8 | 38 | 35.2 | 40.3 | 347 | 210 | 2000 | 16.2 | 33.6 | 550 | 50.4 | Room | On | 28.1 | 35.1 | 40.1 | 37.75 | 1012.3702 | 3998.1306 | 5.1 | 9667.6644 | 4.3 | 114% | 10.1 | 6300 | 24.1 | 58.7 | 546.5825 | 38 | 270.8841 | 275.6984 | 2.104 | 1.8456 | 3.8871
45618.3107 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 24.1 | 41 | 6.2 | -3 | 58.7 | 66.7 | 1.6 | 6.3 | 16 | 179 | 52 | -2.7 | -3.8 | 38 | 35.2 | 40.3 | 347 | 210 | 2000 | 16.2 | 33.6 | 550 | 50.4 | Room | On | 28.1 | 35.2 | 40.3 | 37.75 | 1012.3702 | 3998.3658 | 5.1 | 9668.233 | 4.3 | 114% | 10.1 | 6300 | 24.1 | 58.7 | 546.5825 | 38 | 270.8841 | 275.6984 | 2.1041 | 1.8457 | 3.8871
45618.3109 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 24.1 | 41 | 6.2 | -3 | 59 | 66.8 | 1.6 | 6.3 | 16 | 179 | 52 | -2.7 | -3.8 | 38.1 | 35.4 | 40.5 | 347 | 217 | 2000 | 16.3 | 33.6 | 550 | 50.4 | Room | On | 28.1 | 35.2 | 40.3 | 37.95 | 1012.2741 | 3998.3658 | 5.1 | 9667.3151 | 4.3 | 114% | 9.9 | 6300 | 24.1 | 59 | 547.0523 | 38.1 | 271.0797 | 275.9726 | 2.1018 | 1.8437 | 3.8871
45618.311 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 24 | 41 | 6.2 | -3 | 59.1 | 67.1 | 1.6 | 6.3 | 16 | 179 | 52 | -2.7 | -3.8 | 38.2 | 35.4 | 40.5 | 347 | 217 | 2000 | 16.3 | 33.7 | 550 | 50.4 | Room | On | 28.1 | 35.2 | 40.3 | 37.95 | 1012.2741 | 3998.3658 | 5.1 | 9667.3151 | 4.3 | 114% | 9.9 | 6300 | 24 | 59.1 | 547.4433 | 38.2 | 271.2684 | 276.1749 | 2.1003 | 1.8423 | 3.871
45618.3111 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 24.2 | 41 | 6.2 | -3 | 59.2 | 67.2 | 1.6 | 6.4 | 17 | 179 | 52 | -2.7 | -3.8 | 38.2 | 35.4 | 40.5 | 347 | 217 | 2000 | 16.4 | 33.7 | 550 | 50.4 | Room | On | 28.1 | 35.2 | 40.3 | 37.95 | 1012.2741 | 3998.3658 | 5.1 | 9667.3151 | 4.3 | 114% | 9.9 | 6400 | 24.2 | 59.2 | 547.1311 | 38.2 | 271.2823 | 275.8489 | 2.1027 | 1.8445 | 3.9032
45618.3112 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 24.3 | 42 | 6.2 | -3 | 59.4 | 67.4 | 1.6 | 6.4 | 17 | 179 | 52 | -2.7 | -3.7 | 38.2 | 35.7 | 40.8 | 345 | 217 | 2000 | 16.6 | 33.7 | 550 | 50.4 | Room | On | 28.1 | 35.7 | 40.8 | 38.25 | 1012.1295 | 3999.5414 | 5.1 | 9668.7764 | 4.3 | 114% | 9.6 | 6400 | 24.3 | 59.4 | 547.2113 | 38.2 | 271.2892 | 275.9221 | 2.1025 | 1.8443 | 3.9194
45618.3113 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 24.3 | 42 | 6.2 | -3 | 59.5 | 67.7 | 1.6 | 6.4 | 16 | 179 | 52 | -2.6 | -3.7 | 38.5 | 35.8 | 41 | 345 | 224 | 2000 | 16.7 | 33.8 | 550 | 50.4 | Room | On | 27.9 | 35.7 | 40.8 | 38.4 | 1012.057 | 3999.5414 | 5.2 | 9787.493 | 4.2 | 114% | 9.4 | 6400 | 24.3 | 59.5 | 547.3688 | 38.5 | 271.8765 | 275.4923 | 2.1316 | 1.8699 | 3.9194
45618.3114 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 24.4 | 42 | 6.2 | -3 | 59.7 | 67.8 | 1.6 | 6.4 | 17 | 179 | 53 | -2.6 | -3.7 | 38.5 | 35.8 | 41 | 345 | 224 | 2000 | 16.7 | 34 | 550 | 50.4 | Room | On | 27.9 | 35.7 | 40.8 | 38.4 | 1012.057 | 3999.5414 | 5.2 | 9787.493 | 4.2 | 114% | 9.4 | 6400 | 24.4 | 59.7 | 547.4507 | 38.5 | 271.8837 | 275.5671 | 2.1311 | 1.8693 | 3.9355
45618.3116 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 24.5 | 42 | 6.2 | -3 | 60 | 68 | 1.7 | 6.4 | 17 | 179 | 53 | -2.5 | -3.7 | 38.7 | 36.1 | 41.1 | 345 | 224 | 2000 | 16.8 | 34.1 | 550 | 50.4 | Room | On | 27.9 | 35.7 | 40.8 | 38.6 | 1011.9602 | 3999.5414 | 5 | 9410.1504 | 4.2 | 114% | 9.3 | 6400 | 24.5 | 60 | 547.6925 | 38.7 | 272.2826 | 275.4098 | 2.0501 | 1.7983 | 3.9516
45618.3117 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 24.5 | 42 | 6.2 | -3 | 60 | 68.1 | 1.7 | 6.4 | 17 | 179 | 53 | -2.5 | -3.6 | 38.8 | 36.1 | 41.1 | 345 | 224 | 2000 | 16.9 | 34.1 | 550 | 50.4 | Room | On | 27.9 | 35.7 | 40.8 | 38.6 | 1011.9602 | 3999.5414 | 5 | 9410.1504 | 4.2 | 114% | 9.3 | 6400 | 24.5 | 60 | 547.6925 | 38.8 | 272.4786 | 275.2139 | 2.0515 | 1.7996 | 3.9516
45618.3118 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 24.5 | 42 | 6.2 | -3 | 60.1 | 68.4 | 1.7 | 6.5 | 17 | 179 | 53 | -2.5 | -3.6 | 38.8 | 36.1 | 41.1 | 345 | 231 | 2000 | 17 | 34.2 | 550 | 50.4 | Room | On | 27.9 | 36.1 | 41.1 | 38.6 | 1011.9602 | 4000.4819 | 5 | 9412.3633 | 4.2 | 114% | 9.3 | 6500 | 24.5 | 60.1 | 547.8509 | 38.8 | 272.4786 | 275.3724 | 2.0508 | 1.799 | 3.9516
45618.3119 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 24.6 | 42 | 6.2 | -3 | 60.3 | 68.5 | 1.7 | 6.5 | 17 | 179 | 54 | -2.5 | -3.6 | 39 | 36.4 | 41.3 | 344 | 231 | 2000 | 17.1 | 34.2 | 550 | 50.4 | Room | On | 27.9 | 36.1 | 41.1 | 38.85 | 1011.8388 | 4000.4819 | 4.9 | 9223.0098 | 4.2 | 114% | 9.1 | 6500 | 24.6 | 60.3 | 547.9365 | 39 | 272.8779 | 275.0586 | 2.0119 | 1.7648 | 3.9677
45618.312 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 24.6 | 42 | 6.2 | -3 | 60.5 | 68.7 | 1.7 | 6.5 | 17 | 179 | 54 | -2.5 | -3.6 | 39 | 36.4 | 41.3 | 344 | 231 | 2000 | 17.3 | 34.2 | 550 | 50.4 | Room | On | 27.9 | 36.1 | 41.1 | 38.85 | 1011.8388 | 4000.4819 | 4.9 | 9223.0098 | 4.2 | 114% | 9.1 | 6500 | 24.6 | 60.5 | 548.2543 | 39 | 272.8779 | 275.3764 | 2.0095 | 1.7628 | 3.9677
45618.3121 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 24.7 | 42 | 6.2 | -3 | 60.6 | 68.7 | 1.7 | 6.5 | 17 | 179 | 54 | -2.6 | -3.6 | 39.1 | 36.4 | 41.5 | 344 | 231 | 2000 | 17.3 | 34.2 | 550 | 50.4 | Room | On | 27.9 | 36.1 | 41.1 | 38.95 | 1011.7901 | 4000.4819 | 5.1 | 9598.9977 | 4.3 | 114% | 8.9 | 6500 | 24.7 | 60.6 | 548.1828 | 39.1 | 273.0815 | 275.1013 | 2.0936 | 1.8365 | 3.9839
45618.3122 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 24.8 | 42 | 6.2 | -3 | 60.8 | 69 | 1.7 | 6.6 | 17 | 179 | 54 | -2.6 | -3.7 | 39.1 | 36.7 | 41.6 | 344 | 238 | 2000 | 17.4 | 34.2 | 550 | 50.4 | Room | On | 28.3 | 36.4 | 41.5 | 39.15 | 1011.6927 | 4001.1873 | 4.9 | 9355.5378 | 4.3 | 114% | 8.8 | 6600 | 24.8 | 60.8 | 548.2717 | 39.1 | 273.0892 | 275.1825 | 2.0399 | 1.7893 | 4
45618.3124 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 24.9 | 43 | 6.2 | -3 | 60.8 | 69 | 1.7 | 6.6 | 17 | 179 | 54 | -2.6 | -3.6 | 39.1 | 36.7 | 41.6 | 344 | 238 | 2000 | 17.6 | 34.4 | 540 | 50.4 | Room | On | 28.3 | 36.4 | 41.5 | 39.15 | 1011.6927 | 4001.1873 | 4.9 | 9355.5378 | 4.3 | 114% | 8.8 | 6600 | 24.9 | 60.8 | 548.0413 | 39.1 | 273.0968 | 274.9446 | 2.0416 | 1.7909 | 4.0161
45618.3125 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 24.9 | 43 | 6.2 | -3 | 60.8 | 69 | 1.7 | 6.6 | 17 | 179 | 54 | -2.6 | -3.6 | 39.2 | 36.8 | 41.8 | 344 | 238 | 2000 | 17.6 | 34.4 | 540 | 50.4 | Room | On | 28.3 | 36.4 | 41.5 | 39.3 | 1011.6194 | 4001.1873 | 5 | 9545.7761 | 4.3 | 114% | 8.6 | 6600 | 24.9 | 60.8 | 548.0413 | 39.2 | 273.293 | 274.7483 | 2.0846 | 1.8286 | 4.0161
45618.3126 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25 | 43 | 6.2 | -3 | 61 | 69.1 | 1.7 | 6.6 | 17 | 179 | 55 | -2.6 | -3.6 | 39.4 | 37 | 42 | 342 | 238 | 2000 | 17.8 | 34.5 | 550 | 50.4 | Room | On | 28.3 | 36.4 | 41.5 | 39.5 | 1011.5216 | 4001.1873 | 5 | 9544.8528 | 4.3 | 114% | 8.4 | 6600 | 25 | 61 | 548.132 | 39.4 | 273.6933 | 274.4388 | 2.0868 | 1.8305 | 4.0323
45618.3127 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.1 | 43 | 6.2 | -3 | 61.1 | 69.2 | 1.7 | 6.6 | 17 | 179 | 55 | -2.5 | -3.6 | 39.5 | 37 | 42.1 | 342 | 245 | 2000 | 17.8 | 34.7 | 550 | 50.4 | Room | On | 28.1 | 37 | 42.1 | 39.55 | 1011.4971 | 4002.5981 | 5.1 | 9670.1202 | 4.2 | 114% | 8.3 | 6600 | 25.1 | 61.1 | 548.0629 | 39.5 | 273.8975 | 274.1654 | 2.1163 | 1.8564 | 4.0484
45618.3128 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.1 | 43 | 6.2 | -3 | 61.2 | 69.4 | 1.7 | 6.6 | 17 | 179 | 55 | -2.5 | -3.6 | 39.5 | 37.1 | 42.1 | 342 | 245 | 2000 | 17.8 | 34.8 | 550 | 50.4 | Room | On | 28.1 | 37 | 42.1 | 39.6 | 1011.4726 | 4002.5981 | 5 | 9480.2803 | 4.2 | 114% | 8.3 | 6600 | 25.1 | 61.2 | 548.2241 | 39.5 | 273.8975 | 274.3266 | 2.0735 | 1.8189 | 4.0484
45618.3129 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.1 | 43 | 6.2 | -3 | 61.2 | 69.5 | 1.7 | 6.7 | 17 | 179 | 55 | -2.5 | -3.6 | 39.7 | 37.1 | 42.1 | 342 | 245 | 2000 | 18.1 | 34.8 | 550 | 50.4 | Room | On | 28.1 | 37 | 42.1 | 39.6 | 1011.4726 | 4002.5981 | 5 | 9480.2803 | 4.2 | 114% | 8.3 | 6700 | 25.1 | 61.2 | 548.2241 | 39.7 | 274.2902 | 273.9339 | 2.0765 | 1.8215 | 4.0484
45618.3131 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.3 | 43 | 6.2 | -3 | 61.4 | 69.7 | 1.7 | 6.7 | 17 | 179 | 55 | -2.5 | -3.5 | 39.8 | 37.4 | 42.4 | 342 | 245 | 2000 | 18.3 | 34.7 | 550 | 50.4 | Room | On | 28.1 | 37 | 42.1 | 39.9 | 1011.3252 | 4002.5981 | 5 | 9478.8991 | 4.2 | 114% | 8 | 6700 | 25.3 | 61.4 | 548.0883 | 39.8 | 274.5029 | 273.5854 | 2.0788 | 1.8235 | 4.0806
45618.3132 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.4 | 43 | 6.2 | -3 | 61.5 | 69.7 | 1.7 | 6.7 | 18 | 179 | 56 | -2.5 | -3.5 | 39.8 | 37.5 | 42.4 | 342 | 251 | 2000 | 18.5 | 34.7 | 550 | 50.4 | Room | On | 27.9 | 37.4 | 42.4 | 39.95 | 1011.3006 | 4003.5386 | 4.9 | 9225.1477 | 4.2 | 114% | 8 | 6700 | 25.4 | 61.5 | 548.0211 | 39.8 | 274.511 | 273.5101 | 2.0237 | 1.7752 | 4.0968
45618.3133 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.3 | 43 | 6.2 | -3 | 61.5 | 69.8 | 1.7 | 6.7 | 17 | 179 | 56 | -2.4 | -3.5 | 40 | 37.7 | 42.7 | 343 | 251 | 2000 | 18.6 | 34.8 | 550 | 50.4 | Room | On | 27.9 | 37.4 | 42.4 | 40.2 | 1011.1774 | 4003.5386 | 5 | 9412.2688 | 4.1 | 114% | 7.7 | 6700 | 25.3 | 61.5 | 548.2504 | 40 | 274.8959 | 273.3545 | 2.0659 | 1.8122 | 4.0806
45618.3134 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.3 | 43 | 6.2 | -3 | 61.7 | 69.8 | 1.7 | 6.7 | 17 | 179 | 56 | -2.5 | -3.5 | 40.1 | 37.5 | 42.5 | 343 | 251 | 2000 | 18.6 | 34.8 | 550 | 50.4 | Room | On | 27.9 | 37.4 | 42.4 | 40 | 1011.276 | 4003.5386 | 5 | 9413.1869 | 4.2 | 114% | 7.9 | 6700 | 25.3 | 61.7 | 548.5747 | 40.1 | 275.0924 | 273.4823 | 2.0652 | 1.8116 | 4.0806
45618.3135 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.4 | 43 | 6.2 | -3 | 61.8 | 70 | 1.7 | 6.8 | 18 | 179 | 56 | -2.4 | -3.4 | 40.1 | 37.7 | 42.5 | 343 | 251 | 2000 | 18.7 | 34.8 | 550 | 50.4 | Room | On | 27.9 | 37.4 | 42.4 | 40.1 | 1011.2267 | 4003.5386 | 4.8 | 9036.219 | 4.1 | 114% | 7.9 | 6800 | 25.4 | 61.8 | 548.5089 | 40.1 | 275.1008 | 273.4081 | 1.983 | 1.7395 | 4.0968
45618.3136 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.6 | 44 | 6.2 | -3 | 61.8 | 70.1 | 1.7 | 6.8 | 18 | 179 | 56 | -2.4 | -3.4 | 40.3 | 38 | 42.8 | 343 | 257 | 2000 | 18.8 | 34.8 | 550 | 50.4 | Room | On | 27.9 | 37.7 | 42.5 | 40.4 | 1011.0785 | 4004.244 | 4.8 | 9036.4865 | 4.1 | 114% | 7.6 | 6800 | 25.6 | 61.8 | 548.0518 | 40.3 | 275.511 | 272.5407 | 1.9894 | 1.7451 | 4.129
45618.3138 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.6 | 44 | 6.2 | -3 | 62 | 70.2 | 1.7 | 6.8 | 18 | 179 | 56 | -2.4 | -3.5 | 40.3 | 38 | 42.8 | 343 | 257 | 2000 | 19 | 34.8 | 550 | 50.4 | Room | On | 27.9 | 37.7 | 42.5 | 40.4 | 1011.0785 | 4004.244 | 4.8 | 9036.4865 | 4.1 | 114% | 7.6 | 6800 | 25.6 | 62 | 548.3789 | 40.3 | 275.511 | 272.8678 | 1.987 | 1.743 | 4.129
45618.3139 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.6 | 44 | 6.2 | -3 | 62.1 | 70.2 | 1.7 | 6.8 | 18 | 179 | 56 | -2.4 | -3.5 | 40.5 | 38.1 | 43 | 343 | 257 | 2000 | 19 | 35 | 550 | 50.4 | Room | On | 27.9 | 37.7 | 42.5 | 40.55 | 1011.0042 | 4004.244 | 4.9 | 9224.0689 | 4.1 | 114% | 7.4 | 6800 | 25.6 | 62.1 | 548.5424 | 40.5 | 275.9045 | 272.6379 | 2.03 | 1.7807 | 4.129
45618.314 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.6 | 44 | 6.2 | -3 | 62.2 | 70.4 | 1.7 | 6.8 | 18 | 179 | 57 | -2.4 | -3.5 | 40.5 | 38.1 | 43 | 341 | 257 | 2000 | 19.1 | 35.1 | 550 | 50.4 | Room | On | 27.9 | 37.7 | 42.5 | 40.55 | 1011.0042 | 4004.244 | 4.9 | 9224.0689 | 4.1 | 114% | 7.4 | 6800 | 25.6 | 62.2 | 548.706 | 40.5 | 275.9045 | 272.8015 | 2.0287 | 1.7796 | 4.129
45618.3141 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.7 | 44 | 6.2 | -3 | 62.2 | 70.4 | 1.7 | 6.8 | 18 | 179 | 57 | -2.4 | -3.5 | 40.5 | 38.1 | 43 | 341 | 264 | 2000 | 19.1 | 35.1 | 550 | 50.4 | Room | On | 27.5 | 38.1 | 43 | 40.55 | 1011.0042 | 4005.1845 | 4.9 | 9093.9597 | 4.1 | 114% | 7.4 | 6800 | 25.7 | 62.2 | 548.4786 | 40.5 | 275.9132 | 272.5654 | 2.0019 | 1.756 | 4.1452
45618.3142 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.9 | 44 | 6.2 | -3 | 62.4 | 70.5 | 1.7 | 6.9 | 18 | 179 | 57 | -2.4 | -3.4 | 40.6 | 38.4 | 43.1 | 341 | 264 | 2000 | 19.1 | 35.2 | 550 | 50.4 | Room | On | 27.5 | 38.1 | 43 | 40.75 | 1010.905 | 4005.1845 | 4.7 | 8721.9213 | 4.1 | 114% | 7.3 | 6900 | 25.9 | 62.4 | 548.3526 | 40.6 | 276.1275 | 272.2251 | 1.9224 | 1.6863 | 4.1774
45618.3143 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.9 | 44 | 6.3 | -3 | 62.5 | 70.7 | 1.7 | 6.9 | 18 | 179 | 57 | -2.3 | -3.4 | 40.8 | 38.4 | 43.3 | 341 | 264 | 2000 | 19.3 | 35.2 | 550 | 50.4 | Room | On | 27.5 | 38.1 | 43 | 40.85 | 1010.8553 | 4005.1845 | 4.9 | 9092.6198 | 4 | 114% | 7.1 | 6900 | 25.9 | 62.5 | 548.5176 | 40.8 | 276.5215 | 271.9961 | 2.0058 | 1.7594 | 4.1111
45618.3144 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 26 | 44 | 6.3 | -3 | 62.7 | 70.8 | 1.8 | 6.9 | 18 | 179 | 57 | -2.3 | -3.4 | 41 | 38.5 | 43.5 | 341 | 264 | 2000 | 19.4 | 35.2 | 550 | 50.4 | Room | On | 27.5 | 38.1 | 43 | 41 | 1010.7806 | 4005.1845 | 5 | 9277.4981 | 4.1 | 114% | 6.9 | 6900 | 26 | 62.7 | 548.6213 | 41 | 276.9245 | 271.6968 | 2.0488 | 1.7972 | 4.127
45618.3146 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.9 | 44 | 6.2 | -3 | 62.8 | 71 | 1.8 | 6.9 | 18 | 179 | 57 | -2.3 | -3.4 | 41 | 38.5 | 43.5 | 341 | 270 | 2000 | 19.5 | 35.4 | 550 | 50.3 | Room | On | 27.9 | 38.5 | 43.5 | 41 | 1010.7806 | 4006.1251 | 5 | 9414.6538 | 4.1 | 114% | 6.8 | 6900 | 25.9 | 62.8 | 549.0126 | 41 | 276.9154 | 272.0971 | 2.076 | 1.8211 | 4.1774
45618.3147 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 26.1 | 44 | 6.2 | -3 | 63 | 71.1 | 1.8 | 6.9 | 18 | 179 | 57 | -2.4 | -3.4 | 41 | 38.7 | 43.5 | 342 | 270 | 2000 | 19.5 | 35.4 | 550 | 50.3 | Room | On | 27.9 | 38.5 | 43.5 | 41.1 | 1010.7308 | 4006.1251 | 4.8 | 9037.622 | 4.2 | 114% | 6.8 | 6900 | 26.1 | 63 | 548.8924 | 41 | 276.9335 | 271.9589 | 1.9939 | 1.749 | 4.2097
45618.3148 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 26 | 44 | 6.3 | -3 | 63 | 71.2 | 1.8 | 6.9 | 18 | 179 | 58 | -2.4 | -3.4 | 41.1 | 38.7 | 43.6 | 342 | 270 | 2000 | 19.7 | 35.4 | 550 | 50.3 | Room | On | 27.9 | 38.5 | 43.5 | 41.15 | 1010.7058 | 4006.1251 | 4.9 | 9225.6781 | 4.2 | 114% | 6.7 | 6900 | 26 | 63 | 549.1177 | 41.1 | 277.1215 | 271.9962 | 2.0351 | 1.7852 | 4.127
45618.3149 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.9 | 44 | 6.3 | -3 | 63.1 | 71.4 | 1.7 | 6.9 | 18 | 179 | 58 | -2.3 | -3.4 | 41.1 | 38.5 | 43.6 | 342 | 270 | 2000 | 19.8 | 35.4 | 540 | 50.3 | Room | On | 27.9 | 38.5 | 43.5 | 41.05 | 1010.7557 | 4006.1251 | 5.1 | 9602.7102 | 4 | 114% | 6.7 | 6900 | 25.9 | 63.1 | 549.5075 | 41.1 | 277.1124 | 272.3951 | 2.1152 | 1.8554 | 4.1111
45618.315 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.6 | 44 | 6.3 | -3 | 63.2 | 71.5 | 1.7 | 6.8 | 18 | 179 | 58 | -2.3 | -3.4 | 41.1 | 38 | 43.1 | 342 | 276 | 2000 | 19.8 | 35.2 | 550 | 50.4 | Room | On | 27.9 | 38.5 | 43.6 | 40.55 | 1011.0042 | 4006.1251 | 5.1 | 9605.0715 | 4 | 114% | 7.3 | 6800 | 25.6 | 63.2 | 550.3416 | 41.1 | 277.085 | 273.2566 | 2.109 | 1.85 | 4.0635
45618.3151 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.3 | 43 | 6.2 | -3 | 63.4 | 71.5 | 1.8 | 6.8 | 18 | 183 | 58 | -2.3 | -3.4 | 41 | 37.5 | 43 | 342 | 276 | 2000 | 19.8 | 34.8 | 550 | 50.4 | Room | On | 27.9 | 38.5 | 43.6 | 40.25 | 1011.1527 | 4006.1251 | 5.5 | 10359.9314 | 4.1 | 114% | 7.4 | 6800 | 25.3 | 63.4 | 551.3312 | 41 | 276.8611 | 274.4701 | 2.2647 | 1.9866 | 4.0806
45618.3153 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.1 | 43 | 6.2 | -3 | 63.4 | 71.5 | 1.8 | 6.7 | 17 | 183 | 58 | -2.4 | -3.4 | 40.8 | 37.1 | 42.5 | 342 | 276 | 2000 | 19.9 | 34.1 | 550 | 50.4 | Room | On | 27.9 | 38.5 | 43.6 | 39.8 | 1011.3744 | 4006.1251 | 5.4 | 10173.7995 | 4.2 | 114% | 7.9 | 6700 | 25.1 | 63.4 | 551.7707 | 40.8 | 276.4502 | 275.3204 | 2.2172 | 1.9449 | 4.0484
45618.3154 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 24.9 | 43 | 6.2 | -3 | 63.2 | 71.5 | 1.8 | 6.7 | 17 | 183 | 57 | -2.4 | -3.4 | 40.5 | 36.8 | 42.2 | 333 | 276 | 2000 | 20 | 33.3 | 550 | 50.4 | Room | On | 27.9 | 38.5 | 43.6 | 39.5 | 1011.5216 | 4006.1251 | 5.4 | 10175.2802 | 4.2 | 114% | 8.2 | 6700 | 24.9 | 63.2 | 551.8879 | 40.5 | 275.8438 | 276.0442 | 2.2117 | 1.9401 | 4.0161
45618.3155 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.1 | 43 | 6.2 | -3 | 63.1 | 71.4 | 1.8 | 6.8 | 18 | 183 | 57 | -2.4 | -3.4 | 40.1 | 37 | 42.1 | 333 | 278 | 2000 | 20 | 32.6 | 550 | 50.3 | Room | On | 27.9 | 36.8 | 42.2 | 39.55 | 1011.4971 | 4002.1278 | 5.1 | 9600.1657 | 4.2 | 114% | 8.2 | 6800 | 25.1 | 63.1 | 551.2871 | 40.1 | 275.0757 | 276.2114 | 2.0854 | 1.8293 | 4.0484
45618.3156 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.1 | 43 | 6.2 | -3 | 63 | 71.2 | 1.8 | 6.7 | 18 | 183 | 57 | -2.4 | -3.5 | 40.1 | 37 | 42.2 | 333 | 278 | 2000 | 20.1 | 32 | 550 | 50.3 | Room | On | 27.9 | 36.8 | 42.2 | 39.6 | 1011.4726 | 4002.1278 | 5.2 | 9788.1671 | 4.2 | 114% | 8.1 | 6700 | 25.1 | 63 | 551.1258 | 40.1 | 275.0757 | 276.0502 | 2.1275 | 1.8662 | 4.0484
45618.3157 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.1 | 43 | 6.2 | -3 | 63 | 71.2 | 1.8 | 6.7 | 18 | 183 | 57 | -2.4 | -3.5 | 40.1 | 37 | 42.2 | 333 | 278 | 2000 | 20.1 | 32 | 550 | 50.3 | Room | On | 27.9 | 36.8 | 42.2 | 39.6 | 1011.4726 | 4002.1278 | 5.2 | 9788.1671 | 4.2 | 114% | 8.1 | 6700 | 25.1 | 63 | 551.1258 | 40.1 | 275.0757 | 276.0502 | 2.1275 | 1.8662 | 4.0484
45618.3158 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.1 | 43 | 6.2 | -3 | 62.8 | 71.1 | 1.8 | 6.7 | 18 | 183 | 56 | -2.5 | -3.4 | 40.1 | 36.8 | 42.2 | 333 | 278 | 2000 | 20.2 | 31.4 | 550 | 50.3 | Room | On | 27.9 | 36.8 | 42.2 | 39.5 | 1011.5216 | 4002.1278 | 5.4 | 10165.1275 | 4.3 | 114% | 8.1 | 6700 | 25.1 | 62.8 | 550.8034 | 40.1 | 275.0757 | 275.7278 | 2.212 | 1.9403 | 4.0484
45618.316 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.2 | 43 | 6.2 | -3 | 62.7 | 70.8 | 1.8 | 6.8 | 18 | 183 | 56 | -2.5 | -3.5 | 40 | 37.1 | 42.2 | 333 | 279 | 2000 | 20.2 | 30.8 | 550 | 50.3 | Room | On | 27.9 | 37.1 | 42.2 | 39.65 | 1011.4481 | 4002.8332 | 5.1 | 9601.3923 | 4.3 | 114% | 8.1 | 6800 | 25.2 | 62.7 | 550.4194 | 40 | 274.8876 | 275.5318 | 2.0908 | 1.834 | 4.0645
45618.3161 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.3 | 43 | 6.2 | -3 | 62.7 | 70.8 | 1.8 | 6.8 | 18 | 183 | 56 | -2.5 | -3.5 | 40 | 37.2 | 42.4 | 339 | 279 | 2000 | 20.2 | 30.7 | 550 | 50.3 | Room | On | 27.9 | 37.1 | 42.2 | 39.8 | 1011.3744 | 4002.8332 | 5.2 | 9788.9419 | 4.3 | 114% | 7.9 | 6800 | 25.3 | 62.7 | 550.1961 | 40 | 274.8959 | 275.3002 | 2.1334 | 1.8714 | 4.0806
45618.3162 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.3 | 43 | 6.2 | -3 | 62.5 | 70.5 | 1.8 | 6.8 | 17 | 183 | 55 | -2.5 | -3.5 | 40.1 | 37.2 | 42.5 | 339 | 279 | 2000 | 20.3 | 30.7 | 550 | 50.3 | Room | On | 27.9 | 37.1 | 42.2 | 39.85 | 1011.3498 | 4002.8332 | 5.3 | 9976.9483 | 4.3 | 114% | 7.8 | 6800 | 25.3 | 62.5 | 549.8719 | 40.1 | 275.0924 | 274.7794 | 2.1785 | 1.911 | 4.0806
45618.3163 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.4 | 43 | 6.2 | -3 | 62.5 | 70.4 | 1.8 | 6.8 | 18 | 183 | 55 | -2.5 | -3.5 | 40.1 | 37.5 | 42.5 | 339 | 279 | 2000 | 20.3 | 30.8 | 550 | 50.3 | Room | On | 27.9 | 37.1 | 42.2 | 40 | 1011.276 | 4002.8332 | 5 | 9411.5283 | 4.3 | 114% | 7.8 | 6800 | 25.4 | 62.5 | 549.6472 | 40.1 | 275.1008 | 274.5464 | 2.0568 | 1.8042 | 4.0968
45618.3164 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.6 | 44 | 6.2 | -3 | 62.5 | 70.4 | 1.8 | 6.9 | 18 | 183 | 55 | -2.5 | -3.5 | 40.1 | 37.8 | 42.8 | 339 | 283 | 2000 | 20.3 | 31.2 | 550 | 50.3 | Room | On | 27.9 | 37.8 | 42.8 | 40.3 | 1011.128 | 4004.4791 | 5 | 9414.02 | 4.3 | 114% | 7.5 | 6900 | 25.6 | 62.5 | 549.1967 | 40.1 | 275.1175 | 274.0791 | 2.0609 | 1.8078 | 4.129
45618.3165 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.7 | 44 | 6.2 | -3 | 62.7 | 70.4 | 1.8 | 6.9 | 18 | 183 | 55 | -2.5 | -3.6 | 40.5 | 38 | 43 | 339 | 283 | 2000 | 20.3 | 31.7 | 550 | 50.3 | Room | On | 27.9 | 37.8 | 42.8 | 40.5 | 1011.029 | 4004.4791 | 5 | 9413.0986 | 4.3 | 114% | 7.3 | 6900 | 25.7 | 62.7 | 549.2988 | 40.5 | 275.9132 | 273.3856 | 2.0659 | 1.8122 | 4.1452
45618.3166 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.9 | 44 | 6.2 | -3 | 62.8 | 70.4 | 1.8 | 6.9 | 18 | 180 | 55 | -2.5 | -3.5 | 40.6 | 38.4 | 43.3 | 339 | 283 | 2000 | 20.4 | 32.2 | 550 | 50.3 | Room | On | 27.9 | 37.8 | 42.8 | 40.85 | 1010.8553 | 4004.4791 | 4.9 | 9223.2514 | 4.3 | 114% | 7 | 6900 | 25.9 | 62.8 | 549.0126 | 40.6 | 276.1275 | 272.885 | 2.0279 | 1.7789 | 4.1774
45618.3168 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 25.9 | 44 | 6.2 | -3 | 63 | 70.5 | 1.8 | 7 | 18 | 180 | 55 | -2.4 | -3.5 | 40.8 | 38.4 | 43.3 | 338 | 283 | 2000 | 20.5 | 32.7 | 550 | 50.3 | Room | On | 27.9 | 37.8 | 42.8 | 40.85 | 1010.8553 | 4004.4791 | 4.9 | 9223.2514 | 4.2 | 114% | 7 | 7000 | 25.9 | 63 | 549.3425 | 40.8 | 276.5215 | 272.8211 | 2.0284 | 1.7793 | 4.1774
45618.3169 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 26.1 | 44 | 6.2 | -3 | 63.1 | 70.5 | 1.8 | 7 | 18 | 180 | 56 | -2.4 | -3.4 | 41 | 38.5 | 43.5 | 338 | 290 | 2000 | 20.5 | 33.2 | 550 | 50.3 | Room | On | 28.1 | 38.4 | 43.3 | 41 | 1010.7806 | 4005.8899 | 5 | 9481.5859 | 4.2 | 114% | 6.8 | 7000 | 26.1 | 63.1 | 549.0584 | 41 | 276.9335 | 272.1249 | 2.0906 | 1.8338 | 4.2097
45618.317 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 26.3 | 45 | 6.2 | -3 | 63.2 | 70.8 | 1.8 | 7.1 | 18 | 180 | 56 | -2.4 | -3.4 | 41.1 | 39 | 43.8 | 338 | 290 | 2000 | 20.5 | 33.5 | 560 | 50.3 | Room | On | 28.1 | 38.4 | 43.3 | 41.4 | 1010.5809 | 4005.8899 | 4.8 | 9100.5238 | 4.2 | 114% | 6.5 | 7100 | 26.3 | 63.2 | 548.7744 | 41.1 | 277.1489 | 271.6255 | 2.0102 | 1.7634 | 4.2419
45618.3171 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 26.2 | 45 | 6.3 | -3 | 63.4 | 71 | 1.8 | 7 | 18 | 180 | 56 | -2.4 | -3.4 | 41.3 | 39.1 | 44 | 338 | 290 | 2000 | 20.7 | 33.8 | 550 | 50.3 | Room | On | 28.1 | 38.4 | 43.3 | 41.55 | 1010.5057 | 4005.8899 | 4.9 | 9289.4274 | 4.2 | 114% | 6.3 | 7000 | 26.2 | 63.4 | 549.3324 | 41.3 | 277.5342 | 271.7983 | 2.0507 | 1.7988 | 4.1587
45618.3172 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 26.3 | 45 | 6.3 | -3 | 63.7 | 71.1 | 1.8 | 7.1 | 18 | 180 | 56 | -2.3 | -3.4 | 41.5 | 39.1 | 44 | 338 | 290 | 2000 | 20.7 | 34.1 | 550 | 50.3 | Room | On | 28.1 | 38.4 | 43.3 | 41.55 | 1010.5057 | 4005.8899 | 4.9 | 9289.4274 | 4.1 | 114% | 6.3 | 7100 | 26.3 | 63.7 | 549.609 | 41.5 | 277.938 | 271.671 | 2.0516 | 1.7997 | 4.1746
45618.3173 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 26.6 | 45 | 6.3 | -3 | 63.8 | 71.2 | 1.8 | 7.1 | 18 | 180 | 57 | -2.3 | -3.3 | 41.6 | 39.2 | 44.2 | 338 | 296 | 2000 | 20.8 | 34.2 | 550 | 50.3 | Room | On | 28.1 | 39.1 | 44 | 41.7 | 1010.4305 | 4007.5358 | 5 | 9482.196 | 4.1 | 114% | 6.1 | 7100 | 26.6 | 63.8 | 549.1066 | 41.6 | 278.1638 | 270.9428 | 2.0998 | 1.8419 | 4.2222
45618.3175 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 26.6 | 45 | 6.3 | -3 | 63.8 | 71.2 | 1.8 | 7.1 | 18 | 180 | 57 | -2.3 | -3.3 | 41.6 | 39.2 | 44.2 | 337 | 296 | 2000 | 20.8 | 34.2 | 550 | 50.3 | Room | On | 28.1 | 39.1 | 44 | 41.7 | 1010.4305 | 4007.5358 | 5 | 9482.196 | 4.1 | 114% | 6.1 | 7100 | 26.6 | 63.8 | 549.1066 | 41.6 | 278.1638 | 270.9428 | 2.0998 | 1.8419 | 4.2222
45618.3176 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 26.6 | 45 | 6.3 | -3 | 64.1 | 71.5 | 1.9 | 7.1 | 18 | 180 | 57 | -2.3 | -3.3 | 41.8 | 39.5 | 44.6 | 337 | 296 | 2000 | 21 | 34.4 | 540 | 50.3 | Room | On | 28.1 | 39.1 | 44 | 42.05 | 1010.2544 | 4007.5358 | 5.1 | 9670.1545 | 4.2 | 114% | 5.7 | 7100 | 26.6 | 64.1 | 549.6117 | 41.8 | 278.5588 | 271.0529 | 2.1406 | 1.8777 | 4.2222
45618.3177 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 26.6 | 45 | 6.3 | -3 | 64.2 | 71.8 | 1.9 | 7.1 | 18 | 180 | 57 | -2.3 | -3.3 | 42 | 39.5 | 44.6 | 337 | 296 | 2000 | 21.1 | 34.5 | 550 | 50.3 | Room | On | 28.1 | 39.1 | 44 | 42.05 | 1010.2544 | 4007.5358 | 5.1 | 9670.1545 | 4.2 | 114% | 5.7 | 7100 | 26.6 | 64.2 | 549.7801 | 42 | 278.9538 | 270.8263 | 2.1424 | 1.8793 | 4.2222
45618.3178 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 26.7 | 45 | 6.3 | -3 | 64.5 | 72 | 1.9 | 7.2 | 19 | 180 | 57 | -2.2 | -3.3 | 42.1 | 39.5 | 44.8 | 337 | 300 | 2000 | 21.2 | 34.8 | 550 | 50.3 | Room | On | 28.1 | 39.5 | 44.8 | 42.15 | 1010.204 | 4008.4763 | 5.3 | 10051.2329 | 4.1 | 114% | 5.5 | 7200 | 26.7 | 64.5 | 550.0647 | 42.1 | 279.1612 | 270.9035 | 2.2262 | 1.9528 | 4.2381
45618.3179 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 26.9 | 46 | 6.3 | -3 | 64.8 | 72.2 | 1.9 | 7.3 | 19 | 180 | 58 | -2.2 | -3.3 | 42.1 | 40 | 44.8 | 337 | 300 | 2000 | 21.2 | 34.8 | 550 | 50.3 | Room | On | 28.1 | 39.5 | 44.8 | 42.4 | 1010.0776 | 4008.4763 | 4.8 | 9101.8649 | 4.1 | 114% | 5.5 | 7300 | 26.9 | 64.8 | 550.132 | 42.1 | 279.181 | 270.951 | 2.0155 | 1.768 | 4.2698
45618.318 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 27 | 46 | 6.2 | -3 | 65 | 72.4 | 1.9 | 7.2 | 19 | 180 | 58 | -2.2 | -3.3 | 42.4 | 40.1 | 45.1 | 337 | 300 | 2000 | 21.3 | 35 | 550 | 50.3 | Room | On | 28.1 | 39.5 | 44.8 | 42.6 | 1009.9763 | 4008.4763 | 5 | 9480.1583 | 4.1 | 114% | 5.2 | 7200 | 27 | 65 | 550.2524 | 42.4 | 279.7842 | 270.4681 | 2.1031 | 1.8448 | 4.3548
45618.3182 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 27.1 | 46 | 6.3 | -3 | 65.1 | 72.7 | 1.9 | 7.3 | 19 | 180 | 58 | -2.2 | -3.3 | 42.4 | 40.1 | 45.1 | 338 | 300 | 2000 | 21.4 | 35.4 | 540 | 50.3 | Room | On | 28.1 | 39.5 | 44.8 | 42.6 | 1009.9763 | 4008.4763 | 5 | 9480.1583 | 4.1 | 114% | 5.2 | 7300 | 27.1 | 65.1 | 550.2035 | 42.4 | 279.7944 | 270.4092 | 2.1035 | 1.8452 | 4.3016
45618.3183 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 27.1 | 46 | 6.3 | -3 | 65.4 | 73 | 1.9 | 7.3 | 19 | 180 | 58 | -2.2 | -3.3 | 42.5 | 40.3 | 45.3 | 338 | 300 | 2000 | 21.4 | 35.5 | 550 | 50.3 | Room | On | 27.9 | 40.3 | 45.3 | 42.8 | 1009.8748 | 4010.3574 | 5 | 9416.1541 | 4.1 | 114% | 5 | 7300 | 27.1 | 65.4 | 550.716 | 42.5 | 279.9922 | 270.7238 | 2.0869 | 1.8306 | 4.3016
45618.3184 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 27.2 | 46 | 6.2 | -3 | 65.7 | 73.2 | 1.9 | 7.3 | 19 | 180 | 59 | -2.2 | -3.3 | 42.7 | 40.5 | 45.6 | 338 | 300 | 2000 | 21.4 | 35.8 | 550 | 50.3 | Room | On | 27.9 | 40.3 | 45.3 | 43.05 | 1009.7475 | 4010.3574 | 5.1 | 9603.267 | 4.1 | 114% | 4.7 | 7300 | 27.2 | 65.7 | 551.0119 | 42.7 | 280.3983 | 270.6136 | 2.1292 | 1.8677 | 4.3871
45618.3185 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 27.2 | 46 | 6.3 | -3 | 65.8 | 73.5 | 1.8 | 7.3 | 19 | 180 | 59 | -2.2 | -3.3 | 42.8 | 40.5 | 45.6 | 338 | 300 | 2000 | 21.4 | 36 | 550 | 50.3 | Room | On | 27.9 | 40.3 | 45.3 | 43.05 | 1009.7475 | 4010.3574 | 5.1 | 9603.267 | 4 | 114% | 4.7 | 7300 | 27.2 | 65.8 | 551.1832 | 42.8 | 280.5963 | 270.5869 | 2.1294 | 1.8679 | 4.3175
45618.3186 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 27.2 | 46 | 6.3 | -3 | 66.1 | 73.8 | 1.8 | 7.3 | 19 | 180 | 59 | -2.2 | -3.2 | 42.8 | 40.5 | 45.6 | 338 | 300 | 2000 | 21.4 | 36.1 | 540 | 50.3 | Room | On | 27.9 | 40.3 | 45.3 | 43.05 | 1009.7475 | 4010.3574 | 5.1 | 9603.267 | 4 | 114% | 4.7 | 7300 | 27.2 | 66.1 | 551.6972 | 42.8 | 280.5963 | 271.1009 | 2.1254 | 1.8644 | 4.3175
45618.3187 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 27.4 | 46 | 6.3 | -3 | 66.2 | 74 | 1.8 | 7.4 | 19 | 180 | 59 | -2.1 | -3.2 | 43 | 40.8 | 45.8 | 338 | 300 | 2000 | 21.5 | 36.1 | 550 | 50.3 | Room | On | 27.9 | 40.8 | 45.8 | 43.3 | 1009.6199 | 4011.533 | 5 | 9416.5376 | 3.9 | 114% | 4.5 | 7400 | 27.4 | 66.2 | 551.4391 | 43 | 281.0133 | 270.4258 | 2.0893 | 1.8327 | 4.3492
45618.3188 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 27.4 | 46 | 6.3 | -3 | 66.5 | 74.2 | 1.9 | 7.4 | 19 | 180 | 60 | -2.1 | -3.1 | 43.1 | 40.8 | 45.8 | 321 | 300 | 2000 | 21.6 | 36.2 | 550 | 50.3 | Room | On | 27.9 | 40.8 | 45.8 | 43.3 | 1009.6199 | 4011.533 | 5 | 9416.5376 | 4 | 114% | 4.5 | 7400 | 27.4 | 66.5 | 551.956 | 43.1 | 281.2114 | 270.7446 | 2.0868 | 1.8305 | 4.3492
45618.319 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 27.6 | 47 | 6.3 | -3 | 66.7 | 74.3 | 1.9 | 7.4 | 19 | 180 | 60 | -2.1 | -3.2 | 43.1 | 40.8 | 46 | 321 | 300 | 2000 | 21.6 | 36.2 | 550 | 50.3 | Room | On | 27.9 | 40.8 | 45.8 | 43.4 | 1009.5688 | 4011.533 | 5.2 | 9792.7031 | 4 | 114% | 4.3 | 7400 | 27.6 | 66.7 | 551.8747 | 43.1 | 281.2327 | 270.642 | 2.171 | 1.9044 | 4.381
45618.3191 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 27.7 | 47 | 6.3 | -3 | 67 | 74.3 | 1.9 | 7.5 | 19 | 180 | 60 | -2.2 | -3.2 | 43.1 | 40.8 | 46 | 321 | 300 | 2000 | 21.7 | 36.1 | 550 | 50.3 | Room | On | 27.9 | 40.8 | 45.8 | 43.4 | 1009.5688 | 4011.533 | 5.2 | 9792.7031 | 4.1 | 114% | 4.3 | 7500 | 27.7 | 67 | 552.1827 | 43.1 | 281.2434 | 270.9393 | 2.1686 | 1.9023 | 4.3968
45618.3192 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 27.7 | 47 | 6.3 | -3 | 67 | 74.6 | 1.9 | 7.5 | 19 | 180 | 60 | -2.2 | -3.2 | 43.3 | 41.1 | 46.1 | 304 | 300 | 2000 | 21.8 | 36.1 | 550 | 50.3 | Room | On | 28.3 | 41.1 | 46.1 | 43.6 | 1009.4664 | 4012.2384 | 5 | 9551.7681 | 4.1 | 114% | 4.2 | 7500 | 27.7 | 67 | 552.1827 | 43.3 | 281.64 | 270.5426 | 2.1184 | 1.8582 | 4.3968
45618.3193 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 27.9 | 47 | 6.3 | -3 | 67.1 | 74.8 | 1.9 | 7.5 | 20 | 180 | 60 | -2.2 | -3.2 | 43.5 | 41.3 | 46.5 | 304 | 300 | 2000 | 22.1 | 35.8 | 550 | 50.3 | Room | On | 28.3 | 41.1 | 46.1 | 43.9 | 1009.3123 | 4012.2384 | 5.2 | 9932.3226 | 4.1 | 114% | 3.8 | 7500 | 27.9 | 67.1 | 551.9323 | 43.5 | 282.0586 | 269.8737 | 2.2082 | 1.937 | 4.4286
45618.3194 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 28 | 47 | 6.3 | -3 | 67.4 | 75 | 1.9 | 7.5 | 20 | 180 | 60 | -2.2 | -3.2 | 43.8 | 41.3 | 46.5 | 304 | 300 | 2000 | 22.1 | 35.4 | 550 | 50.3 | Room | On | 28.3 | 41.1 | 46.1 | 43.9 | 1009.3123 | 4012.2384 | 5.2 | 9932.3226 | 4.1 | 114% | 3.8 | 7500 | 28 | 67.4 | 552.2456 | 43.8 | 282.6652 | 269.5804 | 2.2106 | 1.9391 | 4.4444
45618.3195 | On | Off | Off | Off | Off | Normal Operation | 57 | 54 | 57 | 28.2 | 48 | 6.2 | -3 | 67.7 | 75.2 | 1.9 | 7.6 | 20 | 180 | 60 | -2.3 | -3.3 | 44 | 41.5 | 46.8 | 288 | 300 | 2000 | 22.3 | 34 | 550 | 50.3 | Room | On | 28.3 | 41.1 | 46.1 | 44.15 | 1009.1835 | 4012.2384 | 5.3 | 10122.0371 | 4.2 | 114% | 3.5 | 7600 | 28.2 | 67.7 | 552.3513 | 44 | 283.085 | 269.2664 | 2.2555 | 1.9785 | 4.5484
45618.3197 | On | Off | Off | Off | Off | Normal Operation | 57 | 54 | 57 | 28.2 | 48 | 6.2 | -3 | 67.8 | 75.5 | 1.9 | 7.6 | 20 | 180 | 59 | -2.4 | -3.3 | 44.2 | 41.5 | 46.8 | 288 | 300 | 2000 | 22.5 | 32.3 | 550 | 50.3 | Room | On | 27.9 | 41.5 | 46.8 | 44.15 | 1009.1835 | 4013.1789 | 5.3 | 9981.3086 | 4.3 | 114% | 3.5 | 7600 | 28.2 | 67.8 | 552.5277 | 44.2 | 283.4824 | 269.0453 | 2.2259 | 1.9526 | 4.5484
45618.3198 | On | Off | Off | Off | Off | Normal Operation | 56 | 54 | 56 | 28.5 | 48 | 6.2 | -3 | 68.1 | 75.8 | 2 | 7.6 | 20 | 183 | 59 | -2.5 | -3.4 | 44.4 | 41.5 | 47 | 288 | 300 | 2000 | 22.4 | 27.7 | 550 | 50.3 | Room | On | 27.9 | 41.5 | 46.8 | 44.25 | 1009.1319 | 4013.1789 | 5.5 | 10357.432 | 4.5 | 112% | 3.3 | 7600 | 28.5 | 68.1 | 552.4297 | 44.4 | 283.9147 | 268.515 | 2.3144 | 2.0664 | 4.5968
45618.3199 | On | Off | Off | Off | Off | Normal Operation | 55 | 54 | 55 | 28.6 | 48 | 6.2 | -3 | 68.2 | 75.8 | 2 | 7.5 | 20 | 183 | 58 | -2.6 | -3.5 | 44.6 | 41.6 | 47.1 | 288 | 300 | 2000 | 22.3 | 25.4 | 550 | 50.3 | Room | On | 27.9 | 41.5 | 46.8 | 44.35 | 1009.0802 | 4013.1789 | 5.5 | 10356.9017 | 4.6 | 110% | 3.2 | 7500 | 28.6 | 68.2 | 552.3983 | 44.6 | 284.3243 | 268.074 | 2.3181 | 2.1073 | 4.6129
45618.32 | On | Off | Off | Off | Off | Normal Operation | 55 | 54 | 55 | 28.6 | 48 | 6.2 | -3 | 68.2 | 76 | 2 | 7.4 | 20 | 183 | 58 | -2.7 | -3.6 | 44.8 | 41.6 | 47.2 | 288 | 300 | 2000 | 22.1 | 23.8 | 550 | 50.3 | Room | On | 27.9 | 41.5 | 46.8 | 44.4 | 1009.0544 | 4013.1789 | 5.6 | 10544.9388 | 4.7 | 110% | 3.1 | 7400 | 28.6 | 68.2 | 552.3983 | 44.8 | 284.7224 | 267.676 | 2.3637 | 2.1488 | 4.6129
45618.3201 | On | Off | Off | Off | Off | Normal Operation | 54 | 54 | 54 | 28.7 | 48 | 6.2 | -3 | 68 | 75.8 | 2 | 7.3 | 20 | 183 | 57 | -2.7 | -3.6 | 45 | 41.8 | 47.2 | 288 | 293 | 2000 | 22.1 | 23.4 | 550 | 50.3 | Room | On | 27.9 | 41.5 | 46.8 | 44.5 | 1009.0026 | 4013.1789 | 5.4 | 10167.8124 | 4.7 | 108% | 3.1 | 7300 | 28.7 | 68 | 551.8309 | 45 | 285.1325 | 266.6985 | 2.2875 | 2.118 | 4.629
45618.3202 | On | Off | Off | Off | Off | Normal Operation | 54 | 51 | 54 | 28.8 | 49 | 6.2 | -3 | 67.4 | 75.4 | 2 | 7.3 | 20 | 183 | 57 | -2.7 | -3.6 | 45 | 42 | 47.2 | 288 | 293 | 2000 | 22.2 | 23.3 | 550 | 50.2 | Room | On | 27.9 | 41.8 | 47.2 | 44.6 | 1008.9508 | 4013.8843 | 5.2 | 9792.4449 | 4.7 | 108% | 3 | 7300 | 28.8 | 67.4 | 550.5434 | 45 | 285.1445 | 265.3988 | 2.2138 | 2.0498 | 4.6452
45618.3204 | On | Off | Off | Off | Off | Normal Operation | 54 | 51 | 54 | 29 | 49 | 6.2 | -3 | 67 | 74.8 | 2 | 7.4 | 20 | 183 | 56 | -2.6 | -3.5 | 45.1 | 42.2 | 47.3 | 288 | 293 | 2000 | 22.4 | 23.2 | 550 | 50.2 | Room | On | 27.9 | 41.8 | 47.2 | 44.75 | 1008.873 | 4013.8843 | 5.1 | 9603.3879 | 4.6 | 108% | 2.9 | 7400 | 29 | 67 | 549.3922 | 45.1 | 285.368 | 264.0242 | 2.1824 | 2.0207 | 4.6774
45618.3205 | On | Off | Off | Off | Off | Normal Operation | 53 | 51 | 53 | 28.9 | 49 | 6.2 | -3 | 66.5 | 74.5 | 2 | 7.2 | 20 | 183 | 56 | -2.6 | -3.4 | 45.3 | 42.2 | 47.5 | 288 | 293 | 2000 | 22.5 | 23.2 | 540 | 50.2 | Room | On | 27.9 | 41.8 | 47.2 | 44.85 | 1008.821 | 4013.8843 | 5.3 | 9979.4775 | 4.6 | 106% | 2.7 | 7200 | 28.9 | 66.5 | 548.7094 | 45.3 | 285.7543 | 262.955 | 2.2771 | 2.1482 | 4.6613
45618.3206 | On | Off | Off | Off | Off | Normal Operation | 52 | 51 | 53 | 28.8 | 49 | 6.2 | -3 | 66.2 | 74 | 2 | 7.2 | 20 | 183 | 56 | -2.6 | -3.4 | 45.3 | 42.2 | 47.5 | 286 | 285 | 2000 | 22.5 | 23.2 | 550 | 50.2 | Room | On | 27.9 | 41.8 | 47.2 | 44.85 | 1008.821 | 4013.8843 | 5.3 | 9979.4775 | 4.6 | 106% | 2.7 | 7200 | 28.8 | 66.2 | 548.3902 | 45.3 | 285.742 | 262.6481 | 2.2797 | 2.1507 | 4.6452
45618.3207 | On | Off | Off | Off | Off | Normal Operation | 52 | 51 | 52 | 28.7 | 48 | 6.3 | -3 | 66.1 | 73.5 | 2 | 7.1 | 20 | 183 | 56 | -2.5 | -3.3 | 45.3 | 42.2 | 47.5 | 286 | 285 | 2000 | 22.5 | 23.2 | 550 | 50.2 | Room | On | 27.9 | 42.2 | 47.5 | 44.85 | 1008.821 | 4014.8249 | 5.3 | 9981.8158 | 4.5 | 104% | 2.7 | 7100 | 28.7 | 66.1 | 548.4315 | 45.3 | 285.7297 | 262.7018 | 2.2798 | 2.1921 | 4.5556
45618.3208 | On | Off | Off | Off | Off | Normal Operation | 51 | 51 | 51 | 28.7 | 48 | 6.3 | -3 | 66.1 | 73.5 | 2 | 7.1 | 20 | 183 | 56 | -2.5 | -3.3 | 45.3 | 42.2 | 47.5 | 286 | 285 | 2000 | 22.5 | 23.2 | 550 | 50.2 | Room | On | 27.9 | 42.2 | 47.5 | 44.85 | 1008.821 | 4014.8249 | 5.3 | 9981.8158 | 4.5 | 102% | 2.7 | 7100 | 28.7 | 66.1 | 548.4315 | 45.3 | 285.7297 | 262.7018 | 2.2798 | 2.2351 | 4.5556
45618.3209 | On | Off | Off | Off | Off | Normal Operation | 51 | 52 | 51 | 28.9 | 49 | 6.3 | -3 | 66 | 73.1 | 2 | 7.1 | 20 | 183 | 56 | -2.5 | -3.3 | 45.3 | 42.5 | 47.5 | 286 | 285 | 2000 | 22.5 | 23.2 | 550 | 50.2 | Room | On | 27.9 | 42.2 | 47.5 | 45 | 1008.743 | 4014.8249 | 5 | 9416.0791 | 4.5 | 102% | 2.7 | 7100 | 28.9 | 66 | 547.8096 | 45.3 | 285.7543 | 262.0553 | 2.1559 | 2.1136 | 4.5873
45618.321 | On | Off | Off | Off | Off | Normal Operation | 51 | 52 | 51 | 28.9 | 49 | 6.3 | -3 | 66 | 72.8 | 2 | 7 | 20 | 183 | 55 | -2.4 | -3.1 | 45.5 | 42.7 | 47.5 | 286 | 277 | 2000 | 22.8 | 23.5 | 550 | 50.2 | Room | On | 27.9 | 42.2 | 47.5 | 45.1 | 1008.6909 | 4014.8249 | 4.8 | 9038.9691 | 4.4 | 102% | 2.7 | 7000 | 28.9 | 66 | 547.8096 | 45.5 | 286.1528 | 261.6568 | 2.0727 | 2.0321 | 4.5873
45618.3212 | On | Off | Off | Off | Off | Normal Operation | 52 | 52 | 52 | 28.8 | 49 | 6.3 | -3 | 66 | 72.7 | 2 | 7 | 20 | 183 | 55 | -2.3 | -3.1 | 45.5 | 42.7 | 47.6 | 286 | 277 | 2000 | 22.8 | 23.5 | 550 | 50.2 | Room | On | 28.1 | 42.7 | 47.5 | 45.15 | 1008.6648 | 4016.0005 | 4.9 | 9295.9075 | 4.3 | 104% | 2.6 | 7000 | 28.8 | 66 | 548.0313 | 45.5 | 286.1404 | 261.891 | 2.1297 | 2.0478 | 4.5714
45618.3213 | On | Off | Off | Off | Off | Normal Operation | 52 | 52 | 52 | 28.9 | 49 | 6.3 | -3 | 66.1 | 72.7 | 2 | 7.2 | 20 | 183 | 55 | -2.3 | -3 | 45.5 | 42.7 | 47.6 | 286 | 277 | 2000 | 22.7 | 23.4 | 550 | 50.2 | Room | On | 28.1 | 42.7 | 47.5 | 45.15 | 1008.6648 | 4016.0005 | 4.9 | 9295.9075 | 4.3 | 104% | 2.6 | 7200 | 28.9 | 66.1 | 547.9896 | 45.5 | 286.1528 | 261.8368 | 2.1302 | 2.0482 | 4.5873
45618.3214 | On | Off | Off | Off | Off | Normal Operation | 52 | 52 | 52 | 29 | 49 | 6.3 | -3 | 66.5 | 72.8 | 2 | 7.2 | 20 | 179 | 55 | -2.3 | -3 | 45.5 | 42.8 | 47.6 | 286 | 277 | 2000 | 22.6 | 23.4 | 550 | 50.2 | Room | On | 28.1 | 42.7 | 47.5 | 45.2 | 1008.6388 | 4016.0005 | 4.8 | 9105.9597 | 4.3 | 104% | 2.6 | 7200 | 29 | 66.5 | 548.4899 | 45.5 | 286.1653 | 262.3246 | 2.0828 | 2.0026 | 4.6032
45618.3215 | On | Off | Off | Off | Off | Normal Operation | 52 | 52 | 52 | 29 | 49 | 6.3 | -3 | 66.8 | 73.1 | 2 | 7.2 | 20 | 179 | 55 | -2.3 | -3.1 | 45.5 | 42.8 | 47.6 | 286 | 277 | 2000 | 22.6 | 23.7 | 550 | 50.2 | Room | On | 28.1 | 42.7 | 47.5 | 45.2 | 1008.6388 | 4016.0005 | 4.8 | 9105.9597 | 4.3 | 104% | 2.6 | 7200 | 29 | 66.8 | 549.0313 | 45.5 | 286.1653 | 262.866 | 2.0785 | 1.9985 | 4.6032
45618.3216 | On | Off | Off | Off | Off | Normal Operation | 52 | 53 | 52 | 29 | 49 | 6.3 | -3 | 67.4 | 73.5 | 2 | 7.2 | 20 | 179 | 55 | -2.3 | -3.1 | 45.5 | 43 | 47.7 | 286 | 277 | 2000 | 22.6 | 24.1 | 550 | 50.2 | Room | On | 28.1 | 42.8 | 47.6 | 45.35 | 1008.5604 | 4016.2356 | 4.7 | 8916.0818 | 4.3 | 104% | 2.5 | 7200 | 29 | 67.4 | 550.1141 | 45.5 | 286.1653 | 263.9489 | 2.0268 | 1.9488 | 4.6032
45618.3217 | On | Off | Off | Off | Off | Normal Operation | 52 | 53 | 52 | 29 | 49 | 6.3 | -3 | 67.8 | 74 | 2 | 7.2 | 20 | 179 | 55 | -2.3 | -3.1 | 45.6 | 43 | 47.7 | 286 | 277 | 2000 | 22.6 | 24.8 | 550 | 50.2 | Room | On | 28.1 | 42.8 | 47.6 | 45.35 | 1008.5604 | 4016.2356 | 4.7 | 8916.0818 | 4.3 | 104% | 2.5 | 7200 | 29 | 67.8 | 550.836 | 45.6 | 286.3646 | 264.4714 | 2.0228 | 1.945 | 4.6032
45618.3219 | On | Off | Off | Off | Off | Normal Operation | 53 | 53 | 53 | 29.2 | 49 | 6.3 | -3 | 68.2 | 74.3 | 2 | 7.4 | 20 | 179 | 56 | -2.3 | -3.1 | 45.6 | 43.1 | 47.8 | 286 | 277 | 2000 | 22.7 | 25.8 | 540 | 50.2 | Room | On | 28.1 | 42.8 | 47.6 | 45.45 | 1008.5082 | 4016.2356 | 4.7 | 8915.6196 | 4.3 | 106% | 2.4 | 7400 | 29.2 | 68.2 | 551.1355 | 45.6 | 286.3897 | 264.7459 | 2.0206 | 1.9062 | 4.6349
45618.322 | On | Off | Off | Off | Off | Normal Operation | 53 | 53 | 53 | 29.2 | 49 | 6.3 | -3 | 68.7 | 74.8 | 2 | 7.4 | 20 | 179 | 56 | -2.3 | -3.1 | 45.8 | 43.1 | 47.8 | 286 | 280 | 2000 | 22.8 | 26.8 | 550 | 50.2 | Room | On | 28.1 | 42.8 | 47.6 | 45.45 | 1008.5082 | 4016.2356 | 4.7 | 8915.6196 | 4.3 | 106% | 2.4 | 7400 | 29.2 | 68.7 | 552.0431 | 45.8 | 286.7886 | 265.2545 | 2.0167 | 1.9025 | 4.6349
45618.3221 | On | Off | Off | Off | Off | Normal Operation | 53 | 53 | 53 | 29.4 | 49 | 6.3 | -3 | 69.1 | 75.2 | 2 | 7.5 | 21 | 179 | 56 | -2.3 | -3.1 | 45.8 | 43.3 | 48 | 286 | 280 | 2000 | 22.8 | 27.2 | 550 | 50.2 | Room | On | 27.7 | 43.1 | 47.8 | 45.65 | 1008.4034 | 4016.941 | 4.7 | 8789.3376 | 4.3 | 106% | 2.2 | 7500 | 29.4 | 69.1 | 552.3548 | 45.8 | 286.814 | 265.5409 | 1.986 | 1.8736 | 4.6667
45618.3222 | On | Off | Off | Off | Off | Normal Operation | 53 | 53 | 53 | 29.4 | 49 | 6.3 | -3 | 69.5 | 75.8 | 2 | 7.5 | 20 | 179 | 56 | -2.3 | -3.1 | 45.8 | 43.3 | 48 | 286 | 280 | 2000 | 22.8 | 26.6 | 550 | 50.2 | Room | On | 27.7 | 43.1 | 47.8 | 45.65 | 1008.4034 | 4016.941 | 4.7 | 8789.3376 | 4.3 | 106% | 2.2 | 7500 | 29.4 | 69.5 | 553.0851 | 45.8 | 286.814 | 266.2711 | 1.9805 | 1.8684 | 4.6667
45618.3223 | On | Off | Off | Off | Off | Normal Operation | 53 | 47 | 53 | 29.6 | 50 | 6.3 | -3 | 70 | 76.2 | 2 | 7.5 | 21 | 179 | 56 | -2.3 | -3.1 | 46 | 43.5 | 48.3 | 286 | 280 | 2000 | 23 | 26.3 | 550 | 50.2 | Room | On | 27.7 | 43.1 | 47.8 | 45.9 | 1008.2722 | 4016.941 | 4.8 | 8975.1766 | 4.3 | 106% | 1.9 | 7500 | 29.6 | 70 | 553.5917 | 46 | 287.2389 | 266.3528 | 2.0218 | 1.9074 | 4.6984
45618.3224 | On | Off | Off | Off | Off | Normal Operation | 53 | 47 | 53 | 29.5 | 50 | 6.3 | -3 | 70.2 | 76.2 | 2 | 7.5 | 21 | 179 | 56 | -2.3 | -3.1 | 46 | 43.5 | 48.3 | 286 | 280 | 2000 | 23 | 25.8 | 550 | 50.2 | Room | On | 27.7 | 43.1 | 47.8 | 45.9 | 1008.2722 | 4016.941 | 4.8 | 8975.1766 | 4.3 | 106% | 1.9 | 7500 | 29.5 | 70.2 | 554.1611 | 46 | 287.226 | 266.9351 | 2.0174 | 1.9032 | 4.6825
45618.3226 | On | Off | Off | Off | Off | Normal Operation | 52 | 47 | 52 | 29.5 | 50 | 6.3 | -3 | 70.2 | 76.7 | 2 | 7.5 | 20 | 179 | 56 | -2.3 | -3.1 | 46.1 | 43.6 | 48.6 | 286 | 280 | 2000 | 23 | 25.8 | 550 | 50.2 | Room | On | 27.5 | 43.6 | 48.6 | 46.1 | 1008.167 | 4018.1167 | 5 | 9283.3869 | 4.3 | 104% | 1.6 | 7500 | 29.5 | 70.2 | 554.1611 | 46.1 | 287.4257 | 266.7354 | 2.0882 | 2.0079 | 4.6825
45618.3227 | On | Off | Off | Off | Off | Normal Operation | 51 | 47 | 52 | 29.2 | 49 | 6.3 | -3 | 70.5 | 77.1 | 2 | 7.3 | 20 | 179 | 56 | -2.3 | -3.2 | 46.1 | 43.1 | 48.3 | 281 | 280 | 2000 | 23.1 | 26.2 | 550 | 50.2 | Room | On | 27.5 | 43.6 | 48.6 | 45.7 | 1008.3772 | 4018.1167 | 5.2 | 9656.7358 | 4.3 | 104% | 1.9 | 7300 | 29.2 | 70.5 | 555.3104 | 46.1 | 287.387 | 267.9234 | 2.1626 | 2.0794 | 4.6349
45618.3228 | On | Off | Off | Off | Off | Normal Operation | 51 | 47 | 51 | 28.9 | 49 | 6.3 | -3 | 70.8 | 77.4 | 2 | 7 | 20 | 179 | 56 | -2.3 | -3.1 | 46.1 | 42.7 | 47.8 | 281 | 280 | 2000 | 23 | 25.2 | 550 | 50.2 | Room | On | 27.5 | 43.6 | 48.6 | 45.25 | 1008.6127 | 4018.1167 | 5.1 | 9473.241 | 4.3 | 102% | 2.4 | 7000 | 28.9 | 70.8 | 556.4473 | 46.1 | 287.3482 | 269.099 | 2.1122 | 2.0708 | 4.5873
45618.3229 | On | Off | Off | Off | Off | Normal Operation | 50 | 47 | 50 | 28.9 | 49 | 6.3 | -3 | 70.8 | 77.7 | 2 | 7 | 20 | 179 | 56 | -2.3 | -3 | 45.8 | 42.7 | 47.6 | 281 | 273 | 2000 | 22.8 | 24.1 | 550 | 50.2 | Room | On | 27.5 | 43.6 | 48.6 | 45.15 | 1008.6648 | 4018.1167 | 4.9 | 9102.2121 | 4.3 | 100% | 2.6 | 7000 | 28.9 | 70.8 | 556.4473 | 45.8 | 286.7505 | 269.6968 | 2.025 | 2.025 | 4.5873
45618.323 | On | Off | Off | Off | Off | Normal Operation | 49 | 54 | 50 | 28.7 | 48 | 6.3 | -3 | 70.8 | 77.8 | 2 | 6.9 | 20 | 177 | 56 | -2.3 | -3 | 45.8 | 42.7 | 47.6 | 281 | 273 | 2000 | 22.8 | 24 | 550 | 50.2 | Room | On | 27.9 | 42.7 | 47.6 | 45.15 | 1008.6648 | 4016.0005 | 4.9 | 9229.7445 | 4.3 | 100% | 2.6 | 6900 | 28.7 | 70.8 | 556.8406 | 45.8 | 286.7252 | 270.1154 | 2.0502 | 2.0502 | 4.5556
45618.3231 | On | Off | Off | Off | Off | Normal Operation | 49 | 54 | 49 | 28.5 | 48 | 6.4 | -2 | 70.7 | 77.8 | 2 | 6.7 | 20 | 177 | 56 | -2.2 | -2.9 | 45.6 | 42.4 | 47.3 | 281 | 273 | 2000 | 22.7 | 23.6 | 550 | 50.2 | Room | On | 27.9 | 42.7 | 47.6 | 44.85 | 1008.821 | 4016.0005 | 4.9 | 9231.1736 | 4.2 | 98% | 2.9 | 6700 | 28.5 | 70.7 | 557.0547 | 45.6 | 286.3019 | 270.7528 | 2.0457 | 2.0874 | 4.4531
45618.3232 | On | Off | Off | Off | Off | Normal Operation | 50 | 54 | 50 | 28.5 | 48 | 6.4 | -2 | 70.2 | 77.7 | 2 | 6.8 | 20 | 177 | 56 | -2.2 | -2.9 | 45.5 | 42.5 | 47.3 | 281 | 273 | 2000 | 22.6 | 23.6 | 540 | 50.2 | Room | On | 27.9 | 42.7 | 47.6 | 44.9 | 1008.795 | 4016.0005 | 4.8 | 9042.5493 | 4.2 | 100% | 2.9 | 6800 | 28.5 | 70.2 | 556.1653 | 45.5 | 286.103 | 270.0623 | 2.009 | 2.009 | 4.4531
45618.3234 | On | Off | Off | Off | Off | Normal Operation | 51 | 54 | 51 | 28.5 | 48 | 6.4 | -2 | 70.2 | 77.4 | 2 | 6.8 | 20 | 177 | 56 | -2.2 | -2.9 | 45.3 | 42.5 | 47.3 | 280 | 273 | 2000 | 22.7 | 24.1 | 550 | 50.2 | Room | On | 27.9 | 42.7 | 47.6 | 44.9 | 1008.795 | 4016.0005 | 4.8 | 9042.5493 | 4.2 | 102% | 2.9 | 6800 | 28.5 | 70.2 | 556.1653 | 45.3 | 285.7051 | 270.4602 | 2.006 | 1.9667 | 4.4531
45618.3235 | On | Off | Off | Off | Off | Normal Operation | 51 | 54 | 51 | 28.2 | 48 | 6.3 | -3 | 70 | 77.1 | 2 | 6.9 | 20 | 177 | 56 | -2.1 | -2.9 | 45.3 | 42 | 47.1 | 280 | 273 | 2000 | 22.6 | 24.3 | 550 | 50.2 | Room | On | 27.9 | 42.5 | 47.3 | 44.55 | 1008.9767 | 4015.5302 | 5.1 | 9608.3136 | 4.1 | 102% | 3.1 | 6900 | 28.2 | 70 | 556.4074 | 45.3 | 285.6682 | 270.7392 | 2.1294 | 2.0876 | 4.4762
45618.3236 | On | Off | Off | Off | Off | Normal Operation | 52 | 54 | 52 | 28.3 | 48 | 6.3 | -3 | 70 | 77 | 2 | 7 | 20 | 177 | 55 | -2.1 | -2.9 | 45 | 42 | 47.1 | 280 | 273 | 2000 | 22.4 | 23.7 | 550 | 50.2 | Room | On | 27.9 | 42.5 | 47.3 | 44.55 | 1008.9767 | 4015.5302 | 5.1 | 9608.3136 | 4.1 | 104% | 3.1 | 7000 | 28.3 | 70 | 556.2084 | 45 | 285.0841 | 271.1243 | 2.1263 | 2.0445 | 4.4921
45618.3237 | On | Off | Off | Off | Off | Normal Operation | 53 | 54 | 53 | 28.3 | 48 | 6.3 | -3 | 70 | 76.8 | 2 | 7 | 20 | 177 | 55 | -2.2 | -3 | 45 | 42 | 47.1 | 280 | 273 | 2000 | 22.3 | 23.2 | 550 | 50.2 | Room | On | 27.9 | 42.5 | 47.3 | 44.55 | 1008.9767 | 4015.5302 | 5.1 | 9608.3136 | 4.2 | 106% | 3.1 | 7000 | 28.3 | 70 | 556.2084 | 45 | 285.0841 | 271.1243 | 2.1263 | 2.006 | 4.4921
45618.3238 | On | Off | Off | Off | Off | Normal Operation | 53 | 54 | 53 | 28.7 | 48 | 6.3 | -3 | 69.8 | 76.7 | 2 | 7.2 | 20 | 177 | 55 | -2.3 | -3 | 45 | 42.1 | 47.1 | 280 | 272 | 2000 | 22.1 | 22.8 | 550 | 50.2 | Room | On | 27.9 | 42.5 | 47.3 | 44.6 | 1008.9508 | 4015.5302 | 5 | 9419.6734 | 4.3 | 106% | 3.1 | 7200 | 28.7 | 69.8 | 555.0514 | 45 | 285.1325 | 269.919 | 2.0939 | 1.9754 | 4.5556
45618.3239 | On | Off | Off | Off | Off | Normal Operation | 54 | 54 | 54 | 28.7 | 48 | 6.2 | -3 | 69.8 | 76.5 | 2 | 7.3 | 20 | 177 | 55 | -2.4 | -3.1 | 45 | 42.1 | 47.3 | 280 | 272 | 2000 | 22 | 22.7 | 550 | 50.2 | Room | On | 27.9 | 42.1 | 47.1 | 44.7 | 1008.8989 | 4014.5897 | 5.2 | 9793.6623 | 4.4 | 108% | 2.9 | 7300 | 28.7 | 69.8 | 555.0514 | 45 | 285.1325 | 269.919 | 2.177 | 2.0158 | 4.629
45618.3241 | On | Off | Off | Off | Off | Normal Operation | 54 | 54 | 54 | 28.7 | 48 | 6.2 | -3 | 69.5 | 76.5 | 2 | 7.3 | 20 | 177 | 55 | -2.5 | -3.3 | 45 | 42.1 | 47.3 | 280 | 272 | 2000 | 21.8 | 22.3 | 550 | 50.2 | Room | On | 27.9 | 42.1 | 47.1 | 44.7 | 1008.8989 | 4014.5897 | 5.2 | 9793.6623 | 4.5 | 108% | 2.9 | 7300 | 28.7 | 69.5 | 554.5147 | 45 | 285.1325 | 269.3822 | 2.1814 | 2.0198 | 4.629
45618.3242 | On | Off | Off | Off | Off | Normal Operation | 54 | 54 | 54 | 28.7 | 48 | 6.2 | -3 | 69.5 | 76.2 | 2 | 7.3 | 20 | 177 | 55 | -2.5 | -3.3 | 45.1 | 42.1 | 47.3 | 280 | 272 | 2000 | 21.8 | 22.3 | 550 | 50.2 | Room | On | 27.9 | 42.1 | 47.1 | 44.7 | 1008.8989 | 4014.5897 | 5.2 | 9793.6623 | 4.5 | 108% | 2.9 | 7300 | 28.7 | 69.5 | 554.5147 | 45.1 | 285.3315 | 269.1831 | 2.183 | 2.0213 | 4.629
45618.3243 | On | Off | Off | Off | Off | Normal Operation | 54 | 54 | 54 | 28.8 | 49 | 6.2 | -3 | 69.4 | 76.1 | 1.9 | 7.3 | 20 | 177 | 55 | -2.6 | -3.3 | 45.1 | 42 | 47.3 | 280 | 272 | 2000 | 21.6 | 22.1 | 550 | 50.2 | Room | On | 27.9 | 42.1 | 47.1 | 44.65 | 1008.9249 | 4014.5897 | 5.3 | 9982.2586 | 4.5 | 108% | 2.9 | 7300 | 28.8 | 69.4 | 554.132 | 45.1 | 285.3437 | 268.7883 | 2.2283 | 2.0632 | 4.6452
45618.3244 | On | Off | Off | Off | Off | Normal Operation | 54 | 57 | 54 | 28.7 | 48 | 6.2 | -3 | 69.1 | 76 | 1.9 | 7.3 | 20 | 177 | 55 | -2.6 | -3.4 | 45.1 | 42 | 47.3 | 280 | 272 | 2000 | 21.5 | 22.1 | 550 | 50.3 | Room | On | 27.9 | 42 | 47.3 | 44.65 | 1008.9249 | 4014.3546 | 5.3 | 9981.674 | 4.5 | 108% | 3 | 7300 | 28.7 | 69.1 | 553.799 | 45.1 | 285.3315 | 268.4675 | 2.2308 | 2.0656 | 4.629
45618.3245 | On | Off | Off | Off | Off | Normal Operation | 54 | 57 | 54 | 29 | 49 | 6.2 | -3 | 68.8 | 75.4 | 1.9 | 7.4 | 20 | 180 | 55 | -2.7 | -3.4 | 45.1 | 42.2 | 47.3 | 280 | 272 | 2000 | 21.6 | 22.1 | 550 | 50.3 | Room | On | 27.9 | 42 | 47.3 | 44.75 | 1008.873 | 4014.3546 | 5.1 | 9604.513 | 4.6 | 108% | 3 | 7400 | 29 | 68.8 | 552.6407 | 45.1 | 285.368 | 267.2727 | 2.1561 | 1.9964 | 4.6774
45618.3246 | On | Off | Off | Off | Off | Normal Operation | 55 | 57 | 55 | 28.9 | 49 | 6.2 | -3 | 68.4 | 75.1 | 1.9 | 7.3 | 20 | 180 | 54 | -2.7 | -3.5 | 45.3 | 42.1 | 47.5 | 280 | 272 | 2000 | 21.6 | 22.1 | 550 | 50.3 | Room | On | 27.9 | 42 | 47.3 | 44.8 | 1008.847 | 4014.3546 | 5.4 | 10169.2226 | 4.6 | 110% | 2.8 | 7300 | 28.9 | 68.4 | 552.1284 | 45.3 | 285.7543 | 266.3741 | 2.2906 | 2.0824 | 4.6613
45618.3248 | On | Off | Off | Off | Off | Normal Operation | 56 | 57 | 55 | 28.9 | 49 | 6.2 | -3 | 68 | 74.8 | 1.9 | 7.4 | 20 | 180 | 54 | -2.7 | -3.5 | 45.3 | 42 | 47.5 | 280 | 271 | 2000 | 21.6 | 22 | 550 | 50.3 | Room | On | 27.9 | 42 | 47.3 | 44.75 | 1008.873 | 4014.3546 | 5.5 | 10357.8082 | 4.6 | 110% | 2.8 | 7400 | 28.9 | 68 | 551.4086 | 45.3 | 285.7543 | 265.6543 | 2.3394 | 2.1267 | 4.6613
45618.3249 | On | Off | Off | Off | Off | Normal Operation | 56 | 57 | 56 | 29.3 | 49 | 6.2 | -3 | 67.5 | 74.3 | 1.9 | 7.7 | 20 | 180 | 54 | -2.7 | -3.5 | 45.5 | 42.4 | 47.6 | 280 | 271 | 2000 | 21.5 | 22 | 550 | 50.3 | Room | On | 27.7 | 42.4 | 47.6 | 45 | 1008.743 | 4015.2951 | 5.2 | 9723.6623 | 4.6 | 112% | 2.7 | 7700 | 29.3 | 67.5 | 549.6495 | 45.5 | 286.2026 | 263.4469 | 2.2146 | 1.9773 | 4.7258
45618.325 | On | Off | Off | Off | Off | Normal Operation | 57 | 57 | 57 | 29.1 | 49 | 6.2 | -3 | 67.1 | 74 | 2 | 7.7 | 20 | 180 | 54 | -2.7 | -3.5 | 45.6 | 42.1 | 47.7 | 280 | 271 | 2000 | 21.5 | 22 | 550 | 50.3 | Room | On | 27.7 | 42.4 | 47.6 | 44.9 | 1008.795 | 4015.2951 | 5.6 | 10472.1765 | 4.7 | 114% | 2.6 | 7700 | 29.1 | 67.1 | 549.356 | 45.6 | 286.3771 | 262.9789 | 2.3893 | 2.0959 | 4.6935
45618.3251 | On | Off | Off | Off | Off | Normal Operation | 57 | 54 | 57 | 29.2 | 49 | 6.1 | -4 | 66.7 | 73.4 | 2 | 7.7 | 20 | 180 | 54 | -2.7 | -3.6 | 45.6 | 42 | 47.6 | 280 | 271 | 2000 | 21.4 | 21.6 | 550 | 50.3 | Room | On | 27.7 | 42.4 | 47.6 | 44.8 | 1008.847 | 4015.2951 | 5.6 | 10472.716 | 4.7 | 114% | 2.7 | 7700 | 29.2 | 66.7 | 548.4128 | 45.6 | 286.3897 | 262.0231 | 2.3981 | 2.1036 | 4.7869
45618.3252 | On | Off | Off | Off | Off | Normal Operation | 57 | 54 | 57 | 29.3 | 49 | 6.1 | -4 | 66.4 | 73 | 2 | 7.7 | 20 | 180 | 54 | -2.8 | -3.6 | 45.6 | 42.1 | 47.6 | 280 | 271 | 2000 | 21.2 | 21.5 | 550 | 50.3 | Room | On | 27.7 | 42.4 | 47.6 | 44.85 | 1008.821 | 4015.2951 | 5.5 | 10285.4383 | 4.8 | 114% | 2.7 | 7700 | 29.3 | 66.4 | 547.6471 | 45.6 | 286.4022 | 261.2449 | 2.3623 | 2.0722 | 4.8033
45618.3253 | On | Off | Off | Off | Off | Normal Operation | 56 | 54 | 56 | 29.5 | 50 | 6.2 | -3 | 66 | 72.4 | 2 | 7.7 | 20 | 180 | 54 | -2.9 | -3.7 | 45.8 | 42.4 | 47.8 | 280 | 271 | 2000 | 21.2 | 21.5 | 550 | 50.2 | Room | On | 28.1 | 42.1 | 47.6 | 45.1 | 1008.6909 | 4014.5897 | 5.4 | 10241.1354 | 4.9 | 112% | 2.4 | 7700 | 29.5 | 66 | 546.4713 | 45.8 | 286.8266 | 259.6446 | 2.3666 | 2.113 | 4.7581
45618.3254 | On | Off | Off | Off | Off | Normal Operation | 55 | 54 | 55 | 29.3 | 49 | 6.2 | -3 | 65.5 | 71.8 | 2 | 7.6 | 20 | 180 | 54 | -2.8 | -3.6 | 46 | 42.2 | 47.8 | 280 | 271 | 2000 | 21.3 | 21.7 | 550 | 50.2 | Room | On | 28.1 | 42.1 | 47.6 | 45 | 1008.743 | 4014.5897 | 5.6 | 10620.9851 | 4.8 | 110% | 2.4 | 7600 | 29.3 | 65.5 | 546.0087 | 46 | 287.2003 | 258.8084 | 2.4623 | 2.2384 | 4.7258
45618.3256 | On | Off | Off | Off | Off | Normal Operation | 55 | 54 | 55 | 29.3 | 49 | 6.2 | -3 | 65 | 71.2 | 2 | 7.5 | 20 | 180 | 53 | -2.8 | -3.6 | 46 | 42.2 | 47.7 | 280 | 271 | 2000 | 21.3 | 21.7 | 550 | 50.2 | Room | On | 28.1 | 42.1 | 47.6 | 44.95 | 1008.769 | 4014.5897 | 5.5 | 10431.5938 | 4.8 | 110% | 2.5 | 7500 | 29.3 | 65 | 545.0985 | 46 | 287.2003 | 257.8982 | 2.4269 | 2.2063 | 4.7258
45618.3257 | On | Off | Off | Off | Off | Normal Operation | 54 | 54 | 54 | 29.3 | 49 | 6.2 | -3 | 65 | 71.2 | 2 | 7.5 | 20 | 180 | 53 | -2.8 | -3.6 | 46 | 42.2 | 47.7 | 280 | 271 | 2000 | 21.3 | 21.7 | 550 | 50.2 | Room | On | 28.1 | 42.1 | 47.6 | 44.95 | 1008.769 | 4014.5897 | 5.5 | 10431.5938 | 4.8 | 108% | 2.5 | 7500 | 29.3 | 65 | 545.0985 | 46 | 287.2003 | 257.8982 | 2.4269 | 2.2471 | 4.7258
45618.3258 | On | Off | Off | Off | Off | Normal Operation | 54 | 54 | 54 | 29.5 | 50 | 6.2 | -3 | 64.7 | 70.7 | 2 | 7.4 | 20 | 180 | 53 | -2.7 | -3.5 | 46 | 42.5 | 47.7 | 280 | 271 | 2000 | 21.4 | 21.8 | 550 | 50.2 | Room | On | 28.3 | 42.5 | 47.7 | 45.1 | 1008.6909 | 4015.5302 | 5.2 | 9934.3519 | 4.7 | 108% | 2.5 | 7400 | 29.5 | 64.7 | 544.0911 | 46 | 287.226 | 256.8651 | 2.3205 | 2.1486 | 4.7581
45618.3259 | On | Off | Off | Off | Off | Normal Operation | 54 | 54 | 54 | 29.6 | 50 | 6.2 | -3 | 64.2 | 70.2 | 2 | 7.5 | 20 | 180 | 53 | -2.6 | -3.4 | 46 | 42.8 | 47.8 | 280 | 271 | 2000 | 21.7 | 22.2 | 550 | 50.2 | Room | On | 28.3 | 42.5 | 47.7 | 45.3 | 1008.5866 | 4015.5302 | 5 | 9551.2733 | 4.6 | 108% | 2.4 | 7500 | 29.6 | 64.2 | 542.9417 | 46 | 287.2389 | 255.7029 | 2.2412 | 2.0752 | 4.7742
45618.326 | On | Off | Off | Off | Off | Normal Operation | 54 | 54 | 54 | 29.5 | 50 | 6.2 | -3 | 64 | 69.7 | 2 | 7.4 | 20 | 180 | 53 | -2.6 | -3.3 | 46.1 | 42.8 | 48 | 280 | 271 | 2000 | 21.8 | 22.3 | 550 | 50.2 | Room | On | 28.3 | 42.5 | 47.7 | 45.4 | 1008.5343 | 4015.5302 | 5.2 | 9932.8096 | 4.6 | 108% | 2.2 | 7400 | 29.5 | 64 | 542.8094 | 46.1 | 287.4257 | 255.3837 | 2.3336 | 2.1608 | 4.7581
45618.3261 | On | Off | Off | Off | Off | Normal Operation | 54 | 54 | 54 | 29.5 | 50 | 6.2 | -3 | 64 | 69.5 | 2 | 7.5 | 20 | 178 | 53 | -2.6 | -3.3 | 46.1 | 42.8 | 48 | 280 | 271 | 2000 | 21.8 | 22.3 | 550 | 50.2 | Room | On | 28.3 | 42.5 | 47.7 | 45.4 | 1008.5343 | 4015.5302 | 5.2 | 9932.8096 | 4.6 | 108% | 2.2 | 7500 | 29.5 | 64 | 542.8094 | 46.1 | 287.4257 | 255.3837 | 2.3336 | 2.1608 | 4.7581
45618.3263 | On | Off | Off | Off | Off | Normal Operation | 54 | 54 | 54 | 29.6 | 50 | 6.2 | -3 | 64 | 69.4 | 2 | 7.5 | 20 | 178 | 53 | -2.5 | -3.3 | 46.1 | 42.8 | 48 | 280 | 271 | 2000 | 21.8 | 22.3 | 550 | 50.2 | Room | On | 28.3 | 42.8 | 48 | 45.4 | 1008.5343 | 4016.2356 | 5.2 | 9934.5544 | 4.5 | 108% | 2.2 | 7500 | 29.6 | 64 | 542.5745 | 46.1 | 287.4386 | 255.1359 | 2.3363 | 2.1632 | 4.7742
45618.3264 | On | Off | Off | Off | Off | Normal Operation | 54 | 54 | 54 | 29.6 | 50 | 6.3 | -3 | 64 | 69.4 | 2 | 7.5 | 20 | 178 | 54 | -2.5 | -3.3 | 46.3 | 43 | 48 | 280 | 271 | 2000 | 21.8 | 22.3 | 550 | 50.2 | Room | On | 28.3 | 42.8 | 48 | 45.5 | 1008.482 | 4016.2356 | 5 | 9551.9607 | 4.5 | 108% | 2.2 | 7500 | 29.6 | 64 | 542.5745 | 46.3 | 287.8382 | 254.7363 | 2.2498 | 2.0832 | 4.6984
45618.3265 | On | Off | Off | Off | Off | Normal Operation | 54 | 48 | 54 | 29.7 | 50 | 6.3 | -3 | 64.1 | 69.5 | 2 | 7.5 | 20 | 178 | 54 | -2.5 | -3.2 | 46.3 | 43.1 | 48.3 | 280 | 271 | 2000 | 22 | 22.3 | 550 | 50.2 | Room | On | 28.3 | 42.8 | 48 | 45.7 | 1008.3772 | 4016.2356 | 5.2 | 9933.0069 | 4.5 | 108% | 1.9 | 7500 | 29.7 | 64.1 | 542.5232 | 46.3 | 287.8512 | 254.672 | 2.3402 | 2.1668 | 4.7143
45618.3266 | On | Off | Off | Off | Off | Normal Operation | 54 | 48 | 54 | 29.9 | 50 | 6.3 | -3 | 64.2 | 69.7 | 2 | 7.6 | 20 | 178 | 54 | -2.5 | -3.2 | 46.5 | 43.3 | 48.6 | 280 | 271 | 2000 | 22 | 22.4 | 550 | 50.2 | Room | On | 28.3 | 42.8 | 48 | 45.95 | 1008.2459 | 4016.2356 | 5.3 | 10122.7079 | 4.5 | 108% | 1.6 | 7600 | 29.9 | 64.2 | 542.2375 | 46.5 | 288.2773 | 253.9602 | 2.3916 | 2.2144 | 4.746
45618.3267 | On | Off | Off | Off | Off | Normal Operation | 53 | 48 | 53 | 29.9 | 50 | 6.2 | -3 | 64.2 | 69.8 | 2 | 7.5 | 20 | 178 | 54 | -2.5 | -3.3 | 46.6 | 43.3 | 48.6 | 280 | 271 | 2000 | 22.1 | 22.5 | 550 | 50.2 | Room | On | 28.1 | 43.3 | 48.6 | 45.95 | 1008.2459 | 4017.4113 | 5.3 | 10054.1116 | 4.5 | 106% | 1.6 | 7500 | 29.9 | 64.2 | 542.2375 | 46.6 | 288.4773 | 253.7602 | 2.3772 | 2.2427 | 4.8226
45618.3268 | On | Off | Off | Off | Off | Normal Operation | 52 | 48 | 52 | 29.8 | 50 | 6.3 | -3 | 64.5 | 70.1 | 2 | 7.4 | 20 | 178 | 54 | -2.5 | -3.3 | 46.6 | 43.3 | 48.6 | 280 | 271 | 2000 | 22.1 | 22.5 | 550 | 50.2 | Room | On | 28.1 | 43.3 | 48.6 | 45.95 | 1008.2459 | 4017.4113 | 5.3 | 10054.1116 | 4.5 | 104% | 1.6 | 7400 | 29.8 | 64.5 | 543.0267 | 46.6 | 288.464 | 254.5626 | 2.3697 | 2.2786 | 4.7302
45618.3269 | On | Off | Off | Off | Off | Normal Operation | 52 | 48 | 52 | 29.8 | 50 | 6.3 | -3 | 64.7 | 70.2 | 2 | 7.3 | 21 | 178 | 54 | -2.5 | -3.3 | 46.6 | 43.5 | 48.6 | 280 | 271 | 2000 | 22.2 | 22.5 | 550 | 50.2 | Room | On | 28.1 | 43.3 | 48.6 | 46.05 | 1008.1933 | 4017.4113 | 5.1 | 9674.2062 | 4.5 | 104% | 1.6 | 7300 | 29.8 | 64.7 | 543.396 | 46.6 | 288.464 | 254.932 | 2.2769 | 2.1893 | 4.7302
45618.3271 | On | Off | Off | Off | Off | Normal Operation | 51 | 48 | 51 | 29.8 | 50 | 6.3 | -3 | 64.8 | 70.5 | 2 | 7.2 | 20 | 178 | 54 | -2.4 | -3.2 | 46.6 | 43.6 | 49 | 280 | 271 | 2000 | 22.4 | 22.7 | 550 | 50.2 | Room | On | 28.1 | 43.3 | 48.6 | 46.3 | 1008.0615 | 4017.4113 | 5.4 | 10241.9381 | 4.4 | 102% | 1.2 | 7200 | 29.8 | 64.8 | 543.5807 | 46.6 | 288.464 | 255.1167 | 2.4088 | 2.3615 | 4.7302
45618.3272 | On | Off | Off | Off | Off | Normal Operation | 50 | 40 | 51 | 29.8 | 50 | 6.3 | -3 | 65.1 | 70.8 | 2 | 7.2 | 20 | 178 | 54 | -2.4 | -3.1 | 46.6 | 43.6 | 49 | 280 | 271 | 2000 | 22.5 | 23 | 550 | 50.2 | Room | On | 28.1 | 43.6 | 49 | 46.3 | 1008.0615 | 4018.1167 | 5.4 | 10243.7365 | 4.4 | 102% | 1.2 | 7200 | 29.8 | 65.1 | 544.1348 | 46.6 | 288.464 | 255.6707 | 2.404 | 2.3568 | 4.7302
45618.3273 | On | Off | Off | Off | Off | Normal Operation | 50 | 40 | 50 | 29.7 | 50 | 6.3 | -3 | 65.2 | 71.1 | 2 | 7.1 | 21 | 178 | 54 | -2.3 | -3 | 46.6 | 43.8 | 49 | 280 | 271 | 2000 | 22.7 | 23.2 | 550 | 50.2 | Room | On | 28.1 | 43.6 | 49 | 46.4 | 1008.0087 | 4018.1167 | 5.2 | 9863.822 | 4.3 | 100% | 1.2 | 7100 | 29.7 | 65.2 | 544.5489 | 46.6 | 288.4508 | 256.0981 | 2.3109 | 2.3109 | 4.7143
45618.3274 | On | Off | Off | Off | Off | Normal Operation | 49 | 40 | 49 | 29.7 | 50 | 6.3 | -3 | 65.2 | 71.1 | 2 | 7.1 | 21 | 178 | 54 | -2.3 | -3 | 46.6 | 43.8 | 49 | 280 | 271 | 2000 | 22.7 | 23.2 | 550 | 50.2 | Room | On | 28.1 | 43.6 | 49 | 46.4 | 1008.0087 | 4018.1167 | 5.2 | 9863.822 | 4.3 | 98% | 1.2 | 7100 | 29.7 | 65.2 | 544.5489 | 46.6 | 288.4508 | 256.0981 | 2.3109 | 2.3581 | 4.7143
45618.3275 | On | Off | Off | Off | Off | Normal Operation | 48 | 40 | 49 | 29.6 | 50 | 6.3 | -3 | 65.5 | 71.4 | 2 | 7 | 20 | 178 | 54 | -2.2 | -2.9 | 46.6 | 43.8 | 49 | 280 | 269 | 2000 | 22.8 | 23.4 | 550 | 50.2 | Room | On | 28.1 | 43.6 | 49 | 46.4 | 1008.0087 | 4018.1167 | 5.2 | 9863.822 | 4.2 | 98% | 1.2 | 7000 | 29.6 | 65.5 | 545.3288 | 46.6 | 288.4375 | 256.8913 | 2.3038 | 2.3508 | 4.6984
45618.3276 | On | Off | Off | Off | Off | Normal Operation | 48 | 40 | 48 | 29.6 | 50 | 6.4 | -2 | 66 | 71.7 | 2 | 6.9 | 20 | 178 | 54 | -2.2 | -2.9 | 46.6 | 43.8 | 48.6 | 280 | 269 | 2000 | 23.1 | 23.7 | 550 | 50.2 | Room | On | 28.1 | 43.8 | 48.6 | 46.2 | 1008.1142 | 4018.5869 | 4.8 | 9107.0858 | 4.2 | 96% | 1.6 | 6900 | 29.6 | 66 | 546.2469 | 46.6 | 288.4375 | 257.8094 | 2.1195 | 2.2078 | 4.625
45618.3277 | On | Off | Off | Off | Off | Normal Operation | 47 | 40 | 47 | 29.5 | 50 | 6.4 | -2 | 66.4 | 72.1 | 2 | 6.8 | 20 | 184 | 55 | -2.1 | -2.8 | 46.5 | 44 | 48.6 | 280 | 269 | 2000 | 23.1 | 24 | 550 | 50.2 | Room | On | 28.1 | 43.8 | 48.6 | 46.3 | 1008.0615 | 4018.5869 | 4.6 | 8727.1671 | 4.1 | 94% | 1.6 | 6800 | 29.5 | 66.4 | 547.2036 | 46.5 | 288.2245 | 258.9792 | 2.0219 | 2.151 | 4.6094
45618.3279 | On | Off | Off | Off | Off | Normal Operation | 46 | 46 | 47 | 29.5 | 50 | 6.4 | -2 | 66.7 | 72.5 | 2.1 | 6.7 | 20 | 184 | 55 | -2.1 | -2.7 | 46.5 | 44.2 | 48.6 | 280 | 269 | 2000 | 23.2 | 25.4 | 550 | 50.2 | Room | On | 28.1 | 43.8 | 48.6 | 46.4 | 1008.0087 | 4018.5869 | 4.4 | 8347.2877 | 4.2 | 94% | 1.6 | 6700 | 29.5 | 66.7 | 547.7529 | 46.5 | 288.2245 | 259.5284 | 1.9298 | 2.053 | 4.6094
45618.328 | On | Off | Off | Off | Off | Normal Operation | 46 | 46 | 46 | 29.5 | 50 | 6.5 | -2 | 67.2 | 73.1 | 2 | 6.6 | 20 | 184 | 55 | -2 | -2.6 | 46.5 | 44.4 | 48.6 | 280 | 258 | 2000 | 23.4 | 28.3 | 550 | 50.2 | Room | On | 28.1 | 43.8 | 48.6 | 46.5 | 1007.9558 | 4018.5869 | 4.2 | 7967.4476 | 4 | 92% | 1.6 | 6600 | 29.5 | 67.2 | 548.6684 | 46.5 | 288.2245 | 260.4439 | 1.8355 | 1.9951 | 4.5385
45618.3281 | On | Off | Off | Off | Off | Normal Operation | 46 | 46 | 46 | 29.3 | 49 | 6.5 | -2 | 67.8 | 73.7 | 2 | 6.5 | 20 | 184 | 55 | -1.9 | -2.5 | 46.5 | 44.6 | 48.6 | 280 | 258 | 2000 | 23.6 | 31.2 | 550 | 50.2 | Room | On | 28.1 | 44.6 | 48.6 | 46.6 | 1007.9029 | 4020.468 | 4 | 7591.1986 | 3.9 | 92% | 1.6 | 6500 | 29.3 | 67.8 | 550.1956 | 46.5 | 288.1981 | 261.9976 | 1.7385 | 1.8896 | 4.5077
45618.3282 | On | Off | Off | Off | Off | Normal Operation | 46 | 46 | 46 | 29.3 | 49 | 6.5 | -2 | 68.4 | 74.3 | 2 | 6.5 | 20 | 184 | 56 | -1.9 | -2.4 | 46.3 | 44.6 | 48.6 | 274 | 258 | 2000 | 23.5 | 34.1 | 550 | 50.2 | Room | On | 28.1 | 44.6 | 48.6 | 46.6 | 1007.9029 | 4020.468 | 4 | 7591.1986 | 3.9 | 92% | 1.6 | 6500 | 29.3 | 68.4 | 551.2879 | 46.3 | 287.799 | 263.4889 | 1.7286 | 1.8789 | 4.5077
45618.3283 | On | Off | Off | Off | Off | Normal Operation | 46 | 46 | 46 | 29.4 | 49 | 6.5 | -2 | 69 | 74.8 | 2 | 6.5 | 20 | 184 | 56 | -1.8 | -2.3 | 46.3 | 44.6 | 48.6 | 274 | 258 | 2000 | 23.4 | 36.2 | 550 | 50.2 | Room | On | 28.1 | 44.6 | 48.6 | 46.6 | 1007.9029 | 4020.468 | 4 | 7591.1986 | 3.8 | 92% | 1.6 | 6500 | 29.4 | 69 | 552.1722 | 46.3 | 287.812 | 264.3602 | 1.7229 | 1.8727 | 4.5231
45618.3284 | On | Off | Off | Off | Off | Normal Operation | 46 | 46 | 46 | 29.6 | 50 | 6.5 | -2 | 69.5 | 75.5 | 2 | 6.6 | 20 | 184 | 57 | -1.7 | -2.3 | 46.3 | 45 | 48.6 | 274 | 258 | 2000 | 23.2 | 37.7 | 550 | 50.2 | Room | On | 28.1 | 44.6 | 48.6 | 46.8 | 1007.7968 | 4020.468 | 3.6 | 6831.36 | 3.7 | 92% | 1.6 | 6600 | 29.6 | 69.5 | 552.6736 | 46.3 | 287.8382 | 264.8354 | 1.5477 | 1.6823 | 4.5538
45618.3286 | On | Off | Off | Off | Off | Normal Operation | 46 | 40 | 46 | 29.6 | 50 | 6.5 | -2 | 70 | 76.2 | 2 | 6.5 | 20 | 184 | 58 | -1.7 | -2.2 | 46.3 | 45 | 49 | 274 | 258 | 2000 | 23.2 | 38.5 | 550 | 50.2 | Room | On | 27.5 | 45 | 49 | 47 | 1007.6906 | 4021.4085 | 4 | 7429.2818 | 3.7 | 92% | 1.2 | 6500 | 29.6 | 70 | 553.5917 | 46.3 | 287.8382 | 265.7535 | 1.6773 | 1.8232 | 4.5538
45618.3287 | On | Off | Off | Off | Off | Normal Operation | 46 | 40 | 46 | 29.5 | 50 | 6.5 | -2 | 70.5 | 77 | 2 | 6.5 | 20 | 184 | 59 | -1.7 | -2.2 | 46.3 | 44.8 | 49 | 274 | 258 | 2000 | 23.2 | 39 | 550 | 50.2 | Room | On | 27.5 | 45 | 49 | 46.9 | 1007.7438 | 4021.4085 | 4.2 | 7801.1574 | 3.7 | 92% | 1.2 | 6500 | 29.5 | 70.5 | 554.7104 | 46.3 | 287.8251 | 266.8853 | 1.7538 | 1.9063 | 4.5385
45618.3288 | On | Off | Off | Off | Off | Normal Operation | 45 | 40 | 45 | 29.7 | 50 | 6.5 | -2 | 70.8 | 77.5 | 2 | 6.4 | 20 | 184 | 59 | -1.6 | -2.1 | 46.3 | 45.1 | 49 | 274 | 258 | 2000 | 23.2 | 39.1 | 550 | 50.2 | Room | On | 27.5 | 45 | 49 | 47.05 | 1007.664 | 4021.4085 | 3.9 | 7243.3586 | 3.6 | 90% | 1.2 | 6400 | 29.7 | 70.8 | 554.8612 | 46.3 | 287.8512 | 267.01 | 1.6277 | 1.8085 | 4.5692
45618.3289 | On | Off | Off | Off | Off | Normal Operation | 44 | 40 | 45 | 29.7 | 50 | 6.6 | -1 | 71.1 | 78.1 | 2 | 6.4 | 20 | 184 | 60 | -1.6 | -2.1 | 46.3 | 45.1 | 49.2 | 275 | 254 | 2000 | 23.5 | 39.2 | 550 | 50.2 | Room | On | 27.5 | 45 | 49 | 47.15 | 1007.6108 | 4021.4085 | 4.1 | 7614.4106 | 3.6 | 90% | 1 | 6400 | 29.7 | 71.1 | 555.4137 | 46.3 | 287.8512 | 267.5625 | 1.7075 | 1.8972 | 4.5
45618.329 | On | Off | Off | Off | Off | Normal Operation | 44 | 40 | 44 | 29.7 | 50 | 6.6 | -1 | 71.1 | 78.1 | 2 | 6.4 | 20 | 184 | 60 | -1.6 | -2.1 | 46.3 | 45.1 | 49.2 | 275 | 254 | 2000 | 23.5 | 39.2 | 550 | 50.2 | Room | On | 27.5 | 45 | 49 | 47.15 | 1007.6108 | 4021.4085 | 4.1 | 7614.4106 | 3.6 | 88% | 1 | 6400 | 29.7 | 71.1 | 555.4137 | 46.3 | 287.8512 | 267.5625 | 1.7075 | 1.9403 | 4.5
45618.3291 | On | Off | Off | Off | Off | Normal Operation | 43 | 40 | 43 | 29.5 | 50 | 6.6 | -1 | 71.4 | 78.7 | 2 | 6.3 | 20 | 184 | 60 | -1.5 | -2 | 46.3 | 45.1 | 49.2 | 275 | 254 | 2000 | 23.6 | 39.4 | 550 | 50.2 | Room | On | 27.7 | 45.1 | 49.2 | 47.15 | 1007.6108 | 4021.6436 | 4.1 | 7670.2366 | 3.5 | 86% | 1 | 6300 | 29.5 | 71.4 | 556.3582 | 46.3 | 287.8251 | 268.5331 | 1.7138 | 1.9928 | 4.4697
45618.3293 | On | Off | Off | Off | Off | Normal Operation | 42 | 39 | 43 | 29.7 | 50 | 6.6 | -1 | 71.5 | 79 | 2 | 6.2 | 20 | 184 | 61 | -1.5 | -2 | 46.3 | 45.5 | 49.2 | 275 | 254 | 2000 | 23.7 | 39.8 | 550 | 50.2 | Room | On | 27.7 | 45.1 | 49.2 | 47.35 | 1007.5041 | 4021.6436 | 3.7 | 6921.1882 | 3.5 | 86% | 1 | 6200 | 29.7 | 71.5 | 556.1503 | 46.3 | 287.8512 | 268.2991 | 1.5478 | 1.7998 | 4.5
45618.3294 | On | Off | Off | Off | Off | Normal Operation | 42 | 39 | 42 | 29.5 | 50 | 6.6 | -1 | 71.5 | 79.2 | 1.9 | 6 | 20 | 180 | 61 | -1.4 | -2 | 46.3 | 45.5 | 49.2 | 275 | 242 | 2000 | 23.8 | 40 | 550 | 50.2 | Room | On | 27.7 | 45.1 | 49.2 | 47.35 | 1007.5041 | 4021.6436 | 3.7 | 6921.1882 | 3.3 | 84% | 1 | 6000 | 29.5 | 71.5 | 556.5413 | 46.3 | 287.8251 | 268.7162 | 1.5454 | 1.8397 | 4.4697
45618.3295 | On | Off | Off | Off | Off | Normal Operation | 41 | 39 | 41 | 29.4 | 49 | 6.7 | -1 | 71.7 | 79.5 | 1.9 | 5.9 | 20 | 180 | 62 | -1.3 | -1.8 | 46.3 | 45.5 | 49.2 | 275 | 242 | 2000 | 23.8 | 40.5 | 550 | 50.2 | Room | On | 27.7 | 45.1 | 49.2 | 47.35 | 1007.5041 | 4021.6436 | 3.7 | 6921.1882 | 3.2 | 82% | 1 | 5900 | 29.4 | 71.7 | 557.1015 | 46.3 | 287.812 | 269.2895 | 1.5421 | 1.8806 | 4.3881
45618.3296 | On | Off | Off | Off | Off | Normal Operation | 41 | 39 | 41 | 29.5 | 50 | 6.7 | -1 | 71.7 | 79.6 | 2 | 5.8 | 20 | 180 | 62 | -1.2 | -1.7 | 46.3 | 45.5 | 49 | 271 | 242 | 2000 | 23.5 | 41 | 550 | 50.3 | Room | On | 28.1 | 45.5 | 49.2 | 47.25 | 1007.5575 | 4022.5842 | 3.5 | 6643.5175 | 3.2 | 82% | 1.3 | 5800 | 29.5 | 71.7 | 556.9075 | 46.3 | 287.8251 | 269.0824 | 1.4814 | 1.8066 | 4.403
45618.3297 | On | Off | Off | Off | Off | Normal Operation | 40 | 39 | 40 | 29.3 | 49 | 6.7 | -1 | 71.5 | 79.6 | 2 | 5.7 | 20 | 180 | 62 | -1.1 | -1.6 | 46.3 | 45.5 | 49 | 271 | 242 | 2000 | 23.5 | 41.3 | 550 | 50.3 | Room | On | 28.1 | 45.5 | 49.2 | 47.25 | 1007.5575 | 4022.5842 | 3.5 | 6643.5175 | 3.1 | 80% | 1.3 | 5700 | 29.3 | 71.5 | 556.9311 | 46.3 | 287.799 | 269.1321 | 1.4811 | 1.8514 | 4.3731
45618.3298 | On | Off | Off | Off | Off | Normal Operation | 39 | 39 | 39 | 29.4 | 49 | 6.8 | -1 | 71.5 | 79.6 | 2 | 5.6 | 20 | 180 | 62 | -1 | -1.5 | 46.3 | 45.5 | 49 | 271 | 235 | 2000 | 23.7 | 41.3 | 550 | 50.3 | Room | On | 28.1 | 45.5 | 49.2 | 47.25 | 1007.5575 | 4022.5842 | 3.5 | 6643.5175 | 3 | 78% | 1.3 | 5600 | 29.4 | 71.5 | 556.7364 | 46.3 | 287.812 | 268.9243 | 1.4822 | 1.9003 | 4.3235
45618.3299 | On | Off | Off | Off | Off | Normal Operation | 39 | 39 | 39 | 29.5 | 50 | 6.8 | -1 | 71.4 | 79.6 | 2 | 5.6 | 20 | 180 | 62 | -1 | -1.4 | 46.3 | 45.6 | 49 | 271 | 235 | 2000 | 23.7 | 41.3 | 550 | 50.3 | Room | On | 28.1 | 45.5 | 49.2 | 47.3 | 1007.5308 | 4022.5842 | 3.4 | 6453.5319 | 3 | 78% | 1.3 | 5600 | 29.5 | 71.4 | 556.3582 | 46.3 | 287.8251 | 268.5331 | 1.442 | 1.8487 | 4.3382
45618.3301 | On | Off | Off | Off | Off | Normal Operation | 39 | 41 | 39 | 29.5 | 50 | 6.8 | -1 | 71.2 | 79.6 | 2 | 5.6 | 20 | 180 | 63 | -1 | -1.4 | 46.3 | 45.6 | 49 | 271 | 235 | 2000 | 23.7 | 41.6 | 550 | 50.2 | Room | On | 28.3 | 45.6 | 49 | 47.3 | 1007.5308 | 4022.8193 | 3.4 | 6499.8444 | 3 | 78% | 1.2 | 5600 | 29.5 | 71.2 | 555.992 | 46.3 | 287.8251 | 268.1669 | 1.4543 | 1.8645 | 4.3382
45618.3302 | On | Off | Off | Off | Off | Normal Operation | 40 | 41 | 40 | 29.6 | 50 | 6.8 | -1 | 71.1 | 79.6 | 2 | 5.7 | 20 | 180 | 63 | -1 | -1.3 | 46.3 | 45.6 | 49 | 271 | 235 | 2000 | 23.8 | 41.6 | 550 | 50.2 | Room | On | 28.3 | 45.6 | 49 | 47.3 | 1007.5308 | 4022.8193 | 3.4 | 6499.8444 | 3 | 80% | 1.2 | 5700 | 29.6 | 71.1 | 555.6115 | 46.3 | 287.8382 | 267.7733 | 1.4564 | 1.8205 | 4.3529
45618.3303 | On | Off | Off | Off | Off | Normal Operation | 40 | 41 | 40 | 29.7 | 50 | 6.7 | -1 | 71 | 79.5 | 2 | 5.7 | 20 | 180 | 63 | -1 | -1.3 | 46.3 | 45.8 | 49.2 | 272 | 235 | 2000 | 23.8 | 41.6 | 550 | 50.2 | Room | On | 28.3 | 45.6 | 49 | 47.5 | 1007.424 | 4022.8193 | 3.4 | 6499.1553 | 3 | 80% | 1 | 5700 | 29.7 | 71 | 555.2295 | 46.3 | 287.8512 | 267.3783 | 1.4584 | 1.823 | 4.4328
45618.3304 | On | Off | Off | Off | Off | Normal Operation | 41 | 41 | 41 | 29.7 | 50 | 6.7 | -1 | 71 | 79.5 | 2 | 5.9 | 20 | 180 | 63 | -1 | -1.4 | 46.5 | 45.8 | 49.4 | 272 | 235 | 2000 | 23.8 | 41.8 | 550 | 50.2 | Room | On | 28.3 | 45.6 | 49 | 47.6 | 1007.3705 | 4022.8193 | 3.6 | 6881.0932 | 3 | 82% | 0.8 | 5900 | 29.7 | 71 | 555.2295 | 46.5 | 288.2509 | 266.9786 | 1.5464 | 1.8859 | 4.4328
45618.3305 | On | Off | Off | Off | Off | Normal Operation | 41 | 41 | 41 | 29.7 | 50 | 6.7 | -1 | 71 | 79.5 | 2 | 5.9 | 20 | 180 | 63 | -1 | -1.4 | 46.5 | 45.8 | 49.4 | 272 | 235 | 2000 | 23.7 | 41.8 | 550 | 50.2 | Room | On | 28.1 | 45.8 | 49.4 | 47.6 | 1007.3705 | 4023.2895 | 3.6 | 6833.2623 | 3 | 82% | 0.8 | 5900 | 29.7 | 71 | 555.2295 | 46.5 | 288.2509 | 266.9786 | 1.5357 | 1.8728 | 4.4328
45618.3306 | On | Off | Off | Off | Off | Normal Operation | 41 | 40 | 41 | 29.6 | 50 | 6.7 | -1 | 71.1 | 79.5 | 2 | 5.9 | 20 | 180 | 63 | -1 | -1.4 | 46.5 | 45.6 | 49.4 | 272 | 235 | 2000 | 23.7 | 41.8 | 550 | 50.2 | Room | On | 28.1 | 45.8 | 49.4 | 47.5 | 1007.424 | 4023.2895 | 3.8 | 7213.271 | 3 | 82% | 0.8 | 5900 | 29.6 | 71.1 | 555.6115 | 46.5 | 288.2377 | 267.3738 | 1.6187 | 1.974 | 4.4179
45618.3308 | On | Off | Off | Off | Off | Normal Operation | 41 | 40 | 41 | 29.6 | 50 | 6.7 | -1 | 71.1 | 79.5 | 2 | 5.9 | 20 | 180 | 63 | -0.9 | -1.4 | 46.5 | 45.6 | 49.2 | 272 | 238 | 2000 | 23.7 | 41.8 | 550 | 50.2 | Room | On | 28.1 | 45.8 | 49.4 | 47.4 | 1007.4774 | 4023.2895 | 3.6 | 6833.9876 | 2.9 | 82% | 1 | 5900 | 29.6 | 71.1 | 555.6115 | 46.5 | 288.2377 | 267.3738 | 1.5336 | 1.8702 | 4.4179
45618.3309 | On | Off | Off | Off | Off | Normal Operation | 40 | 40 | 40 | 29.7 | 50 | 6.7 | -1 | 71.1 | 79.5 | 2 | 5.9 | 20 | 178 | 63 | -0.9 | -1.4 | 46.5 | 45.8 | 49.2 | 272 | 238 | 2000 | 23.7 | 41.8 | 550 | 50.2 | Room | On | 28.1 | 45.8 | 49.4 | 47.5 | 1007.424 | 4023.2895 | 3.4 | 6453.9793 | 2.9 | 80% | 1 | 5900 | 29.7 | 71.1 | 555.4137 | 46.5 | 288.2509 | 267.1628 | 1.4494 | 1.8118 | 4.4328
45618.331 | On | Off | Off | Off | Off | Normal Operation | 40 | 40 | 40 | 29.7 | 50 | 6.7 | -1 | 71.1 | 79.5 | 2 | 5.7 | 20 | 178 | 63 | -0.9 | -1.4 | 46.5 | 45.8 | 49.2 | 271 | 238 | 2000 | 23.7 | 41.8 | 550 | 50.2 | Room | On | 28.1 | 45.8 | 49.2 | 47.5 | 1007.424 | 4023.2895 | 3.4 | 6453.9793 | 2.9 | 80% | 1 | 5700 | 29.7 | 71.1 | 555.4137 | 46.5 | 288.2509 | 267.1628 | 1.4494 | 1.8118 | 4.4328
45618.3311 | On | Off | Off | Off | Off | Normal Operation | 40 | 40 | 40 | 29.8 | 50 | 6.7 | -1 | 71.1 | 79.5 | 2 | 5.8 | 20 | 178 | 63 | -1 | -1.4 | 46.6 | 45.8 | 49.4 | 271 | 238 | 2000 | 23.8 | 41.8 | 550 | 50.2 | Room | On | 28.1 | 45.8 | 49.2 | 47.6 | 1007.3705 | 4023.2895 | 3.6 | 6833.2623 | 3 | 80% | 0.8 | 5800 | 29.8 | 71.1 | 555.2156 | 46.6 | 288.464 | 266.7515 | 1.537 | 1.9212 | 4.4478
45618.3312 | On | Off | Off | Off | Off | Normal Operation | 40 | 40 | 40 | 29.7 | 50 | 6.7 | -1 | 71.1 | 79.5 | 2 | 5.7 | 20 | 178 | 64 | -1 | -1.4 | 46.6 | 46 | 49.4 | 271 | 235 | 2000 | 23.8 | 41.8 | 550 | 50.2 | Room | On | 28.1 | 45.8 | 49.2 | 47.7 | 1007.317 | 4023.2895 | 3.4 | 6453.2936 | 3 | 80% | 0.8 | 5700 | 29.7 | 71.1 | 555.4137 | 46.6 | 288.4508 | 266.9629 | 1.4504 | 1.813 | 4.4328
45618.3313 | On | Off | Off | Off | Off | Normal Operation | 40 | 39 | 40 | 29.8 | 50 | 6.7 | -1 | 71.1 | 79.5 | 2 | 5.8 | 20 | 178 | 64 | -1 | -1.4 | 46.6 | 45.8 | 49.4 | 271 | 235 | 2000 | 24 | 41.8 | 550 | 50.2 | Room | On | 28.1 | 45.8 | 49.2 | 47.6 | 1007.3705 | 4023.2895 | 3.6 | 6833.2623 | 3 | 80% | 0.8 | 5800 | 29.8 | 71.1 | 555.2156 | 46.6 | 288.464 | 266.7515 | 1.537 | 1.9212 | 4.4478
45618.3315 | On | Off | Off | Off | Off | Normal Operation | 40 | 39 | 40 | 29.8 | 50 | 6.7 | -1 | 71.1 | 79.5 | 2 | 5.8 | 20 | 178 | 64 | -1 | -1.4 | 46.6 | 46 | 49.4 | 271 | 235 | 2000 | 24 | 41.8 | 550 | 50.2 | Room | On | 28.1 | 45.8 | 49.4 | 47.7 | 1007.317 | 4023.2895 | 3.4 | 6453.2936 | 3 | 80% | 0.8 | 5800 | 29.8 | 71.1 | 555.2156 | 46.6 | 288.464 | 266.7515 | 1.4515 | 1.8144 | 4.4478
45618.3316 | On | Off | Off | Off | Off | Normal Operation | 39 | 39 | 39 | 29.7 | 50 | 6.7 | -1 | 71.1 | 79.5 | 2 | 5.7 | 20 | 178 | 64 | -1 | -1.4 | 46.6 | 46 | 49.4 | 271 | 235 | 2000 | 24 | 42 | 550 | 50.2 | Room | On | 28.1 | 45.8 | 49.4 | 47.7 | 1007.317 | 4023.2895 | 3.4 | 6453.2936 | 3 | 78% | 0.8 | 5700 | 29.7 | 71.1 | 555.4137 | 46.6 | 288.4508 | 266.9629 | 1.4504 | 1.8595 | 4.4328
45618.3317 | On | Off | Off | Off | Off | Normal Operation | 39 | 39 | 39 | 29.8 | 50 | 6.7 | -1 | 71.1 | 79.5 | 2 | 5.6 | 20 | 178 | 64 | -1 | -1.4 | 46.6 | 46 | 49.4 | 269 | 231 | 2000 | 24 | 42 | 550 | 50.2 | Room | On | 28.1 | 45.8 | 49.4 | 47.7 | 1007.317 | 4023.2895 | 3.4 | 6453.2936 | 3 | 78% | 0.8 | 5600 | 29.8 | 71.1 | 555.2156 | 46.6 | 288.464 | 266.7515 | 1.4515 | 1.8609 | 4.4478
45618.3318 | On | Off | Off | Off | Off | Normal Operation | 39 | 39 | 39 | 29.8 | 50 | 6.8 | -1 | 71.1 | 79.5 | 2 | 5.6 | 20 | 178 | 64 | -1 | -1.4 | 46.8 | 46 | 49.4 | 269 | 231 | 2000 | 24 | 42 | 550 | 50.2 | Room | On | 28.1 | 45.8 | 49.4 | 47.7 | 1007.317 | 4023.2895 | 3.4 | 6453.2936 | 3 | 78% | 0.8 | 5600 | 29.8 | 71.1 | 555.2156 | 46.8 | 288.8639 | 266.3517 | 1.4537 | 1.8637 | 4.3824
45618.3319 | On | Off | Off | Off | Off | Normal Operation | 39 | 39 | 39 | 29.8 | 50 | 6.8 | -1 | 71.2 | 79.5 | 2 | 5.6 | 20 | 178 | 64 | -0.9 | -1.3 | 46.8 | 46 | 49.4 | 269 | 231 | 2000 | 24.1 | 42 | 550 | 50.2 | Room | On | 28.1 | 46 | 49.4 | 47.7 | 1007.317 | 4023.7598 | 3.4 | 6454.0479 | 2.9 | 78% | 0.8 | 5600 | 29.8 | 71.2 | 555.4003 | 46.8 | 288.8639 | 266.5364 | 1.4529 | 1.8627 | 4.3824
45618.332 | On | Off | Off | Off | Off | Normal Operation | 39 | 40 | 39 | 29.8 | 50 | 6.8 | -1 | 71.2 | 79.5 | 2 | 5.6 | 20 | 178 | 64 | -0.9 | -1.3 | 46.8 | 46 | 49.4 | 269 | 231 | 2000 | 24.1 | 42 | 550 | 50.2 | Room | On | 28.1 | 46 | 49.4 | 47.7 | 1007.317 | 4023.7598 | 3.4 | 6454.0479 | 2.9 | 78% | 0.8 | 5600 | 29.8 | 71.2 | 555.4003 | 46.8 | 288.8639 | 266.5364 | 1.4529 | 1.8627 | 4.3824
45618.3321 | On | Off | Off | Off | Off | Normal Operation | 39 | 40 | 39 | 29.8 | 50 | 6.8 | -1 | 71.2 | 79.5 | 2 | 5.6 | 20 | 178 | 64 | -0.9 | -1.3 | 46.8 | 46.1 | 49.4 | 269 | 231 | 2000 | 24.1 | 42 | 550 | 50.2 | Room | On | 28.1 | 46 | 49.4 | 47.75 | 1007.2902 | 4023.7598 | 3.3 | 6264.0563 | 2.9 | 78% | 0.8 | 5600 | 29.8 | 71.2 | 555.4003 | 46.8 | 288.8639 | 266.5364 | 1.4101 | 1.8078 | 4.3824
45618.3323 | On | Off | Off | Off | Off | Normal Operation | 40 | 40 | 40 | 29.9 | 50 | 6.8 | -1 | 71.2 | 79.6 | 2 | 5.7 | 20 | 178 | 64 | -0.9 | -1.3 | 46.8 | 46.1 | 49.6 | 269 | 231 | 2000 | 24.1 | 42.1 | 550 | 50.2 | Room | On | 28.1 | 46 | 49.4 | 47.85 | 1007.2365 | 4023.7598 | 3.5 | 6643.3424 | 2.9 | 80% | 0.6 | 5700 | 29.9 | 71.2 | 555.2024 | 46.8 | 288.8773 | 266.325 | 1.4967 | 1.8708 | 4.3971
45618.3324 | On | Off | Off | Off | Off | Normal Operation | 40 | 40 | 40 | 29.9 | 50 | 6.7 | -1 | 71.2 | 79.6 | 2 | 5.7 | 20 | 178 | 64 | -0.9 | -1.3 | 46.8 | 46.1 | 49.6 | 268 | 231 | 2000 | 24.1 | 42.1 | 550 | 50.2 | Room | On | 27.9 | 46.1 | 49.6 | 47.85 | 1007.2365 | 4023.9949 | 3.5 | 6596.4443 | 2.9 | 80% | 0.6 | 5700 | 29.9 | 71.2 | 555.2024 | 46.8 | 288.8773 | 266.325 | 1.4861 | 1.8576 | 4.4627
45618.3325 | On | Off | Off | Off | Off | Normal Operation | 40 | 40 | 40 | 29.8 | 50 | 6.7 | -1 | 71.4 | 79.6 | 2 | 5.7 | 20 | 184 | 64 | -0.9 | -1.3 | 46.8 | 46 | 49.6 | 268 | 231 | 2000 | 24 | 42.2 | 550 | 50.2 | Room | On | 27.9 | 46.1 | 49.6 | 47.8 | 1007.2634 | 4023.9949 | 3.6 | 6785.0948 | 2.9 | 80% | 0.6 | 5700 | 29.8 | 71.4 | 555.7696 | 46.8 | 288.8639 | 266.9057 | 1.5253 | 1.9066 | 4.4478
45618.3326 | On | Off | Off | Off | Off | Normal Operation | 40 | 40 | 40 | 29.9 | 50 | 6.7 | -1 | 71.4 | 79.6 | 2 | 5.7 | 20 | 184 | 64 | -0.9 | -1.3 | 46.8 | 46.1 | 49.6 | 268 | 235 | 2000 | 24 | 42.2 | 550 | 50.2 | Room | On | 27.9 | 46.1 | 49.6 | 47.85 | 1007.2365 | 4023.9949 | 3.5 | 6596.4443 | 2.9 | 80% | 0.6 | 5700 | 29.9 | 71.4 | 555.5728 | 46.8 | 288.8773 | 266.6955 | 1.484 | 1.855 | 4.4627
45618.3327 | On | Off | Off | Off | Off | Normal Operation | 40 | 34 | 40 | 30 | 50 | 6.7 | -1 | 71.5 | 79.7 | 2 | 5.8 | 21 | 184 | 64 | -0.9 | -1.3 | 46.8 | 46.3 | 49.8 | 268 | 235 | 2000 | 24 | 42.2 | 550 | 50.2 | Room | On | 27.9 | 46.1 | 49.6 | 48.05 | 1007.1291 | 4023.9949 | 3.5 | 6595.7407 | 2.9 | 80% | 0.4 | 5800 | 30 | 71.5 | 555.5614 | 46.8 | 288.8908 | 266.6706 | 1.484 | 1.855 | 4.4776
45618.3328 | On | Off | Off | Off | Off | Normal Operation | 40 | 34 | 40 | 30 | 50 | 6.7 | -1 | 71.5 | 79.7 | 2 | 5.8 | 20 | 184 | 64 | -0.9 | -1.4 | 47 | 46.1 | 49.8 | 268 | 235 | 2000 | 24 | 42.2 | 550 | 50.2 | Room | On | 28.1 | 46.1 | 49.8 | 47.95 | 1007.1829 | 4023.9949 | 3.7 | 7022.998 | 2.9 | 80% | 0.4 | 5800 | 30 | 71.5 | 555.5614 | 47 | 289.2909 | 266.2705 | 1.5825 | 1.9782 | 4.4776
45618.333 | On | Off | Off | Off | Off | Normal Operation | 39 | 34 | 39 | 29.9 | 50 | 6.7 | -1 | 71.7 | 79.8 | 2 | 5.7 | 20 | 184 | 64 | -0.9 | -1.4 | 47 | 46.1 | 49.8 | 268 | 235 | 2000 | 24 | 42.2 | 550 | 50.2 | Room | On | 28.1 | 46.1 | 49.8 | 47.95 | 1007.1829 | 4023.9949 | 3.7 | 7022.998 | 2.9 | 78% | 0.4 | 5700 | 29.9 | 71.7 | 556.1284 | 47 | 289.2773 | 266.8511 | 1.5791 | 2.0245 | 4.4627
45618.3331 | On | Off | Off | Off | Off | Normal Operation | 39 | 34 | 39 | 29.8 | 50 | 6.7 | -1 | 71.7 | 80 | 2 | 5.6 | 20 | 184 | 64 | -1 | -1.4 | 47 | 46.1 | 49.6 | 266 | 231 | 2000 | 24.1 | 42.2 | 550 | 50.2 | Room | On | 28.1 | 46.1 | 49.8 | 47.85 | 1007.2365 | 4023.9949 | 3.5 | 6643.7306 | 3 | 78% | 0.6 | 5600 | 29.8 | 71.7 | 556.3237 | 47 | 289.2637 | 267.0599 | 1.4926 | 1.9136 | 4.4478
45618.3332 | On | Off | Off | Off | Off | Normal Operation | 38 | 34 | 38 | 30 | 50 | 6.8 | -1 | 71.7 | 80 | 1.9 | 5.5 | 20 | 184 | 64 | -1 | -1.4 | 47 | 46.1 | 49.6 | 266 | 231 | 2000 | 24.2 | 42.2 | 550 | 50.2 | Room | On | 28.1 | 46.1 | 49.8 | 47.85 | 1007.2365 | 4023.9949 | 3.5 | 6643.7306 | 2.9 | 76% | 0.6 | 5500 | 30 | 71.7 | 555.9329 | 47 | 289.2909 | 266.642 | 1.495 | 1.9671 | 4.4118
45618.3333 | On | Off | Off | Off | Off | Normal Operation | 37 | 34 | 37 | 29.9 | 50 | 6.8 | -1 | 71.7 | 80 | 1.9 | 5.4 | 20 | 184 | 64 | -0.9 | -1.3 | 47 | 46.3 | 49.6 | 266 | 231 | 2000 | 24.3 | 42.2 | 550 | 50.3 | Room | On | 28.1 | 46.1 | 49.6 | 47.95 | 1007.1829 | 4023.9949 | 3.3 | 6263.755 | 2.8 | 74% | 0.7 | 5400 | 29.9 | 71.7 | 556.1284 | 47 | 289.2773 | 266.8511 | 1.4084 | 1.9032 | 4.3971
45618.3334 | On | Off | Off | Off | Off | Normal Operation | 37 | 34 | 37 | 29.9 | 50 | 6.8 | -1 | 71.7 | 80.1 | 2 | 5.4 | 20 | 184 | 64 | -0.9 | -1.3 | 47 | 46.3 | 49.6 | 266 | 231 | 2000 | 24.5 | 42.2 | 550 | 50.3 | Room | On | 28.1 | 46.1 | 49.6 | 47.95 | 1007.1829 | 4023.9949 | 3.3 | 6263.755 | 2.9 | 74% | 0.7 | 5400 | 29.9 | 71.7 | 556.1284 | 47 | 289.2773 | 266.8511 | 1.4084 | 1.9032 | 4.3971
45618.3335 | On | Off | Off | Off | Off | Normal Operation | 36 | 38 | 36 | 29.8 | 50 | 6.8 | -1 | 71.7 | 80.1 | 1.9 | 5.3 | 20 | 184 | 64 | -0.9 | -1.2 | 47 | 46.3 | 49.6 | 266 | 219 | 2000 | 24.7 | 42.2 | 550 | 50.3 | Room | On | 28.1 | 46.1 | 49.6 | 47.95 | 1007.1829 | 4023.9949 | 3.3 | 6263.755 | 2.8 | 72% | 0.7 | 5300 | 29.8 | 71.7 | 556.3237 | 47 | 289.2637 | 267.0599 | 1.4073 | 1.9545 | 4.3824
45618.3337 | On | Off | Off | Off | Off | Normal Operation | 37 | 38 | 37 | 29.9 | 50 | 6.8 | -1 | 71.5 | 80.1 | 1.9 | 5.3 | 20 | 184 | 64 | -0.9 | -1.2 | 47 | 46.3 | 49.6 | 266 | 219 | 2000 | 24.8 | 42.2 | 550 | 50.3 | Room | On | 28.1 | 46.1 | 49.6 | 47.95 | 1007.1829 | 4023.9949 | 3.3 | 6263.755 | 2.8 | 74% | 0.7 | 5300 | 29.9 | 71.5 | 555.758 | 47 | 289.2773 | 266.4807 | 1.4103 | 1.9058 | 4.3971
45618.3338 | On | Off | Off | Off | Off | Normal Operation | 37 | 38 | 37 | 29.9 | 50 | 6.8 | -1 | 71.5 | 80.1 | 1.9 | 5.3 | 20 | 184 | 64 | -0.9 | -1.2 | 47 | 46.3 | 49.6 | 265 | 219 | 2000 | 24.8 | 42.2 | 550 | 50.3 | Room | On | 27.9 | 46.3 | 49.6 | 47.95 | 1007.1829 | 4024.4652 | 3.3 | 6219.8999 | 2.8 | 74% | 0.7 | 5300 | 29.9 | 71.5 | 555.758 | 47 | 289.2773 | 266.4807 | 1.4005 | 1.8925 | 4.3971
45618.3339 | On | Off | Off | Off | Off | Normal Operation | 38 | 38 | 38 | 29.8 | 50 | 6.8 | -1 | 71.4 | 80.1 | 1.9 | 5.4 | 20 | 184 | 64 | -0.8 | -1.1 | 47 | 46.3 | 49.6 | 265 | 219 | 2000 | 24.6 | 42.2 | 550 | 50.3 | Room | On | 27.9 | 46.3 | 49.6 | 47.95 | 1007.1829 | 4024.4652 | 3.3 | 6219.8999 | 2.7 | 76% | 0.7 | 5400 | 29.8 | 71.4 | 555.7696 | 47 | 289.2637 | 266.5059 | 1.4003 | 1.8425 | 4.3824
45618.334 | On | Off | Off | Off | Off | Normal Operation | 38 | 38 | 38 | 30 | 50 | 6.8 | -1 | 71.4 | 80.1 | 1.9 | 5.5 | 20 | 181 | 64 | -0.7 | -1.1 | 47 | 46.3 | 49.6 | 265 | 227 | 2000 | 24.4 | 42.4 | 550 | 50.3 | Room | On | 27.9 | 46.3 | 49.6 | 47.95 | 1007.1829 | 4024.4652 | 3.3 | 6219.8999 | 2.6 | 76% | 0.7 | 5500 | 30 | 71.4 | 555.3756 | 47 | 289.2909 | 266.0847 | 1.4025 | 1.8454 | 4.4118
45618.3341 | On | Off | Off | Off | Off | Normal Operation | 38 | 38 | 38 | 30 | 50 | 6.8 | -1 | 71.4 | 80.1 | 1.9 | 5.5 | 20 | 181 | 64 | -0.7 | -1.1 | 47 | 46.3 | 49.6 | 265 | 227 | 2000 | 24.3 | 42.5 | 550 | 50.3 | Room | On | 27.9 | 46.3 | 49.6 | 47.95 | 1007.1829 | 4024.4652 | 3.3 | 6219.8999 | 2.6 | 76% | 0.7 | 5500 | 30 | 71.4 | 555.3756 | 47 | 289.2909 | 266.0847 | 1.4025 | 1.8454 | 4.4118
45618.3342 | On | Off | Off | Off | Off | Normal Operation | 38 | 36 | 38 | 30.2 | 51 | 6.8 | -1 | 71.5 | 80 | 1.9 | 5.5 | 20 | 181 | 64 | -0.7 | -1.1 | 47 | 46.5 | 49.8 | 265 | 227 | 2000 | 24.3 | 42.5 | 550 | 50.3 | Room | On | 28.1 | 46.5 | 49.8 | 48.15 | 1007.0753 | 4024.9354 | 3.3 | 6264.5501 | 2.6 | 76% | 0.5 | 5500 | 30.2 | 71.5 | 555.1672 | 47 | 289.3181 | 265.8492 | 1.4139 | 1.8603 | 4.4412
45618.3343 | On | Off | Off | Off | Off | Normal Operation | 37 | 36 | 37 | 30 | 50 | 6.8 | -1 | 71.7 | 80 | 1.9 | 5.5 | 20 | 181 | 64 | -0.8 | -1.2 | 47 | 46.5 | 49.8 | 265 | 227 | 2000 | 24.3 | 42.5 | 550 | 50.3 | Room | On | 28.1 | 46.5 | 49.8 | 48.15 | 1007.0753 | 4024.9354 | 3.3 | 6264.5501 | 2.7 | 74% | 0.5 | 5500 | 30 | 71.7 | 555.9329 | 47 | 289.2909 | 266.642 | 1.4097 | 1.9049 | 4.4118
45618.3345 | On | Off | Off | Off | Off | Normal Operation | 37 | 36 | 37 | 30 | 50 | 6.8 | -1 | 71.7 | 80 | 1.9 | 5.4 | 20 | 181 | 64 | -0.8 | -1.2 | 47 | 46.5 | 49.8 | 263 | 223 | 2000 | 24.4 | 42.5 | 550 | 50.3 | Room | On | 28.1 | 46.5 | 49.8 | 48.15 | 1007.0753 | 4024.9354 | 3.3 | 6264.5501 | 2.7 | 74% | 0.5 | 5400 | 30 | 71.7 | 555.9329 | 47 | 289.2909 | 266.642 | 1.4097 | 1.9049 | 4.4118
45618.3346 | On | Off | Off | Off | Off | Normal Operation | 36 | 36 | 36 | 30.1 | 50 | 6.8 | -1 | 71.7 | 80.1 | 1.9 | 5.3 | 20 | 181 | 64 | -0.8 | -1.2 | 47 | 46.5 | 49.8 | 263 | 223 | 2000 | 24.5 | 42.5 | 550 | 50.3 | Room | On | 28.1 | 46.5 | 49.8 | 48.15 | 1007.0753 | 4024.9354 | 3.3 | 6264.5501 | 2.7 | 72% | 0.5 | 5300 | 30.1 | 71.7 | 555.737 | 47 | 289.3045 | 266.4325 | 1.4108 | 1.9594 | 4.4265
45618.3347 | On | Off | Off | Off | Off | Normal Operation | 36 | 36 | 36 | 30 | 50 | 6.8 | -1 | 71.7 | 80.1 | 1.9 | 5.3 | 20 | 181 | 64 | -0.8 | -1.2 | 47.1 | 46.5 | 49.8 | 263 | 223 | 2000 | 24.7 | 42.5 | 550 | 50.3 | Room | On | 28.1 | 46.5 | 49.8 | 48.15 | 1007.0753 | 4024.9354 | 3.3 | 6264.5501 | 2.7 | 72% | 0.5 | 5300 | 30 | 71.7 | 555.9329 | 47.1 | 289.491 | 266.4419 | 1.4107 | 1.9593 | 4.4118
45618.3348 | On | Off | Off | Off | Off | Normal Operation | 36 | 36 | 36 | 30 | 50 | 6.8 | -1 | 71.7 | 80.1 | 1.9 | 5.3 | 20 | 181 | 65 | -0.8 | -1.2 | 47.1 | 46.5 | 49.8 | 263 | 223 | 2000 | 24.8 | 42.5 | 550 | 50.3 | Room | On | 28.1 | 46.5 | 49.8 | 48.15 | 1007.0753 | 4024.9354 | 3.3 | 6264.5501 | 2.7 | 72% | 0.5 | 5300 | 30 | 71.7 | 555.9329 | 47.1 | 289.491 | 266.4419 | 1.4107 | 1.9593 | 4.4118
45618.3349 | On | Off | Off | Off | Off | Normal Operation | 36 | 37 | 36 | 30 | 50 | 6.8 | -1 | 71.5 | 80.1 | 1.9 | 5.3 | 20 | 181 | 64 | -0.8 | -1.1 | 47.1 | 46.5 | 49.8 | 263 | 219 | 2000 | 24.8 | 42.5 | 550 | 50.3 | Room | On | 28.1 | 46.5 | 49.8 | 48.15 | 1007.0753 | 4024.9354 | 3.3 | 6264.5501 | 2.7 | 72% | 0.5 | 5300 | 30 | 71.5 | 555.5614 | 47.1 | 289.491 | 266.0704 | 1.4127 | 1.9621 | 4.4118
45618.335 | On | Off | Off | Off | Off | Normal Operation | 37 | 37 | 37 | 30 | 50 | 6.8 | -1 | 71.5 | 80.1 | 1.9 | 5.4 | 21 | 181 | 65 | -0.7 | -1 | 47.1 | 46.6 | 49.8 | 263 | 219 | 2000 | 25 | 42.5 | 550 | 50.3 | Room | On | 28.1 | 46.5 | 49.8 | 48.2 | 1007.0484 | 4024.9354 | 3.2 | 6074.5528 | 2.6 | 74% | 0.5 | 5400 | 30 | 71.5 | 555.5614 | 47.1 | 289.491 | 266.0704 | 1.3698 | 1.8511 | 4.4118
45618.3352 | On | Off | Off | Off | Off | Normal Operation | 37 | 37 | 37 | 30.1 | 50 | 6.8 | -1 | 71.5 | 80.1 | 1.9 | 5.4 | 20 | 181 | 65 | -0.7 | -1 | 47.1 | 46.6 | 49.8 | 264 | 219 | 2000 | 24.8 | 42.5 | 550 | 50.3 | Room | On | 27.9 | 46.6 | 49.8 | 48.2 | 1007.0484 | 4025.1706 | 3.2 | 6031.6699 | 2.6 | 74% | 0.5 | 5400 | 30.1 | 71.5 | 555.3645 | 47.1 | 289.5046 | 265.8598 | 1.3612 | 1.8395 | 4.4265
45618.3353 | On | Off | Off | Off | Off | Normal Operation | 37 | 37 | 37 | 30.1 | 50 | 6.8 | -1 | 71.5 | 80.2 | 1.9 | 5.4 | 20 | 181 | 65 | -0.7 | -1 | 47.1 | 46.6 | 49.8 | 264 | 219 | 2000 | 24.7 | 42.5 | 550 | 50.3 | Room | On | 27.9 | 46.6 | 49.8 | 48.2 | 1007.0484 | 4025.1706 | 3.2 | 6031.6699 | 2.6 | 74% | 0.5 | 5400 | 30.1 | 71.5 | 555.3645 | 47.1 | 289.5046 | 265.8598 | 1.3612 | 1.8395 | 4.4265
45618.3354 | On | Off | Off | Off | Off | Normal Operation | 37 | 37 | 37 | 30.1 | 50 | 6.8 | -1 | 71.7 | 80.2 | 1.9 | 5.4 | 21 | 181 | 65 | -0.7 | -1 | 47.1 | 46.6 | 49.8 | 264 | 223 | 2000 | 24.6 | 42.7 | 550 | 50.3 | Room | On | 27.9 | 46.6 | 49.8 | 48.2 | 1007.0484 | 4025.1706 | 3.2 | 6031.6699 | 2.6 | 74% | 0.5 | 5400 | 30.1 | 71.7 | 555.737 | 47.1 | 289.5046 | 266.2324 | 1.3593 | 1.8369 | 4.4265
45618.3355 | On | Off | Off | Off | Off | Normal Operation | 37 | 37 | 37 | 30.1 | 50 | 6.8 | -1 | 71.7 | 80.2 | 2 | 5.4 | 21 | 181 | 65 | -0.7 | -1 | 47.1 | 46.6 | 49.8 | 264 | 223 | 2000 | 24.6 | 42.7 | 550 | 50.3 | Room | On | 27.9 | 46.6 | 49.8 | 48.2 | 1007.0484 | 4025.1706 | 3.2 | 6031.6699 | 2.7 | 74% | 0.5 | 5400 | 30.1 | 71.7 | 555.737 | 47.1 | 289.5046 | 266.2324 | 1.3593 | 1.8369 | 4.4265
45618.3356 | On | Off | Off | Off | Off | Normal Operation | 37 | 38 | 37 | 30.1 | 50 | 6.8 | -1 | 71.8 | 80.2 | 2 | 5.4 | 21 | 182 | 65 | -0.7 | -1 | 47.1 | 46.6 | 49.8 | 264 | 223 | 2000 | 24.6 | 42.7 | 550 | 50.2 | Room | On | 28.1 | 46.6 | 49.8 | 48.2 | 1007.0484 | 4025.1706 | 3.2 | 6074.9077 | 2.7 | 74% | 0.4 | 5400 | 30.1 | 71.8 | 555.9233 | 47.1 | 289.5046 | 266.4187 | 1.3681 | 1.8488 | 4.4265
45618.3357 | On | Off | Off | Off | Off | Normal Operation | 38 | 38 | 38 | 30 | 50 | 6.8 | -1 | 71.8 | 80.2 | 2 | 5.4 | 20 | 182 | 65 | -0.7 | -1 | 47.1 | 46.6 | 49.8 | 264 | 223 | 2000 | 24.6 | 42.7 | 550 | 50.2 | Room | On | 28.1 | 46.6 | 49.8 | 48.2 | 1007.0484 | 4025.1706 | 3.2 | 6074.9077 | 2.7 | 76% | 0.4 | 5400 | 30 | 71.8 | 556.1186 | 47.1 | 289.491 | 266.6277 | 1.3671 | 1.7988 | 4.4118
45618.3359 | On | Off | Off | Off | Off | Normal Operation | 38 | 38 | 38 | 30.2 | 51 | 6.8 | -1 | 71.8 | 80.2 | 2 | 5.5 | 20 | 182 | 65 | -0.7 | -1.1 | 47.1 | 46.6 | 49.8 | 263 | 227 | 2000 | 24.6 | 42.7 | 550 | 50.2 | Room | On | 28.1 | 46.6 | 49.8 | 48.2 | 1007.0484 | 4025.1706 | 3.2 | 6074.9077 | 2.7 | 76% | 0.4 | 5500 | 30.2 | 71.8 | 555.7277 | 47.1 | 289.5183 | 266.2094 | 1.3692 | 1.8016 | 4.4412
45618.336 | On | Off | Off | Off | Off | Normal Operation | 38 | 38 | 38 | 30.2 | 51 | 6.8 | -1 | 72 | 80.4 | 2 | 5.6 | 21 | 182 | 65 | -0.8 | -1.2 | 47.1 | 46.6 | 50 | 263 | 227 | 2000 | 24.5 | 42.7 | 550 | 50.2 | Room | On | 28.1 | 46.6 | 49.8 | 48.3 | 1006.9945 | 4025.1706 | 3.4 | 6454.2441 | 2.8 | 76% | 0.2 | 5600 | 30.2 | 72 | 556.1013 | 47.1 | 289.5183 | 266.583 | 1.4527 | 1.9114 | 4.4412
45618.3361 | On | Off | Off | Off | Off | Normal Operation | 38 | 38 | 38 | 30.2 | 51 | 6.8 | -1 | 72.1 | 80.4 | 1.9 | 5.6 | 20 | 182 | 65 | -0.8 | -1.2 | 47.1 | 46.6 | 50 | 263 | 227 | 2000 | 24.5 | 42.7 | 550 | 50.3 | Room | On | 28.1 | 46.6 | 50 | 48.3 | 1006.9945 | 4025.1706 | 3.4 | 6454.2441 | 2.7 | 76% | 0.3 | 5600 | 30.2 | 72.1 | 556.2881 | 47.1 | 289.5183 | 266.7698 | 1.4516 | 1.9101 | 4.4412
45618.3362 | On | Off | Off | Off | Off | Normal Operation | 38 | 38 | 38 | 30.3 | 51 | 6.8 | -1 | 72.2 | 80.5 | 1.9 | 5.6 | 20 | 182 | 65 | -0.8 | -1.2 | 47.1 | 46.8 | 50 | 263 | 227 | 2000 | 24.5 | 42.7 | 550 | 50.3 | Room | On | 28.1 | 46.6 | 50 | 48.4 | 1006.9406 | 4025.1706 | 3.2 | 6074.2573 | 2.7 | 76% | 0.3 | 5600 | 30.3 | 72.2 | 556.2812 | 47.1 | 289.532 | 266.7492 | 1.3663 | 1.7977 | 4.4559
45618.3363 | On | Off | Off | Off | Off | Normal Operation | 38 | 36 | 38 | 30.3 | 51 | 6.8 | -1 | 72.2 | 80.5 | 1.9 | 5.6 | 20 | 182 | 65 | -0.8 | -1.2 | 47.2 | 46.8 | 50.2 | 263 | 227 | 2000 | 24.5 | 42.7 | 550 | 50.3 | Room | On | 28.1 | 46.6 | 50 | 48.5 | 1006.8866 | 4025.1706 | 3.4 | 6453.5524 | 2.7 | 76% | 0.1 | 5600 | 30.3 | 72.2 | 556.2812 | 47.2 | 289.7323 | 266.5489 | 1.4527 | 1.9114 | 4.4559
45618.3364 | On | Off | Off | Off | Off | Normal Operation | 37 | 36 | 37 | 30.3 | 51 | 6.8 | -1 | 72.4 | 80.7 | 1.9 | 5.6 | 21 | 182 | 65 | -0.8 | -1.2 | 47.2 | 46.8 | 50.2 | 263 | 227 | 2000 | 24.5 | 42.7 | 550 | 50.3 | Room | On | 28.1 | 46.6 | 50 | 48.5 | 1006.8866 | 4025.1706 | 3.4 | 6453.5524 | 2.7 | 74% | 0.1 | 5600 | 30.3 | 72.4 | 556.6559 | 47.2 | 289.7323 | 266.9236 | 1.4507 | 1.9603 | 4.4559
45618.3365 | On | Off | Off | Off | Off | Normal Operation | 37 | 36 | 37 | 30.3 | 51 | 6.8 | -1 | 72.4 | 80.7 | 1.9 | 5.5 | 21 | 182 | 65 | -0.7 | -1.1 | 47.2 | 46.8 | 50.2 | 260 | 227 | 2000 | 24.6 | 42.7 | 550 | 50.3 | Room | On | 28.1 | 46.8 | 50.2 | 48.5 | 1006.8866 | 4025.6408 | 3.4 | 6454.3063 | 2.6 | 74% | 0.1 | 5500 | 30.3 | 72.4 | 556.6559 | 47.2 | 289.7323 | 266.9236 | 1.4508 | 1.9606 | 4.4559
45618.3367 | On | Off | Off | Off | Off | Normal Operation | 36 | 36 | 36 | 30.3 | 51 | 6.8 | -1 | 72.4 | 80.8 | 1.9 | 5.4 | 21 | 182 | 65 | -0.7 | -1 | 47.2 | 47 | 50.2 | 260 | 227 | 2000 | 24.8 | 42.7 | 550 | 50.3 | Room | On | 28.1 | 46.8 | 50.2 | 48.6 | 1006.8326 | 4025.6408 | 3.2 | 6074.3152 | 2.6 | 72% | 0.1 | 5400 | 30.3 | 72.4 | 556.6559 | 47.2 | 289.7323 | 266.9236 | 1.3654 | 1.8964 | 4.4559
45618.3368 | On | Off | Off | Off | Off | Normal Operation | 36 | 36 | 36 | 30.2 | 51 | 6.8 | -1 | 72.4 | 80.8 | 1.9 | 5.3 | 21 | 182 | 65 | -0.6 | -1 | 47.2 | 46.8 | 50.2 | 260 | 219 | 2000 | 25.1 | 42.7 | 550 | 50.3 | Room | On | 28.1 | 46.8 | 50.2 | 48.5 | 1006.8866 | 4025.6408 | 3.4 | 6454.3063 | 2.5 | 72% | 0.1 | 5300 | 30.2 | 72.4 | 556.8486 | 47.2 | 289.7185 | 267.1301 | 1.4497 | 2.0135 | 4.4412
45618.3369 | On | Off | Off | Off | Off | Normal Operation | 36 | 36 | 36 | 30.2 | 51 | 6.8 | -1 | 72.2 | 80.8 | 2 | 5.3 | 21 | 182 | 65 | -0.6 | -1 | 47.2 | 46.8 | 50.2 | 260 | 219 | 2000 | 25.1 | 42.7 | 550 | 50.3 | Room | On | 28.1 | 46.8 | 50.2 | 48.5 | 1006.8866 | 4025.6408 | 3.4 | 6454.3063 | 2.6 | 72% | 0.1 | 5300 | 30.2 | 72.2 | 556.475 | 47.2 | 289.7185 | 266.7564 | 1.4517 | 2.0163 | 4.4412
45618.337 | On | Off | Off | Off | Off | Normal Operation | 36 | 37 | 36 | 30.2 | 51 | 6.8 | -1 | 72.2 | 80.8 | 2 | 5.3 | 21 | 182 | 65 | -0.6 | -1 | 47.2 | 46.8 | 50 | 260 | 219 | 2000 | 25.1 | 42.7 | 550 | 50.3 | Room | On | 28.1 | 46.8 | 50.2 | 48.4 | 1006.9406 | 4025.6408 | 3.2 | 6074.967 | 2.6 | 72% | 0.3 | 5300 | 30.2 | 72.2 | 556.475 | 47.2 | 289.7185 | 266.7564 | 1.3664 | 1.8978 | 4.4412
45618.3371 | On | Off | Off | Off | Off | Normal Operation | 37 | 37 | 37 | 30.2 | 51 | 6.8 | -1 | 72.2 | 80.8 | 2 | 5.3 | 21 | 182 | 65 | -0.6 | -1 | 47.2 | 46.8 | 50 | 260 | 219 | 2000 | 25.1 | 42.7 | 550 | 50.2 | Room | On | 27.9 | 46.8 | 50 | 48.4 | 1006.9406 | 4025.6408 | 3.2 | 6031.7288 | 2.6 | 74% | 0.2 | 5300 | 30.2 | 72.2 | 556.475 | 47.2 | 289.7185 | 266.7564 | 1.3567 | 1.8334 | 4.4412
45618.3372 | On | Off | Off | Off | Off | Normal Operation | 37 | 37 | 37 | 30.2 | 51 | 6.8 | -1 | 72.2 | 80.8 | 2 | 5.4 | 21 | 179 | 65 | -0.6 | -1 | 47.2 | 46.8 | 50 | 259 | 223 | 2000 | 25.1 | 42.7 | 550 | 50.2 | Room | On | 27.9 | 46.8 | 50 | 48.4 | 1006.9406 | 4025.6408 | 3.2 | 6031.7288 | 2.6 | 74% | 0.2 | 5400 | 30.2 | 72.2 | 556.475 | 47.2 | 289.7185 | 266.7564 | 1.3567 | 1.8334 | 4.4412
45618.3374 | On | Off | Off | Off | Off | Normal Operation | 37 | 37 | 37 | 30.3 | 51 | 6.8 | -1 | 72.2 | 80.8 | 2 | 5.5 | 21 | 179 | 65 | -0.6 | -1 | 47.2 | 46.8 | 50 | 259 | 223 | 2000 | 25 | 42.7 | 550 | 50.2 | Room | On | 27.9 | 46.8 | 50 | 48.4 | 1006.9406 | 4025.6408 | 3.2 | 6031.7288 | 2.6 | 74% | 0.2 | 5500 | 30.3 | 72.2 | 556.2812 | 47.2 | 289.7323 | 266.5489 | 1.3577 | 1.8348 | 4.4559
45618.3375 | On | Off | Off | Off | Off | Normal Operation | 37 | 37 | 37 | 30.3 | 51 | 6.8 | -1 | 72.2 | 80.8 | 2 | 5.5 | 20 | 179 | 65 | -0.6 | -1 | 47.2 | 47 | 50.2 | 259 | 223 | 2000 | 24.8 | 42.8 | 550 | 50.2 | Room | On | 27.9 | 46.8 | 50 | 48.6 | 1006.8326 | 4025.6408 | 3.2 | 6031.0816 | 2.6 | 74% | 0 | 5500 | 30.3 | 72.2 | 556.2812 | 47.2 | 289.7323 | 266.5489 | 1.3576 | 1.8346 | 4.4559
45618.3376 | On | Off | Off | Off | Off | Normal Operation | 37 | 37 | 37 | 30.3 | 51 | 6.8 | -1 | 72.4 | 80.8 | 2 | 5.5 | 21 | 179 | 65 | -0.7 | -1 | 47.3 | 47 | 50.2 | 259 | 223 | 2000 | 24.8 | 42.8 | 550 | 50.2 | Room | On | 28.3 | 47 | 50.2 | 48.6 | 1006.8326 | 4026.1111 | 3.2 | 6118.2634 | 2.7 | 74% | 0 | 5500 | 30.3 | 72.4 | 556.6559 | 47.3 | 289.9326 | 266.7233 | 1.3763 | 1.8599 | 4.4559
45618.3377 | On | Off | Off | Off | Off | Normal Operation | 37 | 35 | 37 | 30.3 | 51 | 6.8 | -1 | 72.4 | 80.8 | 2 | 5.5 | 21 | 179 | 65 | -0.7 | -1 | 47.3 | 47 | 50.2 | 259 | 223 | 2000 | 24.8 | 42.8 | 550 | 50.2 | Room | On | 28.3 | 47 | 50.2 | 48.6 | 1006.8326 | 4026.1111 | 3.2 | 6118.2634 | 2.7 | 74% | 0 | 5500 | 30.3 | 72.4 | 556.6559 | 47.3 | 289.9326 | 266.7233 | 1.3763 | 1.8599 | 4.4559
45618.3378 | On | Off | Off | Off | Off | Normal Operation | 36 | 35 | 36 | 30.3 | 51 | 6.8 | -1 | 72.5 | 81 | 2 | 5.5 | 21 | 179 | 65 | -0.7 | -1 | 47.3 | 47 | 50.2 | 259 | 223 | 2000 | 24.8 | 42.8 | 550 | 50.2 | Room | On | 28.3 | 47 | 50.2 | 48.6 | 1006.8326 | 4026.1111 | 3.2 | 6118.2634 | 2.7 | 72% | 0 | 5500 | 30.3 | 72.5 | 556.8432 | 47.3 | 289.9326 | 266.9107 | 1.3754 | 1.9102 | 4.4559
45618.3379 | On | Off | Off | Off | Off | Normal Operation | 36 | 35 | 36 | 30.3 | 51 | 6.8 | -1 | 72.5 | 81 | 2 | 5.4 | 20 | 179 | 65 | -0.7 | -1 | 47.3 | 47 | 50.2 | 257 | 223 | 2000 | 24.8 | 42.8 | 550 | 50.2 | Room | On | 28.3 | 47 | 50.2 | 48.6 | 1006.8326 | 4026.1111 | 3.2 | 6118.2634 | 2.7 | 72% | 0 | 5400 | 30.3 | 72.5 | 556.8432 | 47.3 | 289.9326 | 266.9107 | 1.3754 | 1.9102 | 4.4559
45618.3381 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.3 | 51 | 6.8 | -1 | 72.5 | 81.1 | 2 | 5.3 | 21 | 179 | 65 | -0.7 | -1 | 47.3 | 47 | 50.2 | 257 | 223 | 2000 | 25.1 | 42.8 | 540 | 50.2 | Room | On | 27.9 | 47 | 50.2 | 48.6 | 1006.8326 | 4026.1111 | 3.2 | 6031.7861 | 2.7 | 70% | 0 | 5300 | 30.3 | 72.5 | 556.8432 | 47.3 | 289.9326 | 266.9107 | 1.3559 | 1.937 | 4.4559
45618.3382 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.3 | 51 | 6.8 | -1 | 72.5 | 81.1 | 2 | 5.3 | 21 | 179 | 65 | -0.6 | -1 | 47.3 | 47 | 50.2 | 257 | 215 | 2000 | 25.3 | 42.8 | 550 | 50.2 | Room | On | 27.9 | 47 | 50.2 | 48.6 | 1006.8326 | 4026.1111 | 3.2 | 6031.7861 | 2.6 | 70% | 0 | 5300 | 30.3 | 72.5 | 556.8432 | 47.3 | 289.9326 | 266.9107 | 1.3559 | 1.937 | 4.4559
45618.3383 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.2 | 51 | 6.9 | 0 | 72.4 | 81.1 | 2 | 5.2 | 21 | 179 | 65 | -0.6 | -0.9 | 47.3 | 47 | 50.2 | 257 | 215 | 2000 | 25.5 | 42.8 | 540 | 50.2 | Room | On | 27.9 | 47 | 50.2 | 48.6 | 1006.8326 | 4026.1111 | 3.2 | 6031.7861 | 2.6 | 70% | 0 | 5200 | 30.2 | 72.4 | 556.8486 | 47.3 | 289.9187 | 266.9298 | 1.3558 | 1.9369 | 4.3768
45618.3384 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.2 | 51 | 6.9 | 0 | 72.4 | 81.1 | 2 | 5.2 | 21 | 179 | 65 | -0.6 | -0.9 | 47.3 | 47 | 50.2 | 257 | 215 | 2000 | 25.5 | 42.8 | 550 | 50.2 | Room | On | 27.9 | 47 | 50.2 | 48.6 | 1006.8326 | 4026.1111 | 3.2 | 6031.7861 | 2.6 | 70% | 0 | 5200 | 30.2 | 72.4 | 556.8486 | 47.3 | 289.9187 | 266.9298 | 1.3558 | 1.9369 | 4.3768
45618.3385 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.4 | 51 | 6.8 | -1 | 72.4 | 81.1 | 2 | 5.3 | 21 | 179 | 65 | -0.6 | -0.9 | 47.3 | 47.1 | 50.2 | 257 | 215 | 2000 | 25.5 | 42.8 | 550 | 50.2 | Room | On | 27.9 | 47 | 50.2 | 48.65 | 1006.8055 | 4026.1111 | 3.1 | 5843.1359 | 2.6 | 70% | 0 | 5300 | 30.4 | 72.4 | 556.4629 | 47.3 | 289.9464 | 266.5165 | 1.3154 | 1.8792 | 4.4706
45618.3386 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.4 | 51 | 6.8 | -1 | 72.4 | 81.1 | 2 | 5.2 | 21 | 179 | 65 | -0.6 | -0.9 | 47.3 | 47.1 | 50.4 | 258 | 215 | 2000 | 25.4 | 43 | 550 | 50.2 | Room | On | 27.9 | 47 | 50.2 | 48.75 | 1006.7514 | 4026.1111 | 3.3 | 6219.7779 | 2.6 | 70% | -0.2 | 5200 | 30.4 | 72.4 | 556.4629 | 47.3 | 289.9464 | 266.5165 | 1.4002 | 2.0003 | 4.4706
45618.3387 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.3 | 51 | 6.8 | -1 | 72.4 | 81.1 | 2 | 5.3 | 21 | 183 | 65 | -0.6 | -0.9 | 47.3 | 47.1 | 50.4 | 258 | 215 | 2000 | 25.4 | 43 | 550 | 50.2 | Room | On | 27.9 | 47 | 50.2 | 48.75 | 1006.7514 | 4026.1111 | 3.3 | 6219.7779 | 2.6 | 70% | -0.2 | 5300 | 30.3 | 72.4 | 556.6559 | 47.3 | 289.9326 | 266.7233 | 1.3992 | 1.9988 | 4.4559
45618.3389 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.3 | 51 | 6.8 | -1 | 72.4 | 81.1 | 2 | 5.3 | 20 | 183 | 65 | -0.6 | -0.9 | 47.3 | 47.1 | 50.4 | 258 | 215 | 2000 | 25.4 | 43 | 550 | 50.2 | Room | On | 27.9 | 47 | 50.2 | 48.75 | 1006.7514 | 4026.1111 | 3.3 | 6219.7779 | 2.6 | 70% | -0.2 | 5300 | 30.3 | 72.4 | 556.6559 | 47.3 | 289.9326 | 266.7233 | 1.3992 | 1.9988 | 4.4559
45618.339 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.3 | 51 | 6.8 | -1 | 72.4 | 81.1 | 1.9 | 5.2 | 21 | 183 | 65 | -0.7 | -1 | 47.3 | 47.1 | 50.4 | 258 | 215 | 2000 | 25.4 | 43 | 550 | 50.3 | Room | On | 28.1 | 47.1 | 50.4 | 48.75 | 1006.7514 | 4026.3462 | 3.3 | 6264.73 | 2.6 | 70% | -0.1 | 5200 | 30.3 | 72.4 | 556.6559 | 47.3 | 289.9326 | 266.7233 | 1.4093 | 2.0132 | 4.4559
45618.3391 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.3 | 51 | 6.8 | -1 | 72.4 | 81.1 | 1.9 | 5.2 | 21 | 183 | 65 | -0.7 | -0.9 | 47.3 | 47.1 | 50.4 | 258 | 215 | 2000 | 25.3 | 43.1 | 550 | 50.3 | Room | On | 28.1 | 47.1 | 50.4 | 48.75 | 1006.7514 | 4026.3462 | 3.3 | 6264.73 | 2.6 | 70% | -0.1 | 5200 | 30.3 | 72.4 | 556.6559 | 47.3 | 289.9326 | 266.7233 | 1.4093 | 2.0132 | 4.4559
45618.3392 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.3 | 51 | 6.8 | -1 | 72.4 | 81.1 | 1.9 | 5.2 | 21 | 183 | 65 | -0.6 | -0.9 | 47.3 | 47.1 | 50.2 | 258 | 215 | 2000 | 25.3 | 43.1 | 550 | 50.3 | Room | On | 28.1 | 47.1 | 50.4 | 48.65 | 1006.8055 | 4026.3462 | 3.1 | 5885.3658 | 2.5 | 70% | 0.1 | 5200 | 30.3 | 72.4 | 556.6559 | 47.3 | 289.9326 | 266.7233 | 1.3239 | 1.8913 | 4.4559
45618.3393 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.3 | 51 | 6.8 | -1 | 72.4 | 81.1 | 1.9 | 5.2 | 20 | 183 | 65 | -0.6 | -0.9 | 47.3 | 47.1 | 50.2 | 256 | 215 | 2000 | 25.3 | 43.1 | 550 | 50.3 | Room | On | 28.1 | 47.1 | 50.4 | 48.65 | 1006.8055 | 4026.3462 | 3.1 | 5885.3658 | 2.5 | 70% | 0.1 | 5200 | 30.3 | 72.4 | 556.6559 | 47.3 | 289.9326 | 266.7233 | 1.3239 | 1.8913 | 4.4559
45618.3394 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.4 | 51 | 6.9 | 0 | 72.4 | 81.1 | 1.9 | 5.3 | 21 | 183 | 65 | -0.6 | -0.9 | 47.3 | 47.1 | 50.2 | 256 | 215 | 2000 | 25.4 | 43 | 550 | 50.3 | Room | On | 28.1 | 47.1 | 50.2 | 48.65 | 1006.8055 | 4026.3462 | 3.1 | 5885.3658 | 2.5 | 70% | 0.1 | 5300 | 30.4 | 72.4 | 556.4629 | 47.3 | 289.9464 | 266.5165 | 1.325 | 1.8928 | 4.4058
45618.3396 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.4 | 51 | 6.9 | 0 | 72.4 | 81.1 | 1.9 | 5.3 | 21 | 183 | 65 | -0.6 | -0.9 | 47.3 | 47.1 | 50.4 | 256 | 215 | 2000 | 25.4 | 43 | 550 | 50.3 | Room | On | 28.1 | 47.1 | 50.2 | 48.75 | 1006.7514 | 4026.3462 | 3.3 | 6264.73 | 2.5 | 70% | -0.1 | 5300 | 30.4 | 72.4 | 556.4629 | 47.3 | 289.9464 | 266.5165 | 1.4104 | 2.0148 | 4.4058
45618.3397 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.5 | 51 | 6.9 | 0 | 72.5 | 81.1 | 1.9 | 5.3 | 21 | 183 | 65 | -0.6 | -0.9 | 47.3 | 47.1 | 50.4 | 256 | 215 | 2000 | 25.4 | 43.1 | 550 | 50.3 | Room | On | 28.1 | 47.1 | 50.2 | 48.75 | 1006.7514 | 4026.3462 | 3.3 | 6264.73 | 2.5 | 70% | -0.1 | 5300 | 30.5 | 72.5 | 556.458 | 47.3 | 289.9602 | 266.4978 | 1.4105 | 2.0149 | 4.4203
45618.3398 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.4 | 51 | 6.9 | 0 | 72.5 | 81.1 | 1.9 | 5.3 | 21 | 183 | 65 | -0.6 | -0.9 | 47.3 | 47.1 | 50.4 | 256 | 215 | 2000 | 25.4 | 43.1 | 550 | 50.3 | Room | On | 28.1 | 47.1 | 50.2 | 48.75 | 1006.7514 | 4026.3462 | 3.3 | 6264.73 | 2.5 | 70% | -0.1 | 5300 | 30.4 | 72.5 | 556.6508 | 47.3 | 289.9464 | 266.7044 | 1.4094 | 2.0134 | 4.4058
45618.3399 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.4 | 51 | 6.9 | 0 | 72.5 | 81.2 | 1.9 | 5.3 | 20 | 183 | 65 | -0.5 | -0.8 | 47.3 | 47.1 | 50.4 | 256 | 215 | 2000 | 25.5 | 43.1 | 550 | 50.3 | Room | On | 27.9 | 47.1 | 50.4 | 48.75 | 1006.7514 | 4026.3462 | 3.3 | 6220.1412 | 2.4 | 70% | -0.1 | 5300 | 30.4 | 72.5 | 556.6508 | 47.3 | 289.9464 | 266.7044 | 1.3993 | 1.999 | 4.4058
45618.34 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.5 | 51 | 6.9 | 0 | 72.5 | 81.2 | 2 | 5.3 | 21 | 183 | 65 | -0.5 | -0.8 | 47.3 | 47.1 | 50.4 | 257 | 215 | 2000 | 25.5 | 43.1 | 550 | 50.3 | Room | On | 27.9 | 47.1 | 50.4 | 48.75 | 1006.7514 | 4026.3462 | 3.3 | 6220.1412 | 2.5 | 70% | -0.1 | 5300 | 30.5 | 72.5 | 556.458 | 47.3 | 289.9602 | 266.4978 | 1.4004 | 2.0006 | 4.4203
45618.3401 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.5 | 51 | 6.9 | 0 | 72.7 | 81.2 | 2 | 5.3 | 21 | 183 | 65 | -0.4 | -0.8 | 47.5 | 47.1 | 50.4 | 257 | 215 | 2000 | 25.5 | 43.1 | 550 | 50.3 | Room | On | 27.9 | 47.1 | 50.4 | 48.75 | 1006.7514 | 4026.3462 | 3.3 | 6220.1412 | 2.4 | 70% | -0.1 | 5300 | 30.5 | 72.7 | 556.8349 | 47.5 | 290.3611 | 266.4738 | 1.4005 | 2.0008 | 4.4203
45618.3403 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.4 | 51 | 6.9 | 0 | 72.7 | 81.2 | 2 | 5.3 | 21 | 183 | 65 | -0.4 | -0.8 | 47.5 | 47.1 | 50.4 | 257 | 215 | 2000 | 25.5 | 43.1 | 550 | 50.3 | Room | On | 27.9 | 47.1 | 50.4 | 48.75 | 1006.7514 | 4026.3462 | 3.3 | 6220.1412 | 2.4 | 70% | -0.1 | 5300 | 30.4 | 72.7 | 557.0266 | 47.5 | 290.3471 | 266.6794 | 1.3995 | 1.9992 | 4.4058
45618.3404 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.5 | 51 | 6.9 | 0 | 72.7 | 81.2 | 2 | 5.3 | 20 | 182 | 65 | -0.5 | -0.8 | 47.5 | 47.1 | 50.4 | 257 | 215 | 2000 | 25.5 | 43.1 | 550 | 50.2 | Room | On | 27.9 | 47.1 | 50.4 | 48.75 | 1006.7514 | 4026.3462 | 3.3 | 6220.1412 | 2.5 | 70% | -0.2 | 5300 | 30.5 | 72.7 | 556.8349 | 47.5 | 290.3611 | 266.4738 | 1.4005 | 2.0008 | 4.4203
45618.3405 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.5 | 51 | 6.9 | 0 | 72.7 | 81.2 | 2 | 5.3 | 20 | 182 | 65 | -0.5 | -0.8 | 47.5 | 47.1 | 50.4 | 257 | 215 | 2000 | 25.5 | 43.1 | 550 | 50.2 | Room | On | 27.9 | 47.1 | 50.4 | 48.75 | 1006.7514 | 4026.3462 | 3.3 | 6220.1412 | 2.5 | 70% | -0.2 | 5300 | 30.5 | 72.7 | 556.8349 | 47.5 | 290.3611 | 266.4738 | 1.4005 | 2.0008 | 4.4203
45618.3406 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.5 | 51 | 6.9 | 0 | 72.7 | 81.2 | 2 | 5.3 | 21 | 182 | 65 | -0.5 | -0.8 | 47.5 | 47.2 | 50.4 | 257 | 215 | 2000 | 25.5 | 43.1 | 540 | 50.2 | Room | On | 27.9 | 47.1 | 50.4 | 48.8 | 1006.7243 | 4026.3462 | 3.2 | 6031.4898 | 2.5 | 70% | -0.2 | 5300 | 30.5 | 72.7 | 556.8349 | 47.5 | 290.3611 | 266.4738 | 1.3581 | 1.9401 | 4.4203
45618.3407 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.5 | 51 | 6.9 | 0 | 72.7 | 81.2 | 2 | 5.3 | 21 | 182 | 66 | -0.4 | -0.8 | 47.5 | 47.2 | 50.4 | 256 | 215 | 2000 | 25.5 | 43.1 | 550 | 50.2 | Room | On | 27.9 | 47.1 | 50.4 | 48.8 | 1006.7243 | 4026.3462 | 3.2 | 6031.4898 | 2.4 | 70% | -0.2 | 5300 | 30.5 | 72.7 | 556.8349 | 47.5 | 290.3611 | 266.4738 | 1.3581 | 1.9401 | 4.4203
45618.3408 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.6 | 51 | 6.9 | 0 | 72.7 | 81.2 | 2 | 5.3 | 21 | 182 | 66 | -0.4 | -0.7 | 47.5 | 47.2 | 50.4 | 256 | 215 | 2000 | 25.6 | 43.1 | 550 | 50.2 | Room | On | 28.1 | 47.2 | 50.4 | 48.8 | 1006.7243 | 4026.5814 | 3.2 | 6075.081 | 2.4 | 70% | -0.2 | 5300 | 30.6 | 72.7 | 556.6429 | 47.5 | 290.3751 | 266.2678 | 1.3689 | 1.9556 | 4.4348
45618.3409 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.6 | 51 | 6.9 | 0 | 72.8 | 81.4 | 2 | 5.3 | 21 | 182 | 66 | -0.4 | -0.7 | 47.5 | 47.3 | 50.6 | 256 | 215 | 2000 | 25.6 | 43.1 | 550 | 50.2 | Room | On | 28.1 | 47.2 | 50.4 | 48.95 | 1006.6429 | 4026.5814 | 3.3 | 6264.4211 | 2.4 | 70% | -0.4 | 5300 | 30.6 | 72.8 | 556.8319 | 47.5 | 290.3751 | 266.4568 | 1.4106 | 2.0151 | 4.4348
45618.3411 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.4 | 51 | 6.9 | 0 | 72.8 | 81.4 | 2 | 5.3 | 21 | 182 | 66 | -0.4 | -0.7 | 47.6 | 47.2 | 50.6 | 256 | 215 | 2000 | 25.6 | 43.3 | 550 | 50.2 | Room | On | 28.1 | 47.2 | 50.4 | 48.9 | 1006.6701 | 4026.5814 | 3.4 | 6454.426 | 2.4 | 70% | -0.4 | 5300 | 30.4 | 72.8 | 557.2145 | 47.6 | 290.5475 | 266.667 | 1.4522 | 2.0746 | 4.4058
45618.3412 | On | Off | Off | Off | Off | Normal Operation | 35 | 33 | 35 | 30.5 | 51 | 6.9 | 0 | 72.8 | 81.4 | 2 | 5.3 | 21 | 182 | 66 | -0.4 | -0.7 | 47.6 | 47.2 | 50.6 | 256 | 215 | 2000 | 25.6 | 43.3 | 550 | 50.2 | Room | On | 28.1 | 47.2 | 50.4 | 48.9 | 1006.6701 | 4026.5814 | 3.4 | 6454.426 | 2.4 | 70% | -0.4 | 5300 | 30.5 | 72.8 | 557.0233 | 47.6 | 290.5615 | 266.4618 | 1.4534 | 2.0762 | 4.4203
45618.3413 | On | Off | Off | Off | Off | Normal Operation | 34 | 33 | 34 | 30.5 | 51 | 6.9 | 0 | 72.8 | 81.4 | 2 | 5.3 | 21 | 182 | 66 | -0.4 | -0.7 | 47.6 | 47.2 | 50.6 | 256 | 215 | 2000 | 25.6 | 43.3 | 550 | 50.2 | Room | On | 28.1 | 47.2 | 50.6 | 48.9 | 1006.6701 | 4026.5814 | 3.4 | 6454.426 | 2.4 | 68% | -0.4 | 5300 | 30.5 | 72.8 | 557.0233 | 47.6 | 290.5615 | 266.4618 | 1.4534 | 2.1373 | 4.4203
45618.3414 | On | Off | Off | Off | Off | Normal Operation | 34 | 33 | 34 | 30.5 | 51 | 6.9 | 0 | 72.8 | 81.5 | 2 | 5.2 | 21 | 182 | 66 | -0.4 | -0.8 | 47.6 | 47.2 | 50.6 | 255 | 211 | 2000 | 25.6 | 43.3 | 550 | 50.2 | Room | On | 28.1 | 47.2 | 50.6 | 48.9 | 1006.6701 | 4026.5814 | 3.4 | 6454.426 | 2.4 | 68% | -0.4 | 5200 | 30.5 | 72.8 | 557.0233 | 47.6 | 290.5615 | 266.4618 | 1.4534 | 2.1373 | 4.4203
45618.3415 | On | Off | Off | Off | Off | Normal Operation | 33 | 33 | 33 | 30.5 | 51 | 6.9 | 0 | 73 | 81.5 | 2 | 5 | 21 | 182 | 66 | -0.4 | -0.7 | 47.6 | 47.2 | 50.6 | 255 | 211 | 2000 | 25.8 | 43.3 | 550 | 50.2 | Room | On | 28.1 | 47.2 | 50.6 | 48.9 | 1006.6701 | 4026.5814 | 3.4 | 6454.426 | 2.4 | 66% | -0.4 | 5000 | 30.5 | 73 | 557.4002 | 47.6 | 290.5615 | 266.8386 | 1.4513 | 2.199 | 4.4203
45618.3416 | On | Off | Off | Off | Off | Normal Operation | 33 | 33 | 33 | 30.5 | 51 | 6.9 | 0 | 73 | 81.5 | 2 | 5 | 21 | 182 | 66 | -0.4 | -0.7 | 47.6 | 47.2 | 50.6 | 255 | 211 | 2000 | 26 | 43.3 | 550 | 50.2 | Room | On | 28.1 | 47.2 | 50.6 | 48.9 | 1006.6701 | 4026.5814 | 3.4 | 6454.426 | 2.4 | 66% | -0.4 | 5000 | 30.5 | 73 | 557.4002 | 47.6 | 290.5615 | 266.8386 | 1.4513 | 2.199 | 4.4203
45618.3418 | On | Off | Off | Off | Off | Normal Operation | 33 | 33 | 33 | 30.6 | 51 | 6.9 | 0 | 73.1 | 81.5 | 2 | 5 | 21 | 182 | 66 | -0.4 | -0.7 | 47.6 | 47.3 | 50.6 | 255 | 211 | 2000 | 26.2 | 43.3 | 550 | 50.2 | Room | On | 28.3 | 47.2 | 50.6 | 48.95 | 1006.6429 | 4026.5814 | 3.3 | 6309.0077 | 2.4 | 66% | -0.4 | 5000 | 30.6 | 73.1 | 557.3988 | 47.6 | 290.5756 | 266.8232 | 1.4187 | 2.1495 | 4.4348
45618.3419 | On | Off | Off | Off | Off | Normal Operation | 33 | 33 | 33 | 30.6 | 51 | 6.9 | 0 | 73.1 | 81.5 | 2 | 5.1 | 21 | 179 | 66 | -0.4 | -0.6 | 47.6 | 47.3 | 50.6 | 255 | 207 | 2000 | 26.2 | 43.5 | 550 | 50.2 | Room | On | 28.3 | 47.2 | 50.6 | 48.95 | 1006.6429 | 4026.5814 | 3.3 | 6309.0077 | 2.4 | 66% | -0.4 | 5100 | 30.6 | 73.1 | 557.3988 | 47.6 | 290.5756 | 266.8232 | 1.4187 | 2.1495 | 4.4348
45618.342 | On | Off | Off | Off | Off | Normal Operation | 33 | 33 | 33 | 30.5 | 51 | 6.9 | 0 | 73.1 | 81.5 | 2 | 5 | 21 | 179 | 66 | -0.4 | -0.6 | 47.6 | 47.3 | 50.6 | 255 | 207 | 2000 | 26.2 | 43.5 | 550 | 50.2 | Room | On | 28.3 | 47.2 | 50.6 | 48.95 | 1006.6429 | 4026.5814 | 3.3 | 6309.0077 | 2.4 | 66% | -0.4 | 5000 | 30.5 | 73.1 | 557.5886 | 47.6 | 290.5615 | 267.0271 | 1.4176 | 2.1479 | 4.4203
45618.3421 | On | Off | Off | Off | Off | Normal Operation | 33 | 33 | 33 | 30.6 | 51 | 6.9 | 0 | 73.1 | 81.5 | 2 | 5 | 20 | 179 | 66 | -0.4 | -0.6 | 47.6 | 47.3 | 50.6 | 256 | 207 | 2000 | 26.2 | 43.5 | 550 | 50.2 | Room | On | 28.3 | 47.2 | 50.6 | 48.95 | 1006.6429 | 4026.5814 | 3.3 | 6309.0077 | 2.4 | 66% | -0.4 | 5000 | 30.6 | 73.1 | 557.3988 | 47.6 | 290.5756 | 266.8232 | 1.4187 | 2.1495 | 4.4348
45618.3422 | On | Off | Off | Off | Off | Normal Operation | 33 | 33 | 33 | 30.6 | 51 | 6.9 | 0 | 73.1 | 81.5 | 2 | 5 | 20 | 179 | 66 | -0.4 | -0.6 | 47.6 | 47.3 | 50.6 | 256 | 207 | 2000 | 26.2 | 43.5 | 550 | 50.2 | Room | On | 28.1 | 47.3 | 50.6 | 48.95 | 1006.6429 | 4026.8165 | 3.3 | 6264.7869 | 2.4 | 66% | -0.4 | 5000 | 30.6 | 73.1 | 557.3988 | 47.6 | 290.5756 | 266.8232 | 1.4088 | 2.1345 | 4.4348
45618.3423 | On | Off | Off | Off | Off | Normal Operation | 33 | 33 | 33 | 30.5 | 51 | 6.9 | 0 | 73.2 | 81.5 | 2 | 5 | 21 | 179 | 66 | -0.3 | -0.6 | 47.6 | 47.3 | 50.6 | 256 | 207 | 2000 | 26.2 | 43.5 | 550 | 50.2 | Room | On | 28.1 | 47.3 | 50.6 | 48.95 | 1006.6429 | 4026.8165 | 3.3 | 6264.7869 | 2.3 | 66% | -0.4 | 5000 | 30.5 | 73.2 | 557.7771 | 47.6 | 290.5615 | 267.2155 | 1.4067 | 2.1313 | 4.4203
45618.3425 | On | Off | Off | Off | Off | Normal Operation | 33 | 33 | 33 | 30.4 | 51 | 6.9 | 0 | 73.2 | 81.5 | 2 | 5 | 21 | 179 | 66 | -0.3 | -0.6 | 47.6 | 47.3 | 50.4 | 256 | 207 | 2000 | 26.2 | 43.6 | 550 | 50.2 | Room | On | 28.1 | 47.3 | 50.6 | 48.85 | 1006.6972 | 4026.8165 | 3.1 | 5885.4199 | 2.3 | 66% | -0.2 | 5000 | 30.4 | 73.2 | 557.966 | 47.6 | 290.5475 | 267.4185 | 1.3205 | 2.0008 | 4.4058
45618.3426 | On | Off | Off | Off | Off | Normal Operation | 33 | 35 | 33 | 30.7 | 51 | 6.9 | 0 | 73.2 | 81.5 | 2 | 5 | 21 | 179 | 66 | -0.3 | -0.6 | 47.6 | 47.5 | 50.4 | 256 | 207 | 2000 | 26.2 | 43.5 | 550 | 50.2 | Room | On | 28.1 | 47.3 | 50.6 | 48.95 | 1006.6429 | 4026.8165 | 2.9 | 5505.4188 | 2.3 | 66% | -0.2 | 5000 | 30.7 | 73.2 | 557.3982 | 47.6 | 290.5896 | 266.8086 | 1.2381 | 1.8758 | 4.4493
45618.3427 | On | Off | Off | Off | Off | Normal Operation | 34 | 35 | 34 | 30.7 | 51 | 6.9 | 0 | 73.2 | 81.5 | 2 | 5 | 21 | 179 | 66 | -0.3 | -0.5 | 47.6 | 47.5 | 50.6 | 256 | 207 | 2000 | 26.2 | 43.5 | 550 | 50.2 | Room | On | 28.1 | 47.5 | 50.6 | 49.05 | 1006.5886 | 4027.2868 | 3.1 | 5885.4726 | 2.3 | 68% | -0.4 | 5000 | 30.7 | 73.2 | 557.3982 | 47.6 | 290.5896 | 266.8086 | 1.3235 | 1.9464 | 4.4493
45618.3428 | On | Off | Off | Off | Off | Normal Operation | 34 | 35 | 34 | 30.7 | 51 | 6.9 | 0 | 73.2 | 81.5 | 2 | 5.2 | 21 | 179 | 66 | -0.3 | -0.5 | 47.6 | 47.5 | 50.8 | 257 | 211 | 2000 | 26.1 | 43.8 | 550 | 50.2 | Room | On | 28.1 | 47.5 | 50.6 | 49.15 | 1006.5343 | 4027.2868 | 3.3 | 6264.8422 | 2.3 | 68% | -0.6 | 5200 | 30.7 | 73.2 | 557.3982 | 47.6 | 290.5896 | 266.8086 | 1.4088 | 2.0718 | 4.4493
45618.3429 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.7 | 51 | 6.9 | 0 | 73.2 | 81.5 | 2 | 5.3 | 21 | 179 | 66 | -0.3 | -0.5 | 47.6 | 47.3 | 50.8 | 257 | 211 | 2000 | 26 | 43.8 | 550 | 50.2 | Room | On | 28.1 | 47.5 | 50.6 | 49.05 | 1006.5886 | 4027.2868 | 3.5 | 6644.8884 | 2.3 | 70% | -0.6 | 5300 | 30.7 | 73.2 | 557.3982 | 47.6 | 290.5896 | 266.8086 | 1.4943 | 2.1347 | 4.4493
45618.343 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.7 | 51 | 6.9 | 0 | 73.2 | 81.5 | 2 | 5.3 | 21 | 179 | 66 | -0.3 | -0.6 | 47.6 | 47.3 | 50.8 | 257 | 211 | 2000 | 25.8 | 43.8 | 550 | 50.2 | Room | On | 28.1 | 47.5 | 50.6 | 49.05 | 1006.5886 | 4027.2868 | 3.5 | 6644.8884 | 2.3 | 70% | -0.6 | 5300 | 30.7 | 73.2 | 557.3982 | 47.6 | 290.5896 | 266.8086 | 1.4943 | 2.1347 | 4.4493
45618.3431 | On | Off | Off | Off | Off | Normal Operation | 35 | 35 | 35 | 30.7 | 51 | 6.9 | 0 | 73.2 | 81.5 | 2 | 5.3 | 21 | 179 | 66 | -0.4 | -0.7 | 47.6 | 47.3 | 50.8 | 257 | 211 | 2000 | 25.6 | 43.8 | 550 | 50.2 | Room | On | 27.9 | 47.3 | 50.8 | 49.05 | 1006.5886 | 4026.8165 | 3.5 | 6596.8235 | 2.4 | 70% | -0.6 | 5300 | 30.7 | 73.2 | 557.3982 | 47.6 | 290.5896 | 266.8086 | 1.4835 | 2.1193 | 4.4493
45618.3433 | On | Off | Off | Off | Off | Normal Operation | 35 | 29 | 35 | 30.9 | 51 | 6.9 | 0 | 73.2 | 81.7 | 2 | 5.3 | 21 | 179 | 66 | -0.4 | -0.7 | 47.6 | 47.5 | 50.8 | 257 | 215 | 2000 | 25.6 | 43.6 | 550 | 50.2 | Room | On | 27.9 | 47.3 | 50.8 | 49.15 | 1006.5343 | 4026.8165 | 3.3 | 6219.5262 | 2.4 | 70% | -0.6 | 5300 | 30.9 | 73.2 | 557.0182 | 47.6 | 290.6177 | 266.4005 | 1.4008 | 2.0011 | 4.4783
45618.3434 | On | Off | Off | Off | Off | Normal Operation | 34 | 29 | 34 | 30.8 | 51 | 6.9 | 0 | 73.2 | 81.7 | 2 | 5.3 | 21 | 179 | 66 | -0.5 | -0.8 | 47.7 | 47.6 | 51 | 257 | 215 | 2000 | 25.5 | 43.8 | 550 | 50.2 | Room | On | 27.9 | 47.3 | 50.8 | 49.3 | 1006.4526 | 4026.8165 | 3.4 | 6407.477 | 2.5 | 68% | -0.8 | 5300 | 30.8 | 73.2 | 557.2084 | 47.7 | 290.8044 | 266.404 | 1.4431 | 2.1222 | 4.4638
45618.3435 | On | Off | Off | Off | Off | Normal Operation | 34 | 29 | 34 | 30.8 | 51 | 6.9 | 0 | 73.2 | 81.8 | 2 | 5.2 | 21 | 183 | 66 | -0.5 | -0.8 | 47.7 | 47.6 | 51 | 257 | 215 | 2000 | 25.7 | 43.8 | 550 | 50.2 | Room | On | 27.9 | 47.3 | 50.8 | 49.3 | 1006.4526 | 4026.8165 | 3.4 | 6407.477 | 2.5 | 68% | -0.8 | 5200 | 30.8 | 73.2 | 557.2084 | 47.7 | 290.8044 | 266.404 | 1.4431 | 2.1222 | 4.4638
45618.3436 | On | Off | Off | Off | Off | Normal Operation | 33 | 29 | 33 | 30.7 | 51 | 6.9 | 0 | 73.4 | 82 | 2 | 5.1 | 21 | 183 | 66 | -0.5 | -0.8 | 47.7 | 47.6 | 51 | 257 | 215 | 2000 | 26 | 43.6 | 550 | 50.2 | Room | On | 28.1 | 47.6 | 51 | 49.3 | 1006.4526 | 4027.5219 | 3.4 | 6454.5392 | 2.5 | 66% | -0.8 | 5100 | 30.7 | 73.4 | 557.7773 | 47.7 | 290.7902 | 266.987 | 1.4505 | 2.1978 | 4.4493
45618.3437 | On | Off | Off | Off | Off | Normal Operation | 32 | 29 | 32 | 30.7 | 51 | 6.9 | 0 | 73.4 | 82 | 2 | 4.9 | 21 | 183 | 66 | -0.4 | -0.7 | 47.7 | 47.6 | 51 | 257 | 204 | 2000 | 26.3 | 43.6 | 540 | 50.2 | Room | On | 28.1 | 47.6 | 51 | 49.3 | 1006.4526 | 4027.5219 | 3.4 | 6454.5392 | 2.4 | 64% | -0.8 | 4900 | 30.7 | 73.4 | 557.7773 | 47.7 | 290.7902 | 266.987 | 1.4505 | 2.2665 | 4.4493
45618.3438 | On | Off | Off | Off | Off | Normal Operation | 32 | 29 | 32 | 30.7 | 51 | 7 | 0 | 73.5 | 82 | 2 | 4.9 | 21 | 183 | 66 | -0.3 | -0.6 | 47.7 | 47.6 | 51 | 257 | 204 | 2000 | 26.5 | 43.6 | 550 | 50.2 | Room | On | 28.1 | 47.6 | 51 | 49.3 | 1006.4526 | 4027.5219 | 3.4 | 6454.5392 | 2.3 | 64% | -0.8 | 4900 | 30.7 | 73.5 | 557.9668 | 47.7 | 290.7902 | 267.1765 | 1.4495 | 2.2648 | 4.3857
45618.344 | On | Off | Off | Off | Off | Normal Operation | 31 | 25 | 31 | 30.7 | 51 | 7 | 0 | 73.5 | 82 | 2 | 4.9 | 21 | 183 | 66 | -0.3 | -0.6 | 47.7 | 47.6 | 51 | 257 | 204 | 2000 | 26.5 | 43.6 | 550 | 50.2 | Room | On | 28.1 | 47.6 | 51 | 49.3 | 1006.4526 | 4027.5219 | 3.4 | 6454.5392 | 2.3 | 62% | -0.8 | 4900 | 30.7 | 73.5 | 557.9668 | 47.7 | 290.7902 | 267.1765 | 1.4495 | 2.3379 | 4.3857
45618.3441 | On | Off | Off | Off | Off | Normal Operation | 30 | 25 | 30 | 30.7 | 51 | 7 | 0 | 73.5 | 82 | 2 | 4.8 | 21 | 183 | 66 | -0.3 | -0.5 | 47.7 | 47.6 | 50.8 | 257 | 204 | 2000 | 26.6 | 43.8 | 540 | 50.2 | Room | On | 27.7 | 47.6 | 50.8 | 49.2 | 1006.5071 | 4027.5219 | 3.2 | 5988.7094 | 2.3 | 60% | -0.6 | 4800 | 30.7 | 73.5 | 557.9668 | 47.7 | 290.7902 | 267.1765 | 1.3449 | 2.2415 | 4.3857
45618.3442 | On | Off | Off | Off | Off | Normal Operation | 30 | 25 | 30 | 30.7 | 51 | 7 | 0 | 73.5 | 82 | 2 | 4.7 | 21 | 183 | 66 | -0.3 | -0.5 | 47.7 | 47.6 | 50.8 | 256 | 196 | 2000 | 26.6 | 44 | 550 | 50.2 | Room | On | 27.7 | 47.6 | 50.8 | 49.2 | 1006.5071 | 4027.5219 | 3.2 | 5988.7094 | 2.3 | 60% | -0.6 | 4700 | 30.7 | 73.5 | 557.9668 | 47.7 | 290.7902 | 267.1765 | 1.3449 | 2.2415 | 4.3857
45618.3443 | On | Off | Off | Off | Off | Normal Operation | 29 | 25 | 29 | 30.6 | 51 | 7 | 0 | 73.5 | 82 | 2 | 4.6 | 21 | 183 | 66 | -0.3 | -0.4 | 47.7 | 47.6 | 50.8 | 256 | 196 | 2000 | 26.7 | 44.2 | 550 | 50.2 | Room | On | 27.7 | 47.6 | 50.8 | 49.2 | 1006.5071 | 4027.5219 | 3.2 | 5988.7094 | 2.3 | 58% | -0.6 | 4600 | 30.6 | 73.5 | 558.1547 | 47.7 | 290.7761 | 267.3786 | 1.3439 | 2.317 | 4.3714
45618.3444 | On | Off | Off | Off | Off | Normal Operation | 28 | 25 | 28 | 30.6 | 51 | 7 | 0 | 73.5 | 82 | 2 | 4.5 | 21 | 183 | 66 | -0.2 | -0.4 | 47.7 | 47.6 | 50.8 | 256 | 196 | 2000 | 26.7 | 44.6 | 550 | 50.2 | Room | On | 27.7 | 47.6 | 50.8 | 49.2 | 1006.5071 | 4027.5219 | 3.2 | 5988.7094 | 2.2 | 56% | -0.6 | 4500 | 30.6 | 73.5 | 558.1547 | 47.7 | 290.7761 | 267.3786 | 1.3439 | 2.3998 | 4.3714
45618.3445 | On | Off | Off | Off | Off | Normal Operation | 28 | 25 | 28 | 30.5 | 51 | 7 | 0 | 73.5 | 82 | 2 | 4.3 | 20 | 183 | 66 | -0.1 | -0.3 | 47.7 | 47.6 | 50.6 | 256 | 196 | 2000 | 26.8 | 45 | 540 | 50.2 | Room | On | 28.1 | 47.6 | 50.6 | 49.1 | 1006.5615 | 4027.5219 | 3 | 5695.7974 | 2.1 | 56% | -0.4 | 4300 | 30.5 | 73.5 | 558.3424 | 47.7 | 290.762 | 267.5804 | 1.2772 | 2.2807 | 4.3571
45618.3447 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.5 | 51 | 7.1 | 0 | 73.4 | 82 | 2 | 4.2 | 20 | 183 | 66 | -0.1 | -0.2 | 47.6 | 47.6 | 50.6 | 256 | 184 | 2000 | 27 | 45.1 | 550 | 50.2 | Room | On | 28.1 | 47.6 | 50.6 | 49.1 | 1006.5615 | 4027.5219 | 3 | 5695.7974 | 2.1 | 54% | -0.4 | 4200 | 30.5 | 73.4 | 558.1539 | 47.6 | 290.5615 | 267.5924 | 1.2771 | 2.365 | 4.2958
45618.3448 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.5 | 51 | 7.1 | 0 | 73.4 | 82 | 2 | 4.2 | 20 | 183 | 66 | 0 | -0.2 | 47.6 | 47.6 | 50.6 | 256 | 184 | 2000 | 27.3 | 45.3 | 550 | 50.2 | Room | On | 28.1 | 47.6 | 50.6 | 49.1 | 1006.5615 | 4027.5219 | 3 | 5695.7974 | 2 | 54% | -0.4 | 4200 | 30.5 | 73.4 | 558.1539 | 47.6 | 290.5615 | 267.5924 | 1.2771 | 2.365 | 4.2958
45618.3449 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.5 | 51 | 7.1 | 0 | 73.4 | 81.8 | 2 | 4.2 | 20 | 183 | 66 | 0 | -0.1 | 47.6 | 47.6 | 50.6 | 254 | 184 | 2000 | 27.6 | 45.3 | 540 | 50.2 | Room | On | 28.1 | 47.6 | 50.6 | 49.1 | 1006.5615 | 4027.5219 | 3 | 5695.7974 | 2 | 54% | -0.4 | 4200 | 30.5 | 73.4 | 558.1539 | 47.6 | 290.5615 | 267.5924 | 1.2771 | 2.365 | 4.2958
45618.345 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.6 | 51 | 7.1 | 0 | 73.2 | 81.7 | 2 | 4.2 | 21 | 183 | 66 | 0 | -0.1 | 47.6 | 47.7 | 50.6 | 254 | 184 | 2000 | 27.7 | 45.5 | 550 | 50.2 | Room | On | 27.9 | 47.7 | 50.6 | 49.15 | 1006.5343 | 4027.757 | 2.9 | 5466.9209 | 2 | 54% | -0.4 | 4200 | 30.6 | 73.2 | 557.5878 | 47.6 | 290.5756 | 267.0122 | 1.2285 | 2.2749 | 4.3099
45618.3451 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.5 | 51 | 7.1 | 0 | 73.1 | 81.7 | 2 | 4.2 | 20 | 182 | 66 | 0 | 0 | 47.6 | 47.7 | 50.6 | 254 | 184 | 2000 | 27.8 | 45.5 | 550 | 50.2 | Room | On | 27.9 | 47.7 | 50.6 | 49.15 | 1006.5343 | 4027.757 | 2.9 | 5466.9209 | 2 | 54% | -0.4 | 4200 | 30.5 | 73.1 | 557.5886 | 47.6 | 290.5615 | 267.0271 | 1.2284 | 2.2748 | 4.2958
45618.3452 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.5 | 51 | 7.1 | 0 | 73.1 | 81.5 | 2 | 4.2 | 20 | 182 | 66 | 0 | 0 | 47.6 | 47.7 | 50.6 | 253 | 184 | 2000 | 27.8 | 45.5 | 550 | 50.2 | Room | On | 27.9 | 47.7 | 50.6 | 49.15 | 1006.5343 | 4027.757 | 2.9 | 5466.9209 | 2 | 54% | -0.4 | 4200 | 30.5 | 73.1 | 557.5886 | 47.6 | 290.5615 | 267.0271 | 1.2284 | 2.2748 | 4.2958
45618.3453 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.6 | 51 | 7.1 | 0 | 73 | 81.4 | 2 | 4.2 | 21 | 182 | 66 | 0 | 0 | 47.6 | 47.7 | 50.6 | 253 | 184 | 2000 | 27.8 | 45.5 | 550 | 50.2 | Room | On | 27.9 | 47.7 | 50.6 | 49.15 | 1006.5343 | 4027.757 | 2.9 | 5466.9209 | 2 | 54% | -0.4 | 4200 | 30.6 | 73 | 557.2098 | 47.6 | 290.5756 | 266.6342 | 1.2302 | 2.2782 | 4.3099
45618.3455 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.6 | 51 | 7.1 | 0 | 73 | 81.4 | 2 | 4.2 | 20 | 182 | 66 | 0 | 0 | 47.6 | 47.7 | 50.6 | 253 | 184 | 2000 | 27.8 | 45.6 | 550 | 50.2 | Room | On | 27.9 | 47.7 | 50.6 | 49.15 | 1006.5343 | 4027.757 | 2.9 | 5466.9209 | 2 | 54% | -0.4 | 4200 | 30.6 | 73 | 557.2098 | 47.6 | 290.5756 | 266.6342 | 1.2302 | 2.2782 | 4.3099
45618.3456 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.6 | 51 | 7.1 | 0 | 73 | 81.4 | 2 | 4.2 | 20 | 182 | 66 | 0 | 0 | 47.6 | 47.7 | 50.6 | 252 | 184 | 2000 | 27.8 | 45.6 | 550 | 50.2 | Room | On | 27.9 | 47.7 | 50.6 | 49.15 | 1006.5343 | 4027.757 | 2.9 | 5466.9209 | 2 | 54% | -0.4 | 4200 | 30.6 | 73 | 557.2098 | 47.6 | 290.5756 | 266.6342 | 1.2302 | 2.2782 | 4.3099
45618.3457 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.5 | 51 | 7.1 | 0 | 73 | 81.2 | 2 | 4.2 | 20 | 182 | 66 | 0 | 0 | 47.6 | 47.7 | 50.6 | 252 | 184 | 2000 | 28 | 45.6 | 550 | 50.2 | Room | On | 27.9 | 47.7 | 50.6 | 49.15 | 1006.5343 | 4027.757 | 2.9 | 5466.9209 | 2 | 54% | -0.4 | 4200 | 30.5 | 73 | 557.4002 | 47.6 | 290.5615 | 266.8386 | 1.2293 | 2.2764 | 4.2958
45618.3458 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.5 | 51 | 7.1 | 0 | 72.8 | 81.1 | 2 | 4.2 | 21 | 182 | 66 | 0 | 0 | 47.6 | 47.7 | 50.6 | 252 | 184 | 2000 | 28 | 45.6 | 550 | 50.2 | Room | On | 27.9 | 47.7 | 50.6 | 49.15 | 1006.5343 | 4027.757 | 2.9 | 5466.9209 | 2 | 54% | -0.4 | 4200 | 30.5 | 72.8 | 557.0233 | 47.6 | 290.5615 | 266.4618 | 1.231 | 2.2796 | 4.2958
45618.3459 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.5 | 51 | 7.1 | 0 | 72.8 | 81.1 | 2 | 4.2 | 20 | 182 | 66 | 0 | 0 | 47.6 | 47.7 | 50.6 | 251 | 184 | 2000 | 28 | 45.6 | 550 | 50.2 | Room | On | 27.9 | 47.7 | 50.6 | 49.15 | 1006.5343 | 4027.757 | 2.9 | 5466.9209 | 2 | 54% | -0.4 | 4200 | 30.5 | 72.8 | 557.0233 | 47.6 | 290.5615 | 266.4618 | 1.231 | 2.2796 | 4.2958
45618.346 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.5 | 51 | 7.1 | 0 | 72.8 | 81.1 | 2 | 4.2 | 21 | 182 | 66 | 0 | 0 | 47.6 | 47.7 | 50.6 | 251 | 184 | 2000 | 28 | 45.6 | 550 | 50.2 | Room | On | 28.1 | 47.7 | 50.6 | 49.15 | 1006.5343 | 4027.757 | 2.9 | 5506.1102 | 2 | 54% | -0.4 | 4200 | 30.5 | 72.8 | 557.0233 | 47.6 | 290.5615 | 266.4618 | 1.2398 | 2.296 | 4.2958
45618.3462 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.5 | 51 | 7.1 | 0 | 72.7 | 81 | 2 | 4.2 | 21 | 182 | 66 | 0 | 0 | 47.6 | 47.7 | 50.6 | 251 | 184 | 2000 | 28 | 45.6 | 550 | 50.2 | Room | On | 28.1 | 47.7 | 50.6 | 49.15 | 1006.5343 | 4027.757 | 2.9 | 5506.1102 | 2 | 54% | -0.4 | 4200 | 30.5 | 72.7 | 556.8349 | 47.6 | 290.5615 | 266.2733 | 1.2407 | 2.2976 | 4.2958
45618.3463 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.5 | 51 | 7.1 | 0 | 72.7 | 81 | 2 | 4.2 | 21 | 182 | 66 | 0 | 0 | 47.6 | 47.7 | 50.6 | 250 | 184 | 2000 | 28 | 45.6 | 550 | 50.2 | Room | On | 28.1 | 47.7 | 50.6 | 49.15 | 1006.5343 | 4027.757 | 2.9 | 5506.1102 | 2 | 54% | -0.4 | 4200 | 30.5 | 72.7 | 556.8349 | 47.6 | 290.5615 | 266.2733 | 1.2407 | 2.2976 | 4.2958
45618.3464 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.5 | 51 | 7.1 | 0 | 72.7 | 81 | 2 | 4.2 | 21 | 182 | 66 | 0 | 0 | 47.6 | 47.7 | 50.6 | 250 | 184 | 2000 | 28 | 45.6 | 540 | 50.2 | Room | On | 28.1 | 47.7 | 50.6 | 49.15 | 1006.5343 | 4027.757 | 2.9 | 5506.1102 | 2 | 54% | -0.4 | 4200 | 30.5 | 72.7 | 556.8349 | 47.6 | 290.5615 | 266.2733 | 1.2407 | 2.2976 | 4.2958
45618.3465 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.6 | 51 | 7.1 | 0 | 72.7 | 80.8 | 2 | 4.2 | 21 | 182 | 66 | 0 | 0 | 47.6 | 47.7 | 50.6 | 250 | 184 | 2000 | 28 | 45.6 | 540 | 50.2 | Room | On | 28.1 | 47.7 | 50.6 | 49.15 | 1006.5343 | 4027.757 | 2.9 | 5506.1102 | 2 | 54% | -0.4 | 4200 | 30.6 | 72.7 | 556.6429 | 47.6 | 290.5756 | 266.0673 | 1.2417 | 2.2994 | 4.3099
45618.3466 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.5 | 51 | 7.1 | 0 | 72.7 | 80.8 | 2 | 4.2 | 20 | 180 | 66 | 0 | 0 | 47.6 | 47.7 | 50.6 | 249 | 184 | 2000 | 28 | 45.6 | 550 | 50.2 | Room | On | 28.1 | 47.7 | 50.6 | 49.15 | 1006.5343 | 4027.757 | 2.9 | 5506.1102 | 2 | 54% | -0.4 | 4200 | 30.5 | 72.7 | 556.8349 | 47.6 | 290.5615 | 266.2733 | 1.2407 | 2.2976 | 4.2958
45618.3467 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.6 | 51 | 7.1 | 0 | 72.5 | 80.8 | 2 | 4.2 | 20 | 180 | 66 | 0 | 0 | 47.6 | 47.7 | 50.6 | 249 | 184 | 2000 | 28 | 45.6 | 550 | 50.2 | Room | On | 28.1 | 47.7 | 50.6 | 49.15 | 1006.5343 | 4027.757 | 2.9 | 5506.1102 | 2 | 54% | -0.4 | 4200 | 30.6 | 72.5 | 556.2649 | 47.6 | 290.5756 | 265.6894 | 1.2434 | 2.3027 | 4.3099
45618.3469 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.7 | 51 | 7.1 | 0 | 72.5 | 80.8 | 2 | 4.2 | 21 | 180 | 66 | 0 | 0 | 47.6 | 47.8 | 50.6 | 249 | 184 | 2000 | 28 | 45.6 | 550 | 50.2 | Room | On | 28.1 | 47.7 | 50.6 | 49.2 | 1006.5071 | 4027.757 | 2.8 | 5316.1007 | 2 | 54% | -0.4 | 4200 | 30.7 | 72.5 | 556.0716 | 47.6 | 290.5896 | 265.4819 | 1.2015 | 2.2249 | 4.3239
45618.347 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.6 | 51 | 7.1 | 0 | 72.5 | 80.8 | 2 | 4.2 | 21 | 180 | 66 | 0 | 0 | 47.6 | 47.8 | 50.6 | 250 | 184 | 2000 | 28.1 | 45.6 | 550 | 50.2 | Room | On | 28.3 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5354.2503 | 2 | 54% | -0.4 | 4200 | 30.6 | 72.5 | 556.2649 | 47.6 | 290.5756 | 265.6894 | 1.2091 | 2.2391 | 4.3099
45618.3471 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.5 | 51 | 7.1 | 0 | 72.5 | 80.8 | 2 | 4.2 | 21 | 180 | 66 | 0 | 0 | 47.6 | 47.7 | 50.6 | 250 | 184 | 2000 | 28.1 | 45.6 | 550 | 50.2 | Room | On | 28.3 | 47.8 | 50.6 | 49.15 | 1006.5343 | 4027.9921 | 2.9 | 5545.6234 | 2 | 54% | -0.4 | 4200 | 30.5 | 72.5 | 556.458 | 47.6 | 290.5615 | 265.8965 | 1.2514 | 2.3174 | 4.2958
45618.3472 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.5 | 51 | 7.1 | 0 | 72.7 | 80.8 | 2 | 4.2 | 21 | 180 | 66 | 0 | -0.1 | 47.6 | 47.7 | 50.6 | 250 | 184 | 2000 | 28.1 | 45.6 | 550 | 50.2 | Room | On | 28.3 | 47.8 | 50.6 | 49.15 | 1006.5343 | 4027.9921 | 2.9 | 5545.6234 | 2 | 54% | -0.4 | 4200 | 30.5 | 72.7 | 556.8349 | 47.6 | 290.5615 | 266.2733 | 1.2496 | 2.3141 | 4.2958
45618.3473 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.7 | 51 | 7.1 | 0 | 72.7 | 80.8 | 2 | 4.2 | 21 | 180 | 66 | 0 | -0.1 | 47.6 | 47.7 | 50.6 | 249 | 184 | 2000 | 28.1 | 45.6 | 550 | 50.2 | Room | On | 28.3 | 47.8 | 50.6 | 49.15 | 1006.5343 | 4027.9921 | 2.9 | 5545.6234 | 2 | 54% | -0.4 | 4200 | 30.7 | 72.7 | 556.4506 | 47.6 | 290.5896 | 265.861 | 1.2515 | 2.3177 | 4.3239
45618.3474 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.7 | 51 | 7.1 | 0 | 72.7 | 80.8 | 2 | 4.2 | 21 | 180 | 66 | 0 | -0.1 | 47.6 | 47.7 | 50.6 | 249 | 184 | 2000 | 28.1 | 45.6 | 550 | 50.2 | Room | On | 28.5 | 47.7 | 50.6 | 49.15 | 1006.5343 | 4027.757 | 2.9 | 5584.489 | 2 | 54% | -0.4 | 4200 | 30.7 | 72.7 | 556.4506 | 47.6 | 290.5896 | 265.861 | 1.2603 | 2.3339 | 4.3239
45618.3475 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.7 | 51 | 7.1 | 0 | 72.7 | 80.8 | 2 | 4.2 | 21 | 180 | 66 | 0 | -0.1 | 47.6 | 47.8 | 50.6 | 249 | 184 | 2000 | 28.1 | 45.6 | 550 | 50.2 | Room | On | 28.5 | 47.7 | 50.6 | 49.2 | 1006.5071 | 4027.757 | 2.8 | 5391.7748 | 2 | 54% | -0.4 | 4200 | 30.7 | 72.7 | 556.4506 | 47.6 | 290.5896 | 265.861 | 1.2168 | 2.2534 | 4.3239
45618.3477 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.7 | 51 | 7.1 | 0 | 72.7 | 81 | 2 | 4.2 | 21 | 180 | 66 | 0 | 0 | 47.6 | 47.8 | 50.6 | 248 | 184 | 2000 | 28.1 | 45.6 | 550 | 50.2 | Room | On | 28.5 | 47.7 | 50.6 | 49.2 | 1006.5071 | 4027.757 | 2.8 | 5391.7748 | 2 | 54% | -0.4 | 4200 | 30.7 | 72.7 | 556.4506 | 47.6 | 290.5896 | 265.861 | 1.2168 | 2.2534 | 4.3239
45618.3478 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.6 | 51 | 7.1 | 0 | 72.7 | 81 | 2 | 4.2 | 20 | 180 | 66 | 0 | 0 | 47.6 | 47.8 | 50.6 | 248 | 184 | 2000 | 28.1 | 45.6 | 550 | 50.2 | Room | On | 28.5 | 47.7 | 50.6 | 49.2 | 1006.5071 | 4027.757 | 2.8 | 5391.7748 | 2 | 54% | -0.4 | 4200 | 30.6 | 72.7 | 556.6429 | 47.6 | 290.5756 | 266.0673 | 1.2159 | 2.2516 | 4.3099
45618.3479 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.6 | 51 | 7.1 | 0 | 72.7 | 81 | 2 | 4.2 | 21 | 180 | 66 | 0 | 0 | 47.6 | 47.8 | 50.6 | 248 | 184 | 2000 | 28.1 | 45.6 | 550 | 50.2 | Room | On | 27.9 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5278.5718 | 2 | 54% | -0.4 | 4200 | 30.6 | 72.7 | 556.6429 | 47.6 | 290.5756 | 266.0673 | 1.1904 | 2.2044 | 4.3099
45618.348 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.6 | 51 | 7.1 | 0 | 72.7 | 81 | 2 | 4.2 | 21 | 180 | 66 | 0 | 0 | 47.6 | 47.8 | 50.6 | 249 | 184 | 2000 | 28.1 | 45.6 | 550 | 50.2 | Room | On | 27.9 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5278.5718 | 2 | 54% | -0.4 | 4200 | 30.6 | 72.7 | 556.6429 | 47.6 | 290.5756 | 266.0673 | 1.1904 | 2.2044 | 4.3099
45618.3481 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.7 | 51 | 7.1 | 0 | 72.7 | 81 | 2 | 4.2 | 21 | 180 | 66 | 0.1 | 0 | 47.6 | 47.8 | 50.6 | 249 | 184 | 2000 | 28.1 | 45.6 | 550 | 50.2 | Room | On | 27.9 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5278.5718 | 1.9 | 54% | -0.4 | 4200 | 30.7 | 72.7 | 556.4506 | 47.6 | 290.5896 | 265.861 | 1.1913 | 2.2061 | 4.3239
45618.3482 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.6 | 51 | 7.1 | 0 | 72.7 | 81 | 2 | 4.2 | 20 | 180 | 66 | 0.1 | 0 | 47.6 | 47.8 | 50.6 | 249 | 184 | 2000 | 28.1 | 45.6 | 550 | 50.2 | Room | On | 27.9 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5278.5718 | 1.9 | 54% | -0.4 | 4200 | 30.6 | 72.7 | 556.6429 | 47.6 | 290.5756 | 266.0673 | 1.1904 | 2.2044 | 4.3099
45618.3484 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.7 | 51 | 7.1 | 0 | 72.7 | 81 | 2 | 4.2 | 21 | 180 | 66 | 0.1 | 0 | 47.6 | 47.8 | 50.6 | 248 | 184 | 2000 | 28.1 | 45.6 | 550 | 50.2 | Room | On | 28.1 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5316.4111 | 1.9 | 54% | -0.4 | 4200 | 30.7 | 72.7 | 556.4506 | 47.6 | 290.5896 | 265.861 | 1.1998 | 2.2219 | 4.3239
45618.3485 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.7 | 51 | 7.1 | 0 | 72.7 | 81 | 2 | 4.2 | 20 | 180 | 66 | 0.1 | 0 | 47.6 | 47.8 | 50.6 | 248 | 184 | 2000 | 28.1 | 45.6 | 550 | 50.2 | Room | On | 28.1 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5316.4111 | 1.9 | 54% | -0.4 | 4200 | 30.7 | 72.7 | 556.4506 | 47.6 | 290.5896 | 265.861 | 1.1998 | 2.2219 | 4.3239
45618.3486 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.7 | 51 | 7.1 | 0 | 72.7 | 81.1 | 2 | 4.2 | 20 | 180 | 66 | 0.1 | 0 | 47.6 | 47.8 | 50.8 | 248 | 184 | 2000 | 28.1 | 45.6 | 550 | 50.2 | Room | On | 28.1 | 47.8 | 50.6 | 49.3 | 1006.4526 | 4027.9921 | 3 | 5695.8466 | 1.9 | 54% | -0.6 | 4200 | 30.7 | 72.7 | 556.4506 | 47.6 | 290.5896 | 265.861 | 1.2854 | 2.3805 | 4.3239
45618.3487 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.7 | 51 | 7.1 | 0 | 72.7 | 81.1 | 2 | 4.2 | 21 | 180 | 66 | 0 | 0 | 47.6 | 47.8 | 50.8 | 247 | 184 | 2000 | 28.1 | 45.6 | 550 | 50.2 | Room | On | 28.1 | 47.8 | 50.6 | 49.3 | 1006.4526 | 4027.9921 | 3 | 5695.8466 | 2 | 54% | -0.6 | 4200 | 30.7 | 72.7 | 556.4506 | 47.6 | 290.5896 | 265.861 | 1.2854 | 2.3805 | 4.3239
45618.3488 | On | Off | Off | Off | Off | Normal Operation | 27 | 25 | 27 | 30.7 | 51 | 7.1 | 0 | 72.8 | 81.1 | 2 | 4.2 | 21 | 180 | 66 | 0 | 0 | 47.7 | 47.8 | 50.8 | 247 | 184 | 2000 | 28.1 | 45.6 | 550 | 50.2 | Room | On | 27.9 | 47.8 | 50.8 | 49.3 | 1006.4526 | 4027.9921 | 3 | 5655.3068 | 2 | 54% | -0.6 | 4200 | 30.7 | 72.8 | 556.6401 | 47.7 | 290.7902 | 265.8499 | 1.2764 | 2.3636 | 4.3239
45618.3489 | On | Off | Off | Off | Off | Normal Operation | 26 | 25 | 26 | 30.7 | 51 | 7.1 | 0 | 72.8 | 81.1 | 2 | 4.1 | 20 | 180 | 66 | 0 | 0 | 47.7 | 47.8 | 50.8 | 247 | 184 | 2000 | 28.1 | 45.6 | 550 | 50.2 | Room | On | 27.9 | 47.8 | 50.8 | 49.3 | 1006.4526 | 4027.9921 | 3 | 5655.3068 | 2 | 52% | -0.6 | 4100 | 30.7 | 72.8 | 556.6401 | 47.7 | 290.7902 | 265.8499 | 1.2764 | 2.4545 | 4.3239
45618.3491 | On | Off | Off | Off | Off | Normal Operation | 26 | 25 | 26 | 30.7 | 51 | 7.1 | 0 | 72.8 | 81.1 | 2 | 4.1 | 20 | 180 | 66 | 0 | 0 | 47.7 | 47.8 | 50.8 | 247 | 184 | 2000 | 28.1 | 45.6 | 550 | 50.2 | Room | On | 27.9 | 47.8 | 50.8 | 49.3 | 1006.4526 | 4027.9921 | 3 | 5655.3068 | 2 | 52% | -0.6 | 4100 | 30.7 | 72.8 | 556.6401 | 47.7 | 290.7902 | 265.8499 | 1.2764 | 2.4545 | 4.3239
45618.3492 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.6 | 51 | 7.1 | 0 | 72.8 | 81.1 | 2 | 4.1 | 20 | 180 | 66 | 0 | 0 | 47.7 | 47.8 | 50.8 | 246 | 184 | 2000 | 28.2 | 45.6 | 550 | 50.2 | Room | On | 27.9 | 47.8 | 50.8 | 49.3 | 1006.4526 | 4027.9921 | 3 | 5655.3068 | 2 | 50% | -0.6 | 4100 | 30.6 | 72.8 | 556.8319 | 47.7 | 290.7761 | 266.0558 | 1.2754 | 2.5507 | 4.3099
45618.3493 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.5 | 51 | 7.1 | 0 | 72.7 | 81.1 | 2 | 4 | 21 | 180 | 66 | 0.1 | 0 | 47.7 | 47.7 | 50.6 | 246 | 176 | 2000 | 28.7 | 45.6 | 550 | 50.2 | Room | On | 27.9 | 47.7 | 50.6 | 49.15 | 1006.5343 | 4027.757 | 2.9 | 5466.9209 | 1.9 | 50% | -0.4 | 4000 | 30.5 | 72.7 | 556.8349 | 47.7 | 290.762 | 266.0729 | 1.2328 | 2.4656 | 4.2958
45618.3494 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.4 | 51 | 7.1 | 0 | 72.7 | 81.1 | 2 | 4 | 21 | 180 | 66 | 0.1 | 0 | 47.6 | 47.7 | 50.4 | 245 | 176 | 2000 | 29.3 | 45.6 | 550 | 50.2 | Room | On | 27.9 | 47.7 | 50.6 | 49.05 | 1006.5886 | 4027.757 | 2.7 | 5090.1667 | 1.9 | 50% | -0.2 | 4000 | 30.4 | 72.7 | 557.0266 | 47.6 | 290.5475 | 266.4791 | 1.1461 | 2.2922 | 4.2817
45618.3495 | On | Off | Off | Off | Off | Normal Operation | 25 | 27 | 25 | 30.7 | 51 | 7.1 | 0 | 72.5 | 81.1 | 2 | 4 | 21 | 180 | 66 | 0.1 | 0.1 | 47.6 | 47.8 | 50.4 | 245 | 176 | 2000 | 29.7 | 45.3 | 550 | 50.2 | Room | On | 27.9 | 47.7 | 50.6 | 49.1 | 1006.5615 | 4027.757 | 2.6 | 4901.5097 | 1.9 | 50% | -0.2 | 4000 | 30.7 | 72.5 | 556.0716 | 47.6 | 290.5896 | 265.4819 | 1.1078 | 2.2155 | 4.3239
45618.3496 | On | Off | Off | Off | Off | Normal Operation | 26 | 27 | 26 | 30.6 | 51 | 7.1 | 0 | 72.5 | 81 | 2.1 | 4 | 21 | 180 | 66 | 0.1 | 0.1 | 47.6 | 47.8 | 50.6 | 245 | 176 | 2000 | 29.7 | 45.3 | 550 | 50.2 | Room | On | 27.9 | 47.7 | 50.6 | 49.2 | 1006.5071 | 4027.757 | 2.8 | 5278.2637 | 2 | 52% | -0.4 | 4000 | 30.6 | 72.5 | 556.2649 | 47.6 | 290.5756 | 265.6894 | 1.192 | 2.2923 | 4.3099
45618.3497 | On | Off | Off | Off | Off | Normal Operation | 26 | 27 | 26 | 30.5 | 51 | 7.1 | 0 | 72.4 | 81 | 2.1 | 4.1 | 21 | 180 | 66 | 0.1 | 0.1 | 47.6 | 47.8 | 50.6 | 244 | 180 | 2000 | 29.8 | 45.5 | 550 | 50.2 | Room | On | 27.7 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5240.7326 | 2 | 52% | -0.4 | 4100 | 30.5 | 72.4 | 556.2696 | 47.6 | 290.5615 | 265.708 | 1.1834 | 2.2758 | 4.2958
45618.3499 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.6 | 51 | 7.1 | 0 | 72.4 | 80.8 | 2.1 | 4.2 | 21 | 183 | 66 | 0.2 | 0.1 | 47.6 | 47.7 | 50.6 | 244 | 180 | 2000 | 29.5 | 45.5 | 550 | 50.2 | Room | On | 27.7 | 47.8 | 50.6 | 49.15 | 1006.5343 | 4027.9921 | 2.9 | 5428.0483 | 1.9 | 54% | -0.4 | 4200 | 30.6 | 72.4 | 556.076 | 47.6 | 290.5756 | 265.5004 | 1.2267 | 2.2716 | 4.3099
45618.35 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.7 | 51 | 7.1 | 0 | 72.4 | 80.8 | 2.1 | 4.2 | 20 | 183 | 66 | 0.2 | 0.1 | 47.6 | 47.7 | 50.6 | 244 | 180 | 2000 | 29 | 45.5 | 550 | 50.2 | Room | On | 27.7 | 47.8 | 50.6 | 49.15 | 1006.5343 | 4027.9921 | 2.9 | 5428.0483 | 1.9 | 54% | -0.4 | 4200 | 30.7 | 72.4 | 555.8821 | 47.6 | 290.5896 | 265.2924 | 1.2276 | 2.2734 | 4.3239
45618.3501 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.7 | 51 | 7.1 | 0 | 72.4 | 80.8 | 2.1 | 4.2 | 20 | 183 | 66 | 0.2 | 0 | 47.6 | 47.8 | 50.6 | 245 | 180 | 2000 | 28.6 | 45.5 | 550 | 50.2 | Room | On | 27.7 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5240.7326 | 1.9 | 54% | -0.4 | 4200 | 30.7 | 72.4 | 555.8821 | 47.6 | 290.5896 | 265.2924 | 1.1853 | 2.195 | 4.3239
45618.3502 | On | Off | Off | Off | Off | Normal Operation | 27 | 25 | 27 | 30.6 | 51 | 7.1 | 0 | 72.5 | 80.7 | 2.1 | 4.2 | 21 | 183 | 66 | 0.2 | 0 | 47.6 | 47.7 | 50.6 | 245 | 184 | 2000 | 28.5 | 45.6 | 550 | 50.2 | Room | On | 27.9 | 47.8 | 50.6 | 49.15 | 1006.5343 | 4027.9921 | 2.9 | 5467.24 | 1.9 | 54% | -0.4 | 4200 | 30.6 | 72.5 | 556.2649 | 47.6 | 290.5756 | 265.6894 | 1.2347 | 2.2864 | 4.3099
45618.3503 | On | Off | Off | Off | Off | Normal Operation | 26 | 25 | 27 | 30.8 | 51 | 7.1 | 0 | 72.5 | 80.7 | 2.2 | 4.2 | 21 | 183 | 66 | 0.2 | 0 | 47.6 | 47.8 | 50.6 | 245 | 184 | 2000 | 28.3 | 45.6 | 550 | 50.2 | Room | On | 27.9 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5278.5718 | 2 | 54% | -0.4 | 4200 | 30.8 | 72.5 | 555.8779 | 47.6 | 290.6037 | 265.2742 | 1.1939 | 2.2109 | 4.338
45618.3504 | On | Off | Off | Off | Off | Normal Operation | 26 | 25 | 26 | 30.7 | 51 | 7.1 | 0 | 72.7 | 80.8 | 2.2 | 4.1 | 21 | 183 | 66 | 0.2 | 0 | 47.7 | 48 | 50.8 | 245 | 184 | 2000 | 28.5 | 45.6 | 550 | 50.2 | Room | On | 27.9 | 47.8 | 50.6 | 49.4 | 1006.3982 | 4027.9921 | 2.8 | 5278.0005 | 2 | 52% | -0.6 | 4100 | 30.7 | 72.7 | 556.4506 | 47.7 | 290.7902 | 265.6604 | 1.192 | 2.2924 | 4.3239
45618.3506 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.6 | 51 | 7.1 | 0 | 72.7 | 80.8 | 2.2 | 4 | 20 | 183 | 66 | 0.2 | 0.1 | 47.7 | 48 | 50.8 | 245 | 184 | 2000 | 28.8 | 45.6 | 550 | 50.2 | Room | On | 27.9 | 47.8 | 50.6 | 49.4 | 1006.3982 | 4027.9921 | 2.8 | 5278.0005 | 2 | 50% | -0.6 | 4000 | 30.6 | 72.7 | 556.6429 | 47.7 | 290.7761 | 265.8668 | 1.1911 | 2.3822 | 4.3099
45618.3507 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.6 | 51 | 7.1 | 0 | 72.7 | 80.8 | 2.2 | 4 | 20 | 183 | 66 | 0.2 | 0.1 | 47.7 | 48 | 50.8 | 245 | 184 | 2000 | 29.3 | 45.6 | 550 | 50.1 | Room | On | 27.9 | 48 | 50.8 | 49.4 | 1006.3982 | 4028.4624 | 2.8 | 5278.6167 | 2 | 50% | -0.7 | 4000 | 30.6 | 72.7 | 556.6429 | 47.7 | 290.7761 | 265.8668 | 1.1913 | 2.3825 | 4.3099
45618.3508 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.6 | 51 | 7.1 | 0 | 72.7 | 80.8 | 2.2 | 4 | 20 | 183 | 66 | 0.2 | 0.1 | 47.7 | 48 | 50.8 | 244 | 176 | 2000 | 29.3 | 45.6 | 550 | 50.1 | Room | On | 27.9 | 48 | 50.8 | 49.4 | 1006.3982 | 4028.4624 | 2.8 | 5278.6167 | 2 | 50% | -0.7 | 4000 | 30.6 | 72.7 | 556.6429 | 47.7 | 290.7761 | 265.8668 | 1.1913 | 2.3825 | 4.3099
45618.3509 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.5 | 51 | 7.1 | 0 | 72.5 | 80.8 | 2.2 | 4 | 21 | 183 | 66 | 0.2 | 0.1 | 47.7 | 47.8 | 50.6 | 244 | 176 | 2000 | 29.7 | 45.6 | 550 | 50.1 | Room | On | 27.9 | 48 | 50.8 | 49.2 | 1006.5071 | 4028.4624 | 2.8 | 5279.1881 | 2 | 50% | -0.5 | 4000 | 30.5 | 72.5 | 556.458 | 47.7 | 290.762 | 265.696 | 1.1922 | 2.3843 | 4.2958
45618.351 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.5 | 51 | 7.1 | 0 | 72.5 | 80.8 | 2.2 | 4 | 21 | 183 | 66 | 0.2 | 0.1 | 47.7 | 47.8 | 50.6 | 244 | 176 | 2000 | 29.7 | 45.6 | 550 | 50.1 | Room | On | 27.9 | 48 | 50.8 | 49.2 | 1006.5071 | 4028.4624 | 2.8 | 5279.1881 | 2 | 50% | -0.5 | 4000 | 30.5 | 72.5 | 556.458 | 47.7 | 290.762 | 265.696 | 1.1922 | 2.3843 | 4.2958
45618.3511 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.5 | 51 | 7.1 | 0 | 72.5 | 80.8 | 2.2 | 4 | 21 | 183 | 66 | 0.2 | 0.1 | 47.7 | 47.8 | 50.6 | 243 | 176 | 2000 | 29.7 | 45.6 | 550 | 50.1 | Room | On | 28.3 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5354.2503 | 2 | 50% | -0.5 | 4000 | 30.5 | 72.5 | 556.458 | 47.7 | 290.762 | 265.696 | 1.2091 | 2.4182 | 4.2958
45618.3512 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.6 | 51 | 7.2 | 1 | 72.4 | 80.8 | 2.2 | 4 | 21 | 183 | 66 | 0.3 | 0.1 | 47.7 | 47.8 | 50.6 | 243 | 176 | 2000 | 29.8 | 45.6 | 550 | 50.1 | Room | On | 28.3 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5354.2503 | 1.9 | 50% | -0.5 | 4000 | 30.6 | 72.4 | 556.076 | 47.7 | 290.7761 | 265.2999 | 1.2109 | 2.4218 | 4.25
45618.3514 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.6 | 51 | 7.2 | 1 | 72.4 | 80.8 | 2.2 | 4 | 21 | 181 | 66 | 0.3 | 0.2 | 47.7 | 47.8 | 50.6 | 243 | 176 | 2000 | 29.8 | 45.6 | 550 | 50.1 | Room | On | 28.3 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5354.2503 | 1.9 | 50% | -0.5 | 4000 | 30.6 | 72.4 | 556.076 | 47.7 | 290.7761 | 265.2999 | 1.2109 | 2.4218 | 4.25
45618.3515 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.5 | 51 | 7.2 | 1 | 72.4 | 80.7 | 2.2 | 4 | 21 | 181 | 66 | 0.3 | 0.2 | 47.7 | 47.8 | 50.6 | 243 | 176 | 2000 | 29.8 | 45.6 | 550 | 50.1 | Room | On | 28.3 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5354.2503 | 1.9 | 50% | -0.5 | 4000 | 30.5 | 72.4 | 556.2696 | 47.7 | 290.762 | 265.5076 | 1.21 | 2.4199 | 4.2361
45618.3516 | On | Off | Off | Off | Off | Normal Operation | 25 | 27 | 25 | 30.5 | 51 | 7.2 | 1 | 72.4 | 80.7 | 2.2 | 4 | 21 | 181 | 66 | 0.3 | 0.2 | 47.6 | 47.7 | 50.4 | 242 | 176 | 2000 | 29.8 | 45.5 | 550 | 50.1 | Room | On | 28.1 | 47.7 | 50.4 | 49.05 | 1006.5886 | 4027.757 | 2.7 | 5126.6553 | 1.9 | 50% | -0.3 | 4000 | 30.5 | 72.4 | 556.2696 | 47.6 | 290.5615 | 265.708 | 1.1577 | 2.3153 | 4.2361
45618.3517 | On | Off | Off | Off | Off | Normal Operation | 26 | 27 | 26 | 30.5 | 51 | 7.2 | 1 | 72.4 | 80.5 | 2.2 | 4 | 21 | 181 | 66 | 0.3 | 0.2 | 47.6 | 47.7 | 50.4 | 242 | 176 | 2000 | 29.8 | 45.5 | 550 | 50.1 | Room | On | 28.1 | 47.7 | 50.4 | 49.05 | 1006.5886 | 4027.757 | 2.7 | 5126.6553 | 1.9 | 52% | -0.3 | 4000 | 30.5 | 72.4 | 556.2696 | 47.6 | 290.5615 | 265.708 | 1.1577 | 2.2263 | 4.2361
45618.3518 | On | Off | Off | Off | Off | Normal Operation | 26 | 27 | 26 | 30.6 | 51 | 7.1 | 0 | 72.2 | 80.5 | 2.2 | 4.1 | 20 | 181 | 66 | 0.3 | 0.2 | 47.6 | 47.7 | 50.4 | 242 | 176 | 2000 | 29.8 | 45.5 | 550 | 50.1 | Room | On | 28.1 | 47.7 | 50.4 | 49.05 | 1006.5886 | 4027.757 | 2.7 | 5126.6553 | 1.9 | 52% | -0.3 | 4100 | 30.6 | 72.2 | 555.698 | 47.6 | 290.5756 | 265.1224 | 1.1602 | 2.2312 | 4.3099
45618.3519 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.7 | 51 | 7.1 | 0 | 72.2 | 80.5 | 2.2 | 4.2 | 20 | 181 | 66 | 0.3 | 0.2 | 47.6 | 47.8 | 50.6 | 243 | 176 | 2000 | 29.6 | 45.5 | 550 | 50.1 | Room | On | 28.1 | 47.7 | 50.4 | 49.2 | 1006.5071 | 4027.757 | 2.8 | 5316.1007 | 1.9 | 54% | -0.5 | 4200 | 30.7 | 72.2 | 555.503 | 47.6 | 290.5896 | 264.9134 | 1.204 | 2.2297 | 4.3239
45618.3521 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.7 | 51 | 7.1 | 0 | 72.4 | 80.5 | 2.2 | 4.2 | 20 | 181 | 66 | 0.3 | 0.2 | 47.6 | 47.8 | 50.8 | 243 | 184 | 2000 | 29 | 45.5 | 550 | 50.1 | Room | On | 28.1 | 47.8 | 50.6 | 49.3 | 1006.4526 | 4027.9921 | 3 | 5695.8466 | 1.9 | 54% | -0.7 | 4200 | 30.7 | 72.4 | 555.8821 | 47.6 | 290.5896 | 265.2924 | 1.2882 | 2.3856 | 4.3239
45618.3522 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.7 | 51 | 7.1 | 0 | 72.5 | 80.5 | 2.2 | 4.2 | 20 | 181 | 66 | 0.3 | 0.2 | 47.6 | 47.8 | 50.8 | 243 | 184 | 2000 | 28.6 | 45.6 | 550 | 50.1 | Room | On | 28.1 | 47.8 | 50.6 | 49.3 | 1006.4526 | 4027.9921 | 3 | 5695.8466 | 1.9 | 54% | -0.7 | 4200 | 30.7 | 72.5 | 556.0716 | 47.6 | 290.5896 | 265.4819 | 1.2873 | 2.3839 | 4.3239
45618.3523 | On | Off | Off | Off | Off | Normal Operation | 27 | 25 | 27 | 30.7 | 51 | 7.1 | 0 | 72.5 | 80.5 | 2.2 | 4.2 | 20 | 181 | 66 | 0.3 | 0.2 | 47.6 | 47.8 | 50.8 | 243 | 184 | 2000 | 28.3 | 45.6 | 550 | 50.1 | Room | On | 28.1 | 47.8 | 50.6 | 49.3 | 1006.4526 | 4027.9921 | 3 | 5695.8466 | 1.9 | 54% | -0.7 | 4200 | 30.7 | 72.5 | 556.0716 | 47.6 | 290.5896 | 265.4819 | 1.2873 | 2.3839 | 4.3239
45618.3524 | On | Off | Off | Off | Off | Normal Operation | 26 | 25 | 26 | 30.7 | 51 | 7.1 | 0 | 72.5 | 80.5 | 2.2 | 4.2 | 21 | 181 | 66 | 0.3 | 0.2 | 47.7 | 47.8 | 50.8 | 243 | 184 | 2000 | 28.3 | 45.6 | 540 | 50.1 | Room | On | 28.1 | 47.8 | 50.6 | 49.3 | 1006.4526 | 4027.9921 | 3 | 5695.8466 | 1.9 | 52% | -0.7 | 4200 | 30.7 | 72.5 | 556.0716 | 47.7 | 290.7902 | 265.2813 | 1.2883 | 2.4774 | 4.3239
45618.3525 | On | Off | Off | Off | Off | Normal Operation | 26 | 25 | 26 | 30.7 | 51 | 7.1 | 0 | 72.7 | 80.7 | 2.2 | 4.1 | 20 | 181 | 66 | 0.3 | 0.2 | 47.7 | 47.8 | 50.8 | 243 | 184 | 2000 | 28.2 | 45.8 | 540 | 50.1 | Room | On | 27.9 | 47.8 | 50.8 | 49.3 | 1006.4526 | 4027.9921 | 3 | 5655.3068 | 1.9 | 52% | -0.7 | 4100 | 30.7 | 72.7 | 556.4506 | 47.7 | 290.7902 | 265.6604 | 1.2773 | 2.4563 | 4.3239
45618.3526 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.7 | 51 | 7.1 | 0 | 72.7 | 80.8 | 2.2 | 4.1 | 21 | 181 | 66 | 0.3 | 0.2 | 47.7 | 47.8 | 50.8 | 243 | 180 | 2000 | 28.5 | 45.8 | 550 | 50.1 | Room | On | 27.9 | 47.8 | 50.8 | 49.3 | 1006.4526 | 4027.9921 | 3 | 5655.3068 | 1.9 | 50% | -0.7 | 4100 | 30.7 | 72.7 | 556.4506 | 47.7 | 290.7902 | 265.6604 | 1.2773 | 2.5545 | 4.3239
45618.3528 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.7 | 51 | 7.1 | 0 | 72.8 | 80.8 | 2.2 | 4 | 21 | 181 | 66 | 0.3 | 0.2 | 47.7 | 47.8 | 50.8 | 243 | 180 | 2000 | 29 | 45.8 | 540 | 50.1 | Room | On | 27.9 | 47.8 | 50.8 | 49.3 | 1006.4526 | 4027.9921 | 3 | 5655.3068 | 1.9 | 50% | -0.7 | 4000 | 30.7 | 72.8 | 556.6401 | 47.7 | 290.7902 | 265.8499 | 1.2764 | 2.5527 | 4.3239
45618.3529 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.5 | 51 | 7.1 | 0 | 72.7 | 81 | 2.2 | 4 | 21 | 181 | 66 | 0.3 | 0.2 | 47.7 | 47.8 | 50.6 | 243 | 180 | 2000 | 29.6 | 45.8 | 550 | 50.1 | Room | On | 27.9 | 47.8 | 50.8 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5278.5718 | 1.9 | 50% | -0.5 | 4000 | 30.5 | 72.7 | 556.8349 | 47.7 | 290.762 | 266.0729 | 1.1903 | 2.3807 | 4.2958
45618.353 | On | Off | Off | Off | Off | Normal Operation | 25 | 26 | 25 | 30.5 | 51 | 7.2 | 1 | 72.7 | 81 | 2.2 | 4 | 21 | 179 | 66 | 0.3 | 0.2 | 47.7 | 47.8 | 50.6 | 242 | 180 | 2000 | 29.7 | 45.6 | 550 | 50.1 | Room | On | 28.3 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5354.2503 | 1.9 | 50% | -0.5 | 4000 | 30.5 | 72.7 | 556.8349 | 47.7 | 290.762 | 266.0729 | 1.2074 | 2.4148 | 4.2361
45618.3531 | On | Off | Off | Off | Off | Normal Operation | 26 | 26 | 26 | 30.7 | 51 | 7.2 | 1 | 72.5 | 81 | 2.2 | 4 | 21 | 179 | 66 | 0.3 | 0.2 | 47.6 | 47.8 | 50.6 | 242 | 176 | 2000 | 29.8 | 45.6 | 550 | 50.1 | Room | On | 28.3 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5354.2503 | 1.9 | 52% | -0.5 | 4000 | 30.7 | 72.5 | 556.0716 | 47.6 | 290.5896 | 265.4819 | 1.2101 | 2.3271 | 4.2639
45618.3532 | On | Off | Off | Off | Off | Normal Operation | 26 | 26 | 26 | 30.7 | 51 | 7.2 | 1 | 72.5 | 81 | 2.2 | 4.1 | 20 | 179 | 66 | 0.3 | 0.2 | 47.6 | 47.8 | 50.6 | 242 | 176 | 2000 | 29.8 | 45.6 | 550 | 50.1 | Room | On | 28.3 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5354.2503 | 1.9 | 52% | -0.5 | 4100 | 30.7 | 72.5 | 556.0716 | 47.6 | 290.5896 | 265.4819 | 1.2101 | 2.3271 | 4.2639
45618.3533 | On | Off | Off | Off | Off | Normal Operation | 26 | 26 | 26 | 30.7 | 51 | 7.1 | 0 | 72.5 | 81 | 2.2 | 4.1 | 20 | 179 | 66 | 0.3 | 0.2 | 47.6 | 47.8 | 50.6 | 242 | 176 | 2000 | 29.5 | 45.6 | 550 | 50.1 | Room | On | 28.3 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5354.2503 | 1.9 | 52% | -0.5 | 4100 | 30.7 | 72.5 | 556.0716 | 47.6 | 290.5896 | 265.4819 | 1.2101 | 2.3271 | 4.3239
45618.3534 | On | Off | Off | Off | Off | Normal Operation | 26 | 26 | 26 | 30.6 | 51 | 7.1 | 0 | 72.5 | 80.8 | 2.2 | 4.1 | 21 | 179 | 66 | 0.3 | 0.2 | 47.6 | 47.8 | 50.6 | 242 | 176 | 2000 | 29.2 | 45.6 | 550 | 50.1 | Room | On | 28.1 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5316.4111 | 1.9 | 52% | -0.5 | 4100 | 30.6 | 72.5 | 556.2649 | 47.6 | 290.5756 | 265.6894 | 1.2006 | 2.3088 | 4.3099
45618.3536 | On | Off | Off | Off | Off | Normal Operation | 26 | 26 | 26 | 30.6 | 51 | 7.1 | 0 | 72.5 | 80.8 | 2.2 | 4.1 | 20 | 179 | 66 | 0.3 | 0.1 | 47.6 | 47.8 | 50.6 | 241 | 180 | 2000 | 29.1 | 45.6 | 550 | 50.1 | Room | On | 28.1 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5316.4111 | 1.9 | 52% | -0.5 | 4100 | 30.6 | 72.5 | 556.2649 | 47.6 | 290.5756 | 265.6894 | 1.2006 | 2.3088 | 4.3099
45618.3537 | On | Off | Off | Off | Off | Normal Operation | 26 | 25 | 26 | 30.6 | 51 | 7.1 | 0 | 72.5 | 80.8 | 2.1 | 4.1 | 21 | 179 | 66 | 0.2 | 0.1 | 47.6 | 47.8 | 50.6 | 241 | 180 | 2000 | 29.1 | 45.6 | 550 | 50.1 | Room | On | 28.1 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5316.4111 | 1.9 | 52% | -0.5 | 4100 | 30.6 | 72.5 | 556.2649 | 47.6 | 290.5756 | 265.6894 | 1.2006 | 2.3088 | 4.3099
45618.3538 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.7 | 51 | 7.1 | 0 | 72.5 | 80.8 | 2.1 | 4 | 21 | 179 | 66 | 0.1 | 0 | 47.6 | 47.8 | 50.6 | 241 | 180 | 2000 | 29.1 | 45.6 | 550 | 50.1 | Room | On | 28.1 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5316.4111 | 2 | 50% | -0.5 | 4000 | 30.7 | 72.5 | 556.0716 | 47.6 | 290.5896 | 265.4819 | 1.2015 | 2.4031 | 4.3239
45618.3539 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.5 | 51 | 7.1 | 0 | 72.7 | 81 | 2.1 | 4 | 20 | 179 | 66 | 0.1 | 0 | 47.6 | 47.8 | 50.6 | 241 | 180 | 2000 | 29.2 | 45.6 | 550 | 50.2 | Room | On | 28.1 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5316.4111 | 2 | 50% | -0.4 | 4000 | 30.5 | 72.7 | 556.8349 | 47.6 | 290.5615 | 266.2733 | 1.198 | 2.3959 | 4.2958
45618.354 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.5 | 51 | 7.1 | 0 | 72.7 | 81 | 2.1 | 4 | 20 | 179 | 66 | 0.1 | 0 | 47.6 | 47.8 | 50.6 | 240 | 176 | 2000 | 29.2 | 45.6 | 540 | 50.2 | Room | On | 28.3 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5354.2503 | 2 | 50% | -0.4 | 4000 | 30.5 | 72.7 | 556.8349 | 47.6 | 290.5615 | 266.2733 | 1.2065 | 2.413 | 4.2958
45618.3541 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.5 | 51 | 7.1 | 0 | 72.7 | 81 | 2 | 4 | 21 | 179 | 66 | 0.1 | 0 | 47.6 | 47.8 | 50.6 | 240 | 176 | 2000 | 29.6 | 45.6 | 540 | 50.2 | Room | On | 28.3 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5354.2503 | 1.9 | 50% | -0.4 | 4000 | 30.5 | 72.7 | 556.8349 | 47.6 | 290.5615 | 266.2733 | 1.2065 | 2.413 | 4.2958
45618.3543 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.5 | 51 | 7.1 | 0 | 72.7 | 81 | 2 | 4 | 20 | 179 | 66 | 0.1 | 0 | 47.6 | 47.8 | 50.6 | 240 | 176 | 2000 | 29.7 | 45.5 | 550 | 50.2 | Room | On | 28.3 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5354.2503 | 1.9 | 50% | -0.4 | 4000 | 30.5 | 72.7 | 556.8349 | 47.6 | 290.5615 | 266.2733 | 1.2065 | 2.413 | 4.2958
45618.3544 | On | Off | Off | Off | Off | Normal Operation | 25 | 27 | 25 | 30.6 | 51 | 7.1 | 0 | 72.7 | 81 | 2 | 4 | 21 | 179 | 66 | 0.2 | 0.1 | 47.6 | 47.8 | 50.6 | 241 | 176 | 2000 | 29.8 | 45.5 | 550 | 50.2 | Room | On | 28.3 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5354.2503 | 1.8 | 50% | -0.4 | 4000 | 30.6 | 72.7 | 556.6429 | 47.6 | 290.5756 | 266.0673 | 1.2074 | 2.4148 | 4.3099
45618.3545 | On | Off | Off | Off | Off | Normal Operation | 26 | 27 | 25 | 30.6 | 51 | 7.1 | 0 | 72.7 | 81 | 2 | 4 | 21 | 179 | 66 | 0.2 | 0.1 | 47.6 | 47.8 | 50.6 | 241 | 176 | 2000 | 29.8 | 45.5 | 550 | 50.2 | Room | On | 28.3 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5354.2503 | 1.8 | 50% | -0.4 | 4000 | 30.6 | 72.7 | 556.6429 | 47.6 | 290.5756 | 266.0673 | 1.2074 | 2.4148 | 4.3099
45618.3546 | On | Off | Off | Off | Off | Normal Operation | 26 | 27 | 26 | 30.7 | 51 | 7.1 | 0 | 72.7 | 81 | 2 | 4.1 | 21 | 179 | 66 | 0.2 | 0.1 | 47.6 | 47.8 | 50.6 | 241 | 176 | 2000 | 29.8 | 45.5 | 550 | 50.2 | Room | On | 28.3 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5354.2503 | 1.8 | 52% | -0.4 | 4100 | 30.7 | 72.7 | 556.4506 | 47.6 | 290.5896 | 265.861 | 1.2084 | 2.3238 | 4.3239
45618.3547 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.6 | 51 | 7.1 | 0 | 72.7 | 81 | 2 | 4.2 | 20 | 179 | 66 | 0.2 | 0.1 | 47.6 | 47.8 | 50.6 | 242 | 176 | 2000 | 29.5 | 45.5 | 550 | 50.2 | Room | On | 28.3 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5354.2503 | 1.8 | 54% | -0.4 | 4200 | 30.6 | 72.7 | 556.6429 | 47.6 | 290.5756 | 266.0673 | 1.2074 | 2.236 | 4.3099
45618.3548 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.7 | 51 | 7.1 | 0 | 72.8 | 81.1 | 2 | 4.2 | 21 | 179 | 66 | 0.2 | 0.1 | 47.6 | 47.8 | 50.8 | 242 | 176 | 2000 | 29.1 | 45.5 | 550 | 50.2 | Room | On | 28.3 | 47.8 | 50.6 | 49.3 | 1006.4526 | 4027.9921 | 3 | 5736.3864 | 1.8 | 54% | -0.6 | 4200 | 30.7 | 72.8 | 556.6401 | 47.6 | 290.5896 | 266.0505 | 1.2937 | 2.3957 | 4.3239
45618.355 | On | Off | Off | Off | Off | Normal Operation | 27 | 27 | 27 | 30.7 | 51 | 7.1 | 0 | 73 | 81.1 | 2 | 4.2 | 20 | 179 | 66 | 0.2 | 0.1 | 47.6 | 47.8 | 50.8 | 242 | 184 | 2000 | 28.6 | 45.6 | 550 | 50.2 | Room | On | 28.1 | 47.8 | 50.8 | 49.3 | 1006.4526 | 4027.9921 | 3 | 5695.8466 | 1.8 | 54% | -0.6 | 4200 | 30.7 | 73 | 557.0192 | 47.6 | 290.5896 | 266.4295 | 1.2827 | 2.3754 | 4.3239
45618.3551 | On | Off | Off | Off | Off | Normal Operation | 27 | 25 | 27 | 30.8 | 51 | 7.1 | 0 | 73.1 | 81.2 | 2 | 4.2 | 21 | 179 | 66 | 0.2 | 0 | 47.6 | 47.8 | 50.8 | 241 | 184 | 2000 | 28.5 | 45.6 | 540 | 50.2 | Room | On | 28.1 | 47.8 | 50.8 | 49.3 | 1006.4526 | 4027.9921 | 3 | 5695.8466 | 1.8 | 54% | -0.6 | 4200 | 30.8 | 73.1 | 557.0183 | 47.6 | 290.6037 | 266.4146 | 1.2828 | 2.3755 | 4.338
45618.3552 | On | Off | Off | Off | Off | Normal Operation | 26 | 25 | 26 | 30.8 | 51 | 7.1 | 0 | 73.1 | 81.2 | 2 | 4.2 | 21 | 179 | 66 | 0.2 | 0 | 47.7 | 48 | 50.8 | 241 | 184 | 2000 | 28.3 | 45.6 | 550 | 50.2 | Room | On | 28.1 | 47.8 | 50.8 | 49.4 | 1006.3982 | 4027.9921 | 2.8 | 5315.8357 | 1.8 | 52% | -0.6 | 4200 | 30.8 | 73.1 | 557.0183 | 47.7 | 290.8044 | 266.214 | 1.1981 | 2.304 | 4.338
45618.3553 | On | Off | Off | Off | Off | Normal Operation | 26 | 25 | 26 | 30.8 | 51 | 7.1 | 0 | 73.2 | 81.4 | 2 | 4.1 | 21 | 179 | 66 | 0.2 | 0 | 47.7 | 48 | 51 | 241 | 184 | 2000 | 28.3 | 45.8 | 550 | 50.2 | Room | On | 28.1 | 47.8 | 50.8 | 49.5 | 1006.3436 | 4027.9921 | 3 | 5695.2295 | 1.8 | 52% | -0.8 | 4100 | 30.8 | 73.2 | 557.2084 | 47.7 | 290.8044 | 266.404 | 1.2827 | 2.4667 | 4.338
45618.3554 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.7 | 51 | 7.1 | 0 | 73.4 | 81.5 | 2 | 4 | 21 | 179 | 66 | 0.2 | 0.1 | 47.7 | 48 | 51 | 241 | 180 | 2000 | 28.8 | 45.8 | 550 | 50.2 | Room | On | 27.9 | 48 | 51 | 49.5 | 1006.3436 | 4028.4624 | 3 | 5655.3542 | 1.8 | 50% | -0.8 | 4000 | 30.7 | 73.4 | 557.7773 | 47.7 | 290.7902 | 266.987 | 1.2709 | 2.5419 | 4.3239
45618.3555 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.7 | 51 | 7.1 | 0 | 73.4 | 81.5 | 2 | 4 | 21 | 179 | 66 | 0.2 | 0.1 | 47.7 | 48 | 51 | 241 | 180 | 2000 | 28.8 | 45.8 | 550 | 50.2 | Room | On | 27.9 | 48 | 51 | 49.5 | 1006.3436 | 4028.4624 | 3 | 5655.3542 | 1.8 | 50% | -0.8 | 4000 | 30.7 | 73.4 | 557.7773 | 47.7 | 290.7902 | 266.987 | 1.2709 | 2.5419 | 4.3239
45618.3556 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.7 | 51 | 7.1 | 0 | 73.4 | 81.5 | 2 | 4 | 21 | 179 | 66 | 0.2 | 0.1 | 47.7 | 48 | 50.8 | 241 | 180 | 2000 | 29.3 | 45.8 | 550 | 50.2 | Room | On | 27.9 | 48 | 51 | 49.4 | 1006.3982 | 4028.4624 | 2.8 | 5278.6167 | 1.8 | 50% | -0.6 | 4000 | 30.7 | 73.4 | 557.7773 | 47.7 | 290.7902 | 266.987 | 1.1863 | 2.3725 | 4.3239
45618.3558 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.6 | 51 | 7.1 | 0 | 73.2 | 81.7 | 2 | 4 | 21 | 179 | 66 | 0.2 | 0.1 | 47.7 | 48 | 50.8 | 240 | 180 | 2000 | 29.7 | 45.8 | 550 | 50.2 | Room | On | 27.9 | 48 | 51 | 49.4 | 1006.3982 | 4028.4624 | 2.8 | 5278.6167 | 1.8 | 50% | -0.6 | 4000 | 30.6 | 73.2 | 557.5878 | 47.7 | 290.7761 | 266.8117 | 1.187 | 2.3741 | 4.3099
45618.3559 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.7 | 51 | 7.1 | 0 | 73.2 | 81.7 | 2 | 4 | 21 | 179 | 66 | 0.3 | 0.2 | 47.7 | 48 | 50.8 | 240 | 176 | 2000 | 29.8 | 45.6 | 550 | 50.2 | Room | On | 28.3 | 48 | 50.8 | 49.4 | 1006.3982 | 4028.4624 | 2.8 | 5354.2958 | 1.7 | 50% | -0.6 | 4000 | 30.7 | 73.2 | 557.3982 | 47.7 | 290.7902 | 266.608 | 1.205 | 2.41 | 4.3239
45618.356 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.7 | 51 | 7.1 | 0 | 73.1 | 81.5 | 2 | 4 | 21 | 179 | 66 | 0.3 | 0.2 | 47.7 | 48 | 50.8 | 240 | 176 | 2000 | 30 | 45.6 | 550 | 50.2 | Room | On | 28.3 | 48 | 50.8 | 49.4 | 1006.3982 | 4028.4624 | 2.8 | 5354.2958 | 1.7 | 50% | -0.6 | 4000 | 30.7 | 73.1 | 557.2087 | 47.7 | 290.7902 | 266.4185 | 1.2058 | 2.4117 | 4.3239
45618.3561 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.7 | 51 | 7.1 | 0 | 73.1 | 81.5 | 2 | 4 | 21 | 179 | 66 | 0.2 | 0.2 | 47.7 | 48 | 50.8 | 241 | 176 | 2000 | 30 | 45.6 | 550 | 50.2 | Room | On | 28.3 | 48 | 50.8 | 49.4 | 1006.3982 | 4028.4624 | 2.8 | 5354.2958 | 1.8 | 50% | -0.6 | 4000 | 30.7 | 73.1 | 557.2087 | 47.7 | 290.7902 | 266.4185 | 1.2058 | 2.4117 | 4.3239
45618.3562 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.7 | 51 | 7.1 | 0 | 73.1 | 81.5 | 2 | 4 | 20 | 179 | 66 | 0.2 | 0.2 | 47.7 | 48 | 50.8 | 241 | 176 | 2000 | 30 | 45.6 | 550 | 50.2 | Room | On | 28.3 | 48 | 50.8 | 49.4 | 1006.3982 | 4028.4624 | 2.8 | 5354.2958 | 1.8 | 50% | -0.6 | 4000 | 30.7 | 73.1 | 557.2087 | 47.7 | 290.7902 | 266.4185 | 1.2058 | 2.4117 | 4.3239
45618.3563 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.7 | 51 | 7.1 | 0 | 73 | 81.5 | 2 | 4 | 21 | 179 | 66 | 0.2 | 0.2 | 47.7 | 48 | 50.8 | 241 | 176 | 2000 | 29.8 | 45.6 | 550 | 50.2 | Room | On | 28.1 | 48 | 50.8 | 49.4 | 1006.3982 | 4028.4624 | 2.8 | 5316.4563 | 1.8 | 50% | -0.6 | 4000 | 30.7 | 73 | 557.0192 | 47.7 | 290.7902 | 266.2289 | 1.1982 | 2.3963 | 4.3239
45618.3565 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.6 | 51 | 7.1 | 0 | 73 | 81.4 | 2 | 4 | 21 | 179 | 66 | 0.3 | 0.2 | 47.7 | 48 | 50.8 | 240 | 176 | 2000 | 29.8 | 45.6 | 550 | 50.2 | Room | On | 28.1 | 48 | 50.8 | 49.4 | 1006.3982 | 4028.4624 | 2.8 | 5316.4563 | 1.7 | 50% | -0.6 | 4000 | 30.6 | 73 | 557.2098 | 47.7 | 290.7761 | 266.4337 | 1.1972 | 2.3945 | 4.3099
45618.3566 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.7 | 51 | 7.2 | 1 | 73 | 81.4 | 2 | 4 | 21 | 179 | 66 | 0.3 | 0.2 | 47.7 | 48 | 50.8 | 240 | 176 | 2000 | 29.8 | 45.6 | 550 | 50.2 | Room | On | 28.1 | 48 | 50.8 | 49.4 | 1006.3982 | 4028.4624 | 2.8 | 5316.4563 | 1.7 | 50% | -0.6 | 4000 | 30.7 | 73 | 557.0192 | 47.7 | 290.7902 | 266.2289 | 1.1982 | 2.3963 | 4.2639
45618.3567 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.8 | 51 | 7.2 | 1 | 73 | 81.4 | 2.1 | 4 | 21 | 179 | 66 | 0.3 | 0.2 | 47.7 | 48.3 | 50.8 | 240 | 176 | 2000 | 30 | 45.6 | 550 | 50.2 | Room | On | 28.1 | 48 | 50.8 | 49.55 | 1006.3163 | 4028.4624 | 2.5 | 4746.4499 | 1.8 | 50% | -0.6 | 4000 | 30.8 | 73 | 556.8282 | 47.7 | 290.8044 | 266.0239 | 1.0705 | 2.1411 | 4.2778
45618.3568 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.8 | 51 | 7.2 | 1 | 73 | 81.4 | 2.1 | 4 | 21 | 179 | 66 | 0.3 | 0.3 | 47.7 | 48.3 | 50.8 | 241 | 176 | 2000 | 30 | 45.6 | 550 | 50.2 | Room | On | 28.1 | 48.3 | 50.8 | 49.55 | 1006.3163 | 4029.1678 | 2.5 | 4747.281 | 1.8 | 50% | -0.6 | 4000 | 30.8 | 73 | 556.8282 | 47.7 | 290.8044 | 266.0239 | 1.0707 | 2.1414 | 4.2778
45618.3569 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.7 | 51 | 7.2 | 1 | 73 | 81.4 | 2.2 | 4 | 21 | 179 | 66 | 0.3 | 0.3 | 47.7 | 48.3 | 50.8 | 241 | 176 | 2000 | 30 | 45.6 | 550 | 50.2 | Room | On | 28.1 | 48.3 | 50.8 | 49.55 | 1006.3163 | 4029.1678 | 2.5 | 4747.281 | 1.9 | 50% | -0.6 | 4000 | 30.7 | 73 | 557.0192 | 47.7 | 290.7902 | 266.2289 | 1.0699 | 2.1398 | 4.2639
45618.357 | On | Off | Off | Off | Off | Normal Operation | 25 | 25 | 25 | 30.7 | 51 | 7.2 | 1 | 73.1 | 81.4 | 2.2 | 4 | 21 | 179 | 66 | 0.4 | 0.3 | 47.7 | 48.3 | 50.8 | 241 | 176 | 2000 | 30 | 45.6 | 550 | 50.2 | Room | On | 28.1 | 48.3 | 50.8 | 49.55 | 1006.3163 | 4029.1678 | 2.5 | 4747.281 | 1.8 | 50% | -0.6 | 4000 | 30.7 | 73.1 | 557.2087 | 47.7 | 290.7902 | 266.4185 | 1.0691 | 2.1383 | 4.2639
45618.3572 | On | Off | Off | Off | On | Normal Operation | 25 | 24 | 25 | 30.7 | 51 | 7.2 | 1 | 73.1 | 81.2 | 2.2 | 3.5 | 17 | 179 | 66 | 0.4 | 0.3 | 47.7 | 48 | 50.8 | 240 | 0 | 0 | 30 | 45.6 | 550 | 50.2 | Room | On | 28.1 | 48.3 | 50.8 | 49.4 | 1006.3982 | 4029.1678 | 2.8 | 5317.3872 | 1.8 | 50% | -0.6 | 3500 | 30.7 | 73.1 | 557.2087 | 47.7 | 290.7902 | 266.4185 | 1.1975 | 2.3951 | 4.2639
45618.3573 | On | Off | Off | Off | On | Normal Operation | 24 | 24 | 25 | 30.7 | 51 | 7.2 | 1 | 73.1 | 81.2 | 2.2 | 3.5 | 17 | 179 | 66 | 0.4 | 0.3 | 47.7 | 48 | 50.8 | 240 | 0 | 0 | 30 | 45.6 | 550 | 50.1 | Room | On | 27.9 | 48 | 50.8 | 49.4 | 1006.3982 | 4028.4624 | 2.8 | 5278.6167 | 1.8 | 50% | -0.7 | 3500 | 30.7 | 73.1 | 557.2087 | 47.7 | 290.7902 | 266.4185 | 1.1888 | 2.3776 | 4.2639
45618.3574 | On | Off | Off | Off | On | Normal Operation | 24 | 24 | 24 | 30.8 | 51 | 7.2 | 1 | 73.1 | 81.2 | 2.2 | 3.2 | 17 | 179 | 66 | 0.4 | 0.3 | 47.7 | 48 | 50.8 | 240 | 0 | 0 | 28 | 45.3 | 540 | 50.1 | Room | On | 27.9 | 48 | 50.8 | 49.4 | 1006.3982 | 4028.4624 | 2.8 | 5278.6167 | 1.8 | 48% | -0.7 | 3200 | 30.8 | 73.1 | 557.0183 | 47.7 | 290.8044 | 266.214 | 1.1897 | 2.4786 | 4.2778
45618.3575 | On | Off | Off | Off | On | Normal Operation | 24 | 24 | 24 | 30.8 | 51 | 7.2 | 1 | 72.8 | 81.2 | 2.2 | 3.2 | 17 | 179 | 65 | 0.4 | 0.3 | 47.7 | 48 | 50.8 | 240 | 0 | 0 | 26.2 | 45 | 550 | 50.1 | Room | On | 27.9 | 48 | 50.8 | 49.4 | 1006.3982 | 4028.4624 | 2.8 | 5278.6167 | 1.8 | 48% | -0.7 | 3200 | 30.8 | 72.8 | 556.4481 | 47.7 | 290.8044 | 265.6438 | 1.1923 | 2.4839 | 4.2778
45618.3576 | On | Off | Off | Off | On | Normal Operation | 24 | 24 | 24 | 30.8 | 51 | 7.2 | 1 | 72.5 | 81.2 | 2.2 | 3.2 | 17 | 179 | 65 | 0.4 | 0.3 | 47.7 | 48.3 | 50.8 | 240 | 0 | 0 | 24.7 | 44.2 | 550 | 50.1 | Room | On | 27.9 | 48 | 50.8 | 49.55 | 1006.3163 | 4028.4624 | 2.5 | 4712.6673 | 1.8 | 48% | -0.7 | 3200 | 30.8 | 72.5 | 555.8779 | 47.7 | 290.8044 | 265.0736 | 1.0667 | 2.2223 | 4.2778
45618.3577 | On | Off | Off | Off | On | Normal Operation | 24 | 24 | 24 | 30.8 | 51 | 7.2 | 1 | 72.4 | 81.4 | 2.2 | 3.2 | 17 | 179 | 65 | 0.4 | 0.3 | 47.7 | 48 | 50.8 | 240 | 0 | 0 | 23.4 | 43.5 | 550 | 50.1 | Room | On | 27.9 | 48 | 50.8 | 49.4 | 1006.3982 | 4028.4624 | 2.8 | 5278.6167 | 1.8 | 48% | -0.7 | 3200 | 30.8 | 72.4 | 555.6879 | 47.7 | 290.8044 | 264.8835 | 1.1957 | 2.491 | 4.2778
45618.3578 | On | Off | Off | Off | On | Normal Operation | 24 | 23 | 24 | 30.8 | 51 | 7.2 | 1 | 72.2 | 81.4 | 2.2 | 3.2 | 17 | 179 | 65 | 0.4 | 0.3 | 47.7 | 48 | 50.8 | 240 | 0 | 0 | 22.2 | 42.8 | 550 | 50.1 | Room | On | 27.9 | 48 | 50.8 | 49.4 | 1006.3982 | 4028.4624 | 2.8 | 5278.6167 | 1.8 | 48% | -0.7 | 3200 | 30.8 | 72.2 | 555.3077 | 47.7 | 290.8044 | 264.5034 | 1.1974 | 2.4946 | 4.2778
45618.358 | On | Off | Off | Off | On | Normal Operation | 23 | 23 | 23 | 30.8 | 51 | 7.2 | 1 | 72 | 81.4 | 2.2 | 3.2 | 17 | 179 | 64 | 0.4 | 0.3 | 47.7 | 48 | 50.8 | 240 | 0 | 0 | 21.1 | 42.2 | 550 | 50.1 | Room | On | 27.9 | 48 | 50.8 | 49.4 | 1006.3982 | 4028.4624 | 2.8 | 5278.6167 | 1.8 | 46% | -0.7 | 3200 | 30.8 | 72 | 554.9276 | 47.7 | 290.8044 | 264.1232 | 1.1991 | 2.6068 | 4.2778
45618.3581 | On | Off | Off | Off | On | Normal Operation | 23 | 23 | 23 | 30.9 | 51 | 7.2 | 1 | 71.7 | 81.4 | 2.2 | 3.1 | 17 | 179 | 64 | 0.5 | 0.4 | 47.7 | 48.3 | 50.8 | 240 | 0 | 0 | 20.4 | 41.6 | 550 | 50.1 | Room | On | 27.9 | 48 | 50.8 | 49.55 | 1006.3163 | 4028.4624 | 2.5 | 4712.6673 | 1.7 | 46% | -0.7 | 3100 | 30.9 | 71.7 | 554.1591 | 47.7 | 290.8185 | 263.3406 | 1.0737 | 2.3342 | 4.2917
45618.3582 | On | Off | Off | Off | On | Normal Operation | 23 | 23 | 23 | 30.9 | 51 | 7.2 | 1 | 71.4 | 81.2 | 2.2 | 3.1 | 17 | 179 | 64 | 0.5 | 0.4 | 47.7 | 48.3 | 50.8 | 240 | 0 | 0 | 19.9 | 40.8 | 550 | 50.1 | Room | On | 28.1 | 48.3 | 50.8 | 49.55 | 1006.3163 | 4029.1678 | 2.5 | 4747.281 | 1.7 | 46% | -0.7 | 3100 | 30.9 | 71.4 | 553.5873 | 47.7 | 290.8185 | 262.7688 | 1.084 | 2.3565 | 4.2917
45618.3583 | On | Off | Off | Off | On | Normal Operation | 23 | 23 | 23 | 30.9 | 51 | 7.2 | 1 | 71.4 | 81.1 | 2.3 | 3.1 | 17 | 179 | 64 | 0.6 | 0.5 | 47.7 | 48.3 | 50.8 | 240 | 0 | 0 | 19.6 | 40.1 | 550 | 50.1 | Room | On | 28.1 | 48.3 | 50.8 | 49.55 | 1006.3163 | 4029.1678 | 2.5 | 4747.281 | 1.7 | 46% | -0.7 | 3100 | 30.9 | 71.4 | 553.5873 | 47.7 | 290.8185 | 262.7688 | 1.084 | 2.3565 | 4.2917
45618.3584 | On | Off | Off | Off | On | Normal Operation | 23 | 23 | 23 | 30.9 | 51 | 7.2 | 1 | 71.1 | 81 | 2.3 | 3.1 | 17 | 179 | 64 | 0.6 | 0.5 | 47.7 | 48.3 | 50.8 | 240 | 0 | 0 | 19.5 | 39.4 | 550 | 50.1 | Room | On | 28.1 | 48.3 | 50.8 | 49.55 | 1006.3163 | 4029.1678 | 2.5 | 4747.281 | 1.7 | 46% | -0.7 | 3100 | 30.9 | 71.1 | 553.0154 | 47.7 | 290.8185 | 262.1969 | 1.0863 | 2.3616 | 4.2917
45618.3585 | On | Off | Off | Off | On | Normal Operation | 23 | 22 | 23 | 30.8 | 51 | 7.2 | 1 | 71 | 81 | 2.3 | 3.1 | 17 | 179 | 64 | 0.6 | 0.5 | 47.7 | 48.3 | 50.8 | 240 | 0 | 0 | 19.4 | 38.8 | 550 | 50.1 | Room | On | 28.1 | 48.3 | 50.8 | 49.55 | 1006.3163 | 4029.1678 | 2.5 | 4747.281 | 1.7 | 46% | -0.7 | 3100 | 30.8 | 71 | 553.027 | 47.7 | 290.8044 | 262.2226 | 1.0862 | 2.3614 | 4.2778
45618.3587 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.9 | 51 | 7.2 | 1 | 70.8 | 80.7 | 2.4 | 3.1 | 17 | 179 | 64 | 0.6 | 0.5 | 47.7 | 48.3 | 50.8 | 240 | 0 | 0 | 19.4 | 38.1 | 550 | 50.1 | Room | On | 27.9 | 48.3 | 50.8 | 49.55 | 1006.3163 | 4029.1678 | 2.5 | 4713.4925 | 1.8 | 44% | -0.7 | 3100 | 30.9 | 70.8 | 552.4436 | 47.7 | 290.8185 | 261.6251 | 1.081 | 2.4568 | 4.2917
45618.3588 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.8 | 51 | 7.2 | 1 | 70.7 | 80.5 | 2.4 | 3 | 17 | 179 | 64 | 0.6 | 0.5 | 47.7 | 48.3 | 50.8 | 240 | 0 | 0 | 19.5 | 37.5 | 550 | 50.1 | Room | On | 27.9 | 48.3 | 50.8 | 49.55 | 1006.3163 | 4029.1678 | 2.5 | 4713.4925 | 1.8 | 44% | -0.7 | 3000 | 30.8 | 70.7 | 552.4568 | 47.7 | 290.8044 | 261.6524 | 1.0809 | 2.4565 | 4.2778
45618.3589 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.7 | 51 | 7.2 | 1 | 70.4 | 80.4 | 2.4 | 3 | 17 | 179 | 64 | 0.6 | 0.5 | 47.7 | 48.3 | 50.8 | 239 | 0 | 0 | 19.6 | 37 | 550 | 50.1 | Room | On | 27.9 | 48.3 | 50.8 | 49.55 | 1006.3163 | 4029.1678 | 2.5 | 4713.4925 | 1.8 | 44% | -0.7 | 3000 | 30.7 | 70.4 | 552.0917 | 47.7 | 290.7902 | 261.3014 | 1.0823 | 2.4598 | 4.2639
45618.359 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.7 | 51 | 7.2 | 1 | 70.4 | 80.2 | 2.4 | 3 | 17 | 179 | 64 | 0.6 | 0.5 | 47.7 | 48.3 | 50.8 | 239 | 0 | 0 | 19.7 | 36.8 | 550 | 50.1 | Room | On | 27.9 | 48.3 | 50.8 | 49.55 | 1006.3163 | 4029.1678 | 2.5 | 4713.4925 | 1.8 | 44% | -0.7 | 3000 | 30.7 | 70.4 | 552.0917 | 47.7 | 290.7902 | 261.3014 | 1.0823 | 2.4598 | 4.2639
45618.3591 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.8 | 51 | 7.2 | 1 | 70.2 | 80.1 | 2.4 | 3 | 17 | 179 | 64 | 0.6 | 0.5 | 47.7 | 48.3 | 50.8 | 239 | 0 | 0 | 19.8 | 36.2 | 550 | 50 | Room | On | 28.1 | 48.3 | 50.8 | 49.55 | 1006.3163 | 4029.1678 | 2.5 | 4747.281 | 1.8 | 44% | -0.8 | 3000 | 30.8 | 70.2 | 551.5065 | 47.7 | 290.8044 | 260.7021 | 1.0926 | 2.4831 | 4.2778
45618.3592 | On | Off | Off | Off | On | Normal Operation | 22 | 21 | 22 | 30.8 | 51 | 7.2 | 1 | 70.1 | 79.8 | 2.4 | 3 | 17 | 183 | 64 | 0.6 | 0.5 | 47.7 | 48.3 | 50.8 | 238 | 0 | 0 | 20.2 | 35.4 | 550 | 50 | Room | On | 28.1 | 48.3 | 50.8 | 49.55 | 1006.3163 | 4029.1678 | 2.5 | 4747.281 | 1.8 | 44% | -0.8 | 3000 | 30.8 | 70.1 | 551.3164 | 47.7 | 290.8044 | 260.512 | 1.0934 | 2.4849 | 4.2778
45618.3594 | On | Off | Off | Off | On | Normal Operation | 21 | 21 | 22 | 30.8 | 51 | 7.2 | 1 | 70 | 79.8 | 2.4 | 3 | 17 | 183 | 64 | 0.7 | 0.5 | 47.7 | 48.3 | 50.8 | 238 | 0 | 0 | 20.4 | 35.1 | 550 | 50 | Room | On | 28.1 | 48.3 | 50.8 | 49.55 | 1006.3163 | 4029.1678 | 2.5 | 4747.281 | 1.7 | 44% | -0.8 | 3000 | 30.8 | 70 | 551.1263 | 47.7 | 290.8044 | 260.322 | 1.0942 | 2.4868 | 4.2778
45618.3595 | On | Off | Off | Off | On | Normal Operation | 21 | 21 | 21 | 30.7 | 51 | 7.3 | 1 | 69.7 | 79.7 | 2.4 | 2.9 | 17 | 183 | 64 | 0.7 | 0.5 | 47.7 | 48.3 | 50.8 | 238 | 0 | 0 | 20.7 | 34.5 | 550 | 50 | Room | On | 28.1 | 48.3 | 50.8 | 49.55 | 1006.3163 | 4029.1678 | 2.5 | 4747.281 | 1.7 | 42% | -0.8 | 2900 | 30.7 | 69.7 | 550.765 | 47.7 | 290.7902 | 259.9748 | 1.0956 | 2.6086 | 4.2055
45618.3596 | On | Off | Off | Off | On | Normal Operation | 21 | 21 | 21 | 30.7 | 51 | 7.3 | 1 | 69.7 | 79.6 | 2.4 | 2.9 | 17 | 183 | 64 | 0.7 | 0.6 | 47.7 | 48.3 | 50.6 | 237 | 0 | 0 | 21.1 | 34.1 | 550 | 50 | Room | On | 28.1 | 48.3 | 50.6 | 49.45 | 1006.3709 | 4029.1678 | 2.3 | 4367.7354 | 1.7 | 42% | -0.6 | 2900 | 30.7 | 69.7 | 550.765 | 47.7 | 290.7902 | 259.9748 | 1.008 | 2.4001 | 4.2055
45618.3597 | On | Off | Off | Off | On | Normal Operation | 21 | 21 | 21 | 30.7 | 51 | 7.3 | 1 | 69.4 | 79.3 | 2.4 | 2.9 | 17 | 183 | 64 | 0.7 | 0.6 | 47.7 | 48.3 | 50.6 | 237 | 0 | 0 | 21.3 | 33.7 | 550 | 50 | Room | On | 28.1 | 48.3 | 50.6 | 49.45 | 1006.3709 | 4029.1678 | 2.3 | 4367.7354 | 1.7 | 42% | -0.6 | 2900 | 30.7 | 69.4 | 550.1965 | 47.7 | 290.7902 | 259.4062 | 1.0102 | 2.4053 | 4.2055
45618.3598 | On | Off | Off | Off | On | Normal Operation | 21 | 21 | 21 | 30.8 | 51 | 7.3 | 1 | 69.2 | 79.2 | 2.4 | 2.9 | 17 | 183 | 64 | 0.8 | 0.6 | 47.7 | 48.3 | 50.6 | 237 | 0 | 0 | 21.6 | 33.2 | 550 | 50 | Room | On | 28.1 | 48.3 | 50.6 | 49.45 | 1006.3709 | 4029.1678 | 2.3 | 4367.7354 | 1.6 | 42% | -0.6 | 2900 | 30.8 | 69.2 | 549.6058 | 47.7 | 290.8044 | 258.8015 | 1.0126 | 2.411 | 4.2192
45618.3599 | On | Off | Off | Off | On | Normal Operation | 21 | 22 | 21 | 30.7 | 51 | 7.3 | 1 | 69.1 | 79 | 2.4 | 2.9 | 17 | 183 | 64 | 0.8 | 0.6 | 47.7 | 48.3 | 50.6 | 238 | 0 | 0 | 22 | 32.8 | 550 | 50 | Room | On | 28.1 | 48.3 | 50.6 | 49.45 | 1006.3709 | 4029.1678 | 2.3 | 4367.7354 | 1.6 | 42% | -0.6 | 2900 | 30.7 | 69.1 | 549.6279 | 47.7 | 290.7902 | 258.8377 | 1.0125 | 2.4106 | 4.2055
45618.36 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.7 | 51 | 7.3 | 1 | 68.8 | 78.8 | 2.4 | 2.9 | 17 | 183 | 64 | 0.8 | 0.7 | 47.7 | 48.3 | 50.6 | 238 | 0 | 0 | 22.3 | 32.5 | 550 | 50 | Room | On | 27.9 | 48.3 | 50.6 | 49.45 | 1006.3709 | 4029.1678 | 2.3 | 4336.6483 | 1.6 | 44% | -0.6 | 2900 | 30.7 | 68.8 | 549.0594 | 47.7 | 290.7902 | 258.2691 | 1.0075 | 2.2897 | 4.2055
45618.3602 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.8 | 51 | 7.3 | 1 | 68.7 | 78.7 | 2.4 | 3 | 17 | 183 | 64 | 0.8 | 0.7 | 47.6 | 48.3 | 50.6 | 238 | 0 | 0 | 22.5 | 32.1 | 550 | 50 | Room | On | 27.9 | 48.3 | 50.6 | 49.45 | 1006.3709 | 4029.1678 | 2.3 | 4336.6483 | 1.6 | 44% | -0.6 | 3000 | 30.8 | 68.7 | 548.6555 | 47.6 | 290.6037 | 258.0518 | 1.0083 | 2.2916 | 4.2192
45618.3603 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.8 | 51 | 7.3 | 1 | 68.5 | 78.4 | 2.4 | 3 | 17 | 183 | 64 | 0.7 | 0.6 | 47.6 | 48.3 | 50.6 | 237 | 0 | 0 | 22.8 | 31.8 | 550 | 50 | Room | On | 27.9 | 48.3 | 50.6 | 49.45 | 1006.3709 | 4029.1678 | 2.3 | 4336.6483 | 1.7 | 44% | -0.6 | 3000 | 30.8 | 68.5 | 548.2754 | 47.6 | 290.6037 | 257.6717 | 1.0098 | 2.295 | 4.2192
45618.3604 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.8 | 51 | 7.3 | 1 | 68.4 | 78.2 | 2.4 | 3 | 17 | 183 | 64 | 0.7 | 0.6 | 47.6 | 48.3 | 50.6 | 237 | 0 | 0 | 23.1 | 31.4 | 550 | 50 | Room | On | 27.9 | 48.3 | 50.6 | 49.45 | 1006.3709 | 4029.1678 | 2.3 | 4336.6483 | 1.7 | 44% | -0.6 | 3000 | 30.8 | 68.4 | 548.0853 | 47.6 | 290.6037 | 257.4816 | 1.0106 | 2.2967 | 4.2192
45618.3605 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.8 | 51 | 7.3 | 1 | 68.4 | 78.1 | 2.4 | 3 | 17 | 183 | 64 | 0.7 | 0.6 | 47.6 | 48.3 | 50.8 | 237 | 0 | 0 | 23.4 | 31 | 550 | 50 | Room | On | 28.3 | 48.3 | 50.6 | 49.55 | 1006.3163 | 4029.1678 | 2.5 | 4781.0695 | 1.7 | 44% | -0.8 | 3000 | 30.8 | 68.4 | 548.0853 | 47.6 | 290.6037 | 257.4816 | 1.1141 | 2.5321 | 4.2192
45618.3606 | On | Off | Off | Off | On | Normal Operation | 22 | 20 | 22 | 30.8 | 51 | 7.3 | 1 | 68.2 | 78 | 2.4 | 3 | 17 | 183 | 64 | 0.7 | 0.6 | 47.6 | 48.3 | 50.8 | 236 | 0 | 0 | 23.5 | 30.7 | 550 | 50 | Room | On | 28.3 | 48.3 | 50.6 | 49.55 | 1006.3163 | 4029.1678 | 2.5 | 4781.0695 | 1.7 | 44% | -0.8 | 3000 | 30.8 | 68.2 | 547.7052 | 47.6 | 290.6037 | 257.1015 | 1.1158 | 2.5358 | 4.2192
45618.3607 | On | Off | Off | Off | On | Normal Operation | 21 | 20 | 22 | 30.8 | 51 | 7.3 | 1 | 68.2 | 78 | 2.4 | 3 | 17 | 183 | 64 | 0.7 | 0.6 | 47.6 | 48.3 | 50.8 | 236 | 0 | 0 | 23.5 | 30.7 | 550 | 50 | Room | On | 28.3 | 48.3 | 50.6 | 49.55 | 1006.3163 | 4029.1678 | 2.5 | 4781.0695 | 1.7 | 44% | -0.8 | 3000 | 30.8 | 68.2 | 547.7052 | 47.6 | 290.6037 | 257.1015 | 1.1158 | 2.5358 | 4.2192
45618.3609 | On | Off | Off | Off | On | Normal Operation | 21 | 20 | 21 | 30.7 | 51 | 7.3 | 1 | 68.1 | 77.8 | 2.4 | 2.9 | 17 | 180 | 64 | 0.8 | 0.7 | 47.6 | 48.3 | 50.8 | 236 | 0 | 0 | 23.8 | 30.4 | 540 | 50 | Room | On | 28.3 | 48.3 | 50.6 | 49.55 | 1006.3163 | 4029.1678 | 2.5 | 4781.0695 | 1.6 | 42% | -0.8 | 2900 | 30.7 | 68.1 | 547.7327 | 47.6 | 290.5896 | 257.1431 | 1.1156 | 2.6561 | 4.2055
45618.361 | On | Off | Off | Off | On | Normal Operation | 20 | 20 | 20 | 30.7 | 51 | 7.3 | 1 | 68.1 | 77.8 | 2.4 | 2.9 | 17 | 180 | 64 | 0.8 | 0.7 | 47.6 | 48.3 | 50.6 | 235 | 0 | 0 | 24 | 30.3 | 550 | 50 | Room | On | 28.1 | 48.3 | 50.6 | 49.45 | 1006.3709 | 4029.1678 | 2.3 | 4367.7354 | 1.6 | 40% | -0.6 | 2900 | 30.7 | 68.1 | 547.7327 | 47.6 | 290.5896 | 257.1431 | 1.0191 | 2.5478 | 4.2055
45618.3611 | On | Off | Off | Off | On | Normal Operation | 20 | 20 | 20 | 30.7 | 51 | 7.3 | 1 | 68 | 77.7 | 2.4 | 2.8 | 17 | 180 | 64 | 0.8 | 0.8 | 47.6 | 48.3 | 50.6 | 235 | 0 | 0 | 24.2 | 30 | 550 | 50 | Room | On | 28.1 | 48.3 | 50.6 | 49.45 | 1006.3709 | 4029.1678 | 2.3 | 4367.7354 | 1.6 | 40% | -0.6 | 2800 | 30.7 | 68 | 547.5432 | 47.6 | 290.5896 | 256.9536 | 1.0199 | 2.5497 | 4.2055
45618.3612 | On | Off | Off | Off | On | Normal Operation | 20 | 20 | 20 | 30.6 | 51 | 7.3 | 1 | 68 | 77.7 | 2.5 | 2.8 | 17 | 180 | 64 | 0.9 | 0.8 | 47.6 | 48.3 | 50.6 | 235 | 0 | 0 | 24.3 | 29.7 | 550 | 50 | Room | On | 28.1 | 48.3 | 50.6 | 49.45 | 1006.3709 | 4029.1678 | 2.3 | 4367.7354 | 1.6 | 40% | -0.6 | 2800 | 30.6 | 68 | 547.761 | 47.6 | 290.5756 | 257.1854 | 1.019 | 2.5474 | 4.1918
45618.3613 | On | Off | Off | Off | On | Normal Operation | 20 | 22 | 20 | 30.5 | 51 | 7.3 | 1 | 67.8 | 77.5 | 2.5 | 2.8 | 17 | 180 | 64 | 1 | 0.9 | 47.6 | 48 | 50.4 | 234 | 0 | 0 | 24.4 | 29.5 | 550 | 50 | Room | On | 28.1 | 48.3 | 50.6 | 49.2 | 1006.5071 | 4029.1678 | 2.4 | 4558.2538 | 1.5 | 40% | -0.4 | 2800 | 30.5 | 67.8 | 547.6016 | 47.6 | 290.5615 | 257.04 | 1.064 | 2.66 | 4.1781
45618.3614 | On | Off | Off | Off | On | Normal Operation | 21 | 22 | 20 | 30.5 | 51 | 7.4 | 2 | 67.7 | 77.4 | 2.5 | 2.8 | 17 | 180 | 64 | 1 | 0.9 | 47.6 | 48 | 50.4 | 234 | 0 | 0 | 24.6 | 29.3 | 550 | 50 | Room | On | 28.1 | 48 | 50.4 | 49.2 | 1006.5071 | 4028.4624 | 2.4 | 4557.4558 | 1.5 | 40% | -0.4 | 2800 | 30.5 | 67.7 | 547.4131 | 47.6 | 290.5615 | 256.8516 | 1.0646 | 2.6615 | 4.1216
45618.3616 | On | Off | Off | Off | On | Normal Operation | 21 | 22 | 21 | 30.5 | 51 | 7.4 | 2 | 67.5 | 77.2 | 2.5 | 2.9 | 17 | 180 | 64 | 1.1 | 0.9 | 47.6 | 48 | 50.4 | 234 | 0 | 0 | 24.7 | 29.1 | 550 | 50 | Room | On | 28.1 | 48 | 50.4 | 49.2 | 1006.5071 | 4028.4624 | 2.4 | 4557.4558 | 1.4 | 42% | -0.4 | 2900 | 30.5 | 67.5 | 547.0363 | 47.6 | 290.5615 | 256.4747 | 1.0662 | 2.5385 | 4.1216
45618.3617 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.8 | 51 | 7.3 | 1 | 67.4 | 77 | 2.5 | 3 | 17 | 180 | 64 | 1.1 | 1 | 47.6 | 48.3 | 50.4 | 234 | 0 | 0 | 24.8 | 28.8 | 550 | 50 | Room | On | 28.1 | 48 | 50.4 | 49.35 | 1006.4254 | 4028.4624 | 2.1 | 3987.4502 | 1.4 | 44% | -0.4 | 3000 | 30.8 | 67.4 | 546.1847 | 47.6 | 290.6037 | 255.581 | 0.93609 | 2.1275 | 4.2192
45618.3618 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.8 | 51 | 7.3 | 1 | 67.2 | 76.8 | 2.5 | 3 | 17 | 180 | 64 | 1.1 | 1 | 47.6 | 48.3 | 50.6 | 234 | 0 | 0 | 25 | 28.7 | 540 | 50 | Room | On | 28.1 | 48 | 50.4 | 49.45 | 1006.3709 | 4028.4624 | 2.3 | 4366.9707 | 1.4 | 44% | -0.6 | 3000 | 30.8 | 67.2 | 545.8045 | 47.6 | 290.6037 | 255.2008 | 1.0267 | 2.3334 | 4.2192
45618.3619 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.7 | 51 | 7.3 | 1 | 67.1 | 76.8 | 2.5 | 3 | 17 | 180 | 64 | 1 | 0.9 | 47.6 | 48.3 | 50.6 | 234 | 0 | 0 | 25.1 | 28.5 | 550 | 50 | Room | On | 28.3 | 48.3 | 50.6 | 49.45 | 1006.3709 | 4029.1678 | 2.3 | 4398.8225 | 1.5 | 44% | -0.6 | 3000 | 30.7 | 67.1 | 545.8375 | 47.6 | 290.5896 | 255.2479 | 1.034 | 2.35 | 4.2055
45618.362 | On | Off | Off | Off | On | Normal Operation | 22 | 20 | 22 | 30.8 | 51 | 7.3 | 1 | 67.1 | 76.7 | 2.5 | 3 | 17 | 180 | 64 | 1 | 0.9 | 47.6 | 48.3 | 50.6 | 233 | 0 | 0 | 25.2 | 28.3 | 550 | 50 | Room | On | 28.3 | 48.3 | 50.6 | 49.45 | 1006.3709 | 4029.1678 | 2.3 | 4398.8225 | 1.5 | 44% | -0.6 | 3000 | 30.8 | 67.1 | 545.6145 | 47.6 | 290.6037 | 255.0108 | 1.035 | 2.3522 | 4.2192
45618.3621 | On | Off | Off | Off | On | Normal Operation | 21 | 20 | 22 | 30.8 | 51 | 7.3 | 1 | 67 | 76.7 | 2.5 | 3 | 17 | 180 | 64 | 1 | 0.9 | 47.6 | 48.3 | 50.6 | 233 | 0 | 0 | 25.3 | 28.2 | 550 | 50 | Room | On | 28.3 | 48.3 | 50.6 | 49.45 | 1006.3709 | 4029.1678 | 2.3 | 4398.8225 | 1.5 | 44% | -0.6 | 3000 | 30.8 | 67 | 545.4244 | 47.6 | 290.6037 | 254.8207 | 1.0357 | 2.354 | 4.2192
45618.3622 | On | Off | Off | Off | On | Normal Operation | 21 | 20 | 21 | 30.7 | 51 | 7.3 | 1 | 67 | 76.7 | 2.5 | 2.9 | 17 | 180 | 64 | 1 | 0.9 | 47.6 | 48.3 | 50.6 | 233 | 0 | 0 | 25.3 | 28 | 540 | 50 | Room | On | 28.3 | 48.3 | 50.6 | 49.45 | 1006.3709 | 4029.1678 | 2.3 | 4398.8225 | 1.5 | 42% | -0.6 | 2900 | 30.7 | 67 | 545.648 | 47.6 | 290.5896 | 255.0584 | 1.0348 | 2.4638 | 4.2055
45618.3624 | On | Off | Off | Off | On | Normal Operation | 20 | 20 | 20 | 30.6 | 51 | 7.4 | 2 | 67 | 76.5 | 2.5 | 2.8 | 17 | 180 | 64 | 1 | 0.9 | 47.6 | 48.3 | 50.6 | 232 | 0 | 0 | 25.4 | 27.8 | 550 | 50 | Room | On | 28.1 | 48.3 | 50.6 | 49.45 | 1006.3709 | 4029.1678 | 2.3 | 4367.7354 | 1.5 | 40% | -0.6 | 2800 | 30.6 | 67 | 545.8712 | 47.6 | 290.5756 | 255.2957 | 1.0265 | 2.5663 | 4.1351
45618.3625 | On | Off | Off | Off | On | Normal Operation | 20 | 20 | 20 | 30.6 | 51 | 7.4 | 2 | 67 | 76.5 | 2.5 | 2.8 | 17 | 181 | 64 | 1 | 0.9 | 47.6 | 48.3 | 50.6 | 232 | 0 | 0 | 25.4 | 27.8 | 550 | 50 | Room | On | 28.1 | 48.3 | 50.6 | 49.45 | 1006.3709 | 4029.1678 | 2.3 | 4367.7354 | 1.5 | 40% | -0.6 | 2800 | 30.6 | 67 | 545.8712 | 47.6 | 290.5756 | 255.2957 | 1.0265 | 2.5663 | 4.1351
45618.3626 | On | Off | Off | Off | On | Normal Operation | 20 | 20 | 20 | 30.6 | 51 | 7.4 | 2 | 66.8 | 76.5 | 2.5 | 2.8 | 17 | 181 | 64 | 1.1 | 1 | 47.6 | 48.3 | 50.6 | 232 | 0 | 0 | 25.5 | 27.7 | 550 | 50 | Room | On | 28.1 | 48.3 | 50.6 | 49.45 | 1006.3709 | 4029.1678 | 2.3 | 4367.7354 | 1.4 | 40% | -0.6 | 2800 | 30.6 | 66.8 | 545.4933 | 47.6 | 290.5756 | 254.9177 | 1.028 | 2.5701 | 4.1351
45618.3627 | On | Off | Off | Off | On | Normal Operation | 20 | 22 | 20 | 30.5 | 51 | 7.4 | 2 | 66.8 | 76.5 | 2.5 | 2.8 | 17 | 181 | 64 | 1.2 | 1.2 | 47.6 | 48 | 50.4 | 231 | 0 | 0 | 25.5 | 27.6 | 550 | 50 | Room | On | 28.1 | 48.3 | 50.6 | 49.2 | 1006.5071 | 4029.1678 | 2.4 | 4558.2538 | 1.3 | 40% | -0.4 | 2800 | 30.5 | 66.8 | 545.7172 | 47.6 | 290.5615 | 255.1557 | 1.0719 | 2.6797 | 4.1216
45618.3628 | On | Off | Off | Off | On | Normal Operation | 21 | 22 | 20 | 30.5 | 51 | 7.4 | 2 | 66.8 | 76.5 | 2.5 | 2.8 | 17 | 181 | 64 | 1.3 | 1.2 | 47.6 | 48 | 50.4 | 231 | 0 | 0 | 25.6 | 27.5 | 550 | 50 | Room | On | 28.1 | 48.3 | 50.6 | 49.2 | 1006.5071 | 4029.1678 | 2.4 | 4558.2538 | 1.2 | 40% | -0.4 | 2800 | 30.5 | 66.8 | 545.7172 | 47.6 | 290.5615 | 255.1557 | 1.0719 | 2.6797 | 4.1216
45618.3629 | On | Off | Off | Off | On | Normal Operation | 21 | 22 | 21 | 30.6 | 51 | 7.4 | 2 | 66.7 | 76.4 | 2.6 | 2.9 | 17 | 181 | 64 | 1.3 | 1.2 | 47.6 | 48 | 50.4 | 231 | 0 | 0 | 25.6 | 27.3 | 550 | 50 | Room | On | 28.1 | 48 | 50.4 | 49.2 | 1006.5071 | 4028.4624 | 2.4 | 4557.4558 | 1.3 | 42% | -0.4 | 2900 | 30.6 | 66.7 | 545.3043 | 47.6 | 290.5756 | 254.7287 | 1.0735 | 2.5559 | 4.1351
45618.3631 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.7 | 51 | 7.4 | 2 | 66.5 | 76.4 | 2.6 | 2.9 | 17 | 181 | 64 | 1.3 | 1.2 | 47.6 | 48 | 50.4 | 231 | 0 | 0 | 25.7 | 27.2 | 550 | 50 | Room | On | 28.1 | 48 | 50.4 | 49.2 | 1006.5071 | 4028.4624 | 2.4 | 4557.4558 | 1.3 | 44% | -0.4 | 2900 | 30.7 | 66.5 | 544.7004 | 47.6 | 290.5896 | 254.1108 | 1.0761 | 2.4457 | 4.1486
45618.3632 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.7 | 51 | 7.4 | 2 | 66.5 | 76.2 | 2.6 | 3 | 17 | 181 | 64 | 1.2 | 1.2 | 47.6 | 48 | 50.4 | 231 | 0 | 0 | 25.7 | 27.1 | 550 | 50 | Room | On | 28.1 | 48 | 50.4 | 49.2 | 1006.5071 | 4028.4624 | 2.4 | 4557.4558 | 1.4 | 44% | -0.4 | 3000 | 30.7 | 66.5 | 544.7004 | 47.6 | 290.5896 | 254.1108 | 1.0761 | 2.4457 | 4.1486
45618.3633 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.7 | 51 | 7.3 | 1 | 66.4 | 76.2 | 2.6 | 3 | 17 | 181 | 64 | 1.1 | 1.1 | 47.6 | 48 | 50.4 | 231 | 0 | 0 | 25.8 | 27.1 | 550 | 50 | Room | On | 28.1 | 48 | 50.4 | 49.2 | 1006.5071 | 4028.4624 | 2.4 | 4557.4558 | 1.5 | 44% | -0.4 | 3000 | 30.7 | 66.4 | 544.5109 | 47.6 | 290.5896 | 253.9213 | 1.0769 | 2.4475 | 4.2055
45618.3634 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.7 | 51 | 7.3 | 1 | 66.4 | 76.2 | 2.6 | 3 | 17 | 181 | 64 | 1.1 | 1 | 47.6 | 48 | 50.4 | 231 | 0 | 0 | 25.8 | 27 | 550 | 50 | Room | On | 27.9 | 48 | 50.4 | 49.2 | 1006.5071 | 4028.4624 | 2.4 | 4525.0184 | 1.5 | 44% | -0.4 | 3000 | 30.7 | 66.4 | 544.5109 | 47.6 | 290.5896 | 253.9213 | 1.0692 | 2.4301 | 4.2055
45618.3635 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.7 | 51 | 7.3 | 1 | 66.4 | 76.2 | 2.5 | 3 | 17 | 181 | 64 | 1 | 0.9 | 47.6 | 48 | 50.4 | 231 | 0 | 0 | 25.8 | 26.8 | 550 | 50 | Room | On | 27.9 | 48 | 50.4 | 49.2 | 1006.5071 | 4028.4624 | 2.4 | 4525.0184 | 1.5 | 44% | -0.4 | 3000 | 30.7 | 66.4 | 544.5109 | 47.6 | 290.5896 | 253.9213 | 1.0692 | 2.4301 | 4.2055
45618.3636 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.7 | 51 | 7.3 | 1 | 66.4 | 76.2 | 2.5 | 3 | 17 | 181 | 64 | 1 | 1 | 47.6 | 48 | 50.4 | 231 | 0 | 0 | 25.8 | 26.7 | 550 | 50 | Room | On | 27.9 | 48 | 50.4 | 49.2 | 1006.5071 | 4028.4624 | 2.4 | 4525.0184 | 1.5 | 44% | -0.4 | 3000 | 30.7 | 66.4 | 544.5109 | 47.6 | 290.5896 | 253.9213 | 1.0692 | 2.4301 | 4.2055
45618.3638 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.7 | 51 | 7.4 | 2 | 66.4 | 76.4 | 2.5 | 3 | 17 | 181 | 64 | 1 | 1 | 47.6 | 48 | 50.4 | 231 | 0 | 0 | 26 | 26.7 | 550 | 50 | Room | On | 27.9 | 48 | 50.4 | 49.2 | 1006.5071 | 4028.4624 | 2.4 | 4525.0184 | 1.5 | 44% | -0.4 | 3000 | 30.7 | 66.4 | 544.5109 | 47.6 | 290.5896 | 253.9213 | 1.0692 | 2.4301 | 4.1486
45618.3639 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.8 | 51 | 7.4 | 2 | 66.4 | 76.4 | 2.5 | 3 | 17 | 181 | 64 | 1.1 | 1 | 47.6 | 48 | 50.6 | 231 | 0 | 0 | 26 | 26.6 | 550 | 50 | Room | On | 28.3 | 48 | 50.4 | 49.3 | 1006.4526 | 4028.4624 | 2.6 | 4972.1153 | 1.4 | 44% | -0.6 | 3000 | 30.8 | 66.4 | 544.284 | 47.6 | 290.6037 | 253.6803 | 1.176 | 2.6727 | 4.1622
45618.364 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.8 | 51 | 7.4 | 2 | 66.4 | 76.4 | 2.5 | 3 | 17 | 180 | 64 | 1.1 | 1 | 47.6 | 48 | 50.6 | 231 | 0 | 0 | 26 | 26.5 | 550 | 50 | Room | On | 28.3 | 48 | 50.4 | 49.3 | 1006.4526 | 4028.4624 | 2.6 | 4972.1153 | 1.4 | 44% | -0.6 | 3000 | 30.8 | 66.4 | 544.284 | 47.6 | 290.6037 | 253.6803 | 1.176 | 2.6727 | 4.1622
45618.3641 | On | Off | Off | Off | On | Normal Operation | 22 | 20 | 22 | 30.7 | 51 | 7.4 | 2 | 66.4 | 76.5 | 2.5 | 3 | 16 | 180 | 64 | 1.1 | 1 | 47.6 | 48 | 50.6 | 231 | 0 | 0 | 26 | 26.5 | 550 | 50 | Room | On | 28.3 | 48 | 50.4 | 49.3 | 1006.4526 | 4028.4624 | 2.6 | 4972.1153 | 1.4 | 44% | -0.6 | 3000 | 30.7 | 66.4 | 544.5109 | 47.6 | 290.5896 | 253.9213 | 1.1749 | 2.6702 | 4.1486
45618.3642 | On | Off | Off | Off | On | Normal Operation | 22 | 20 | 22 | 30.7 | 51 | 7.4 | 2 | 66.4 | 76.5 | 2.5 | 3 | 16 | 180 | 64 | 1.1 | 1 | 47.6 | 48 | 50.6 | 231 | 0 | 0 | 26 | 26.5 | 550 | 50 | Room | On | 28.3 | 48 | 50.4 | 49.3 | 1006.4526 | 4028.4624 | 2.6 | 4972.1153 | 1.4 | 44% | -0.6 | 3000 | 30.7 | 66.4 | 544.5109 | 47.6 | 290.5896 | 253.9213 | 1.1749 | 2.6702 | 4.1486
45618.3643 | On | Off | Off | Off | On | Normal Operation | 21 | 20 | 21 | 30.7 | 51 | 7.4 | 2 | 66.4 | 76.5 | 2.5 | 3 | 17 | 180 | 64 | 1.1 | 1 | 47.6 | 48 | 50.6 | 231 | 0 | 0 | 26.1 | 26.4 | 550 | 50 | Room | On | 28.5 | 48 | 50.6 | 49.3 | 1006.4526 | 4028.4624 | 2.6 | 5007.254 | 1.4 | 42% | -0.6 | 3000 | 30.7 | 66.4 | 544.5109 | 47.6 | 290.5896 | 253.9213 | 1.1832 | 2.8171 | 4.1486
45618.3644 | On | Off | Off | Off | On | Normal Operation | 20 | 20 | 20 | 30.6 | 51 | 7.4 | 2 | 66.4 | 76.7 | 2.5 | 2.9 | 17 | 180 | 64 | 1.2 | 1.1 | 47.6 | 48 | 50.6 | 231 | 0 | 0 | 26.1 | 26.3 | 550 | 50 | Room | On | 28.5 | 48 | 50.6 | 49.3 | 1006.4526 | 4028.4624 | 2.6 | 5007.254 | 1.3 | 40% | -0.6 | 2900 | 30.6 | 66.4 | 544.7374 | 47.6 | 290.5756 | 254.1618 | 1.1821 | 2.9552 | 4.1351
45618.3646 | On | Off | Off | Off | On | Normal Operation | 20 | 20 | 20 | 30.6 | 51 | 7.4 | 2 | 66.4 | 76.7 | 2.5 | 2.8 | 17 | 180 | 64 | 1.2 | 1.1 | 47.6 | 48 | 50.6 | 231 | 0 | 0 | 26.1 | 26.3 | 550 | 50 | Room | On | 28.5 | 48 | 50.6 | 49.3 | 1006.4526 | 4028.4624 | 2.6 | 5007.254 | 1.3 | 40% | -0.6 | 2800 | 30.6 | 66.4 | 544.7374 | 47.6 | 290.5756 | 254.1618 | 1.1821 | 2.9552 | 4.1351
45618.3647 | On | Off | Off | Off | On | Normal Operation | 20 | 20 | 20 | 30.5 | 51 | 7.4 | 2 | 66.4 | 76.7 | 2.5 | 2.8 | 17 | 180 | 64 | 1.3 | 1.2 | 47.6 | 48 | 50.4 | 231 | 0 | 0 | 26.1 | 26.2 | 550 | 50 | Room | On | 28.5 | 48 | 50.6 | 49.2 | 1006.5071 | 4028.4624 | 2.4 | 4622.3306 | 1.2 | 40% | -0.4 | 2800 | 30.5 | 66.4 | 544.9635 | 47.6 | 290.5615 | 254.402 | 1.0902 | 2.7254 | 4.1216
45618.3648 | On | Off | Off | Off | On | Normal Operation | 20 | 22 | 20 | 30.5 | 51 | 7.4 | 2 | 66.4 | 76.8 | 2.5 | 2.8 | 16 | 180 | 64 | 1.3 | 1.3 | 47.5 | 47.8 | 50.4 | 230 | 0 | 0 | 26.1 | 26.2 | 550 | 50 | Room | On | 27.9 | 48 | 50.4 | 49.1 | 1006.5615 | 4028.4624 | 2.6 | 4902.3681 | 1.2 | 40% | -0.4 | 2800 | 30.5 | 66.4 | 544.9635 | 47.5 | 290.3611 | 254.6024 | 1.1553 | 2.8882 | 4.1216
45618.3649 | On | Off | Off | Off | On | Normal Operation | 21 | 22 | 20 | 30.5 | 51 | 7.4 | 2 | 66.2 | 76.7 | 2.5 | 2.8 | 17 | 180 | 64 | 1.4 | 1.3 | 47.5 | 47.8 | 50.4 | 230 | 0 | 0 | 26.1 | 26.1 | 550 | 50 | Room | On | 27.9 | 48 | 50.4 | 49.1 | 1006.5615 | 4028.4624 | 2.6 | 4902.3681 | 1.1 | 40% | -0.4 | 2800 | 30.5 | 66.2 | 544.5866 | 47.5 | 290.3611 | 254.2255 | 1.157 | 2.8925 | 4.1216
45618.365 | On | Off | Off | Off | On | Normal Operation | 21 | 22 | 21 | 30.5 | 51 | 7.4 | 2 | 66.2 | 76.5 | 2.5 | 2.9 | 17 | 180 | 64 | 1.4 | 1.3 | 47.5 | 47.8 | 50.2 | 230 | 0 | 0 | 26.1 | 26.1 | 550 | 50 | Room | On | 27.9 | 48 | 50.4 | 49 | 1006.6158 | 4028.4624 | 2.4 | 4525.5071 | 1.1 | 42% | -0.2 | 2900 | 30.5 | 66.2 | 544.5866 | 47.5 | 290.3611 | 254.2255 | 1.0681 | 2.543 | 4.1216
45618.3651 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.6 | 51 | 7.4 | 2 | 66 | 76.5 | 2.5 | 3 | 17 | 180 | 64 | 1.4 | 1.3 | 47.5 | 47.8 | 50.2 | 229 | 0 | 0 | 26.1 | 26.1 | 540 | 50 | Room | On | 27.9 | 48 | 50.4 | 49 | 1006.6158 | 4028.4624 | 2.4 | 4525.5071 | 1.1 | 44% | -0.2 | 3000 | 30.6 | 66 | 543.9815 | 47.5 | 290.3751 | 253.6064 | 1.0707 | 2.4334 | 4.1351
45618.3653 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.8 | 51 | 7.4 | 2 | 66 | 76.4 | 2.5 | 3 | 17 | 180 | 64 | 1.3 | 1.2 | 47.5 | 48 | 50.4 | 229 | 0 | 0 | 26.1 | 26.1 | 550 | 50 | Room | On | 28.1 | 47.8 | 50.2 | 49.2 | 1006.5071 | 4027.9921 | 2.4 | 4556.9238 | 1.2 | 44% | -0.4 | 3000 | 30.8 | 66 | 543.5238 | 47.5 | 290.403 | 253.1207 | 1.0802 | 2.4549 | 4.1622
45618.3654 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.7 | 51 | 7.4 | 2 | 66 | 76.4 | 2.5 | 3 | 17 | 180 | 64 | 1.2 | 1.1 | 47.5 | 48 | 50.6 | 229 | 0 | 0 | 26.1 | 26 | 550 | 50 | Room | On | 28.1 | 47.8 | 50.2 | 49.3 | 1006.4526 | 4027.9921 | 2.6 | 4936.4004 | 1.3 | 44% | -0.6 | 3000 | 30.7 | 66 | 543.7528 | 47.5 | 290.389 | 253.3638 | 1.169 | 2.6568 | 4.1486
45618.3655 | On | Off | Off | Off | On | Normal Operation | 22 | 20 | 22 | 30.5 | 51 | 7.4 | 2 | 66 | 76.4 | 2.5 | 3 | 17 | 180 | 64 | 1.2 | 1.1 | 47.5 | 47.8 | 50.6 | 229 | 0 | 0 | 26.1 | 26 | 550 | 50 | Room | On | 28.1 | 47.8 | 50.2 | 49.2 | 1006.5071 | 4027.9921 | 2.8 | 5316.4111 | 1.3 | 44% | -0.6 | 3000 | 30.5 | 66 | 544.2098 | 47.5 | 290.3611 | 253.8487 | 1.2566 | 2.8559 | 4.1216
45618.3656 | On | Off | Off | Off | On | Normal Operation | 21 | 20 | 22 | 30.5 | 51 | 7.4 | 2 | 66 | 76.4 | 2.5 | 3 | 16 | 182 | 64 | 1.1 | 1.1 | 47.5 | 47.8 | 50.4 | 229 | 0 | 0 | 26.1 | 26 | 540 | 50 | Room | On | 28.1 | 47.8 | 50.2 | 49.1 | 1006.5615 | 4027.9921 | 2.6 | 4936.9342 | 1.4 | 44% | -0.4 | 3000 | 30.5 | 66 | 544.2098 | 47.5 | 290.3611 | 253.8487 | 1.1669 | 2.652 | 4.1216
45618.3657 | On | Off | Off | Off | On | Normal Operation | 21 | 20 | 21 | 30.5 | 51 | 7.4 | 2 | 65.8 | 76.4 | 2.6 | 2.9 | 17 | 182 | 63 | 1.1 | 1.1 | 47.5 | 47.8 | 50.4 | 229 | 0 | 0 | 26.1 | 26 | 550 | 50 | Room | On | 28.3 | 47.8 | 50.4 | 49.1 | 1006.5615 | 4027.9921 | 2.6 | 4972.0725 | 1.5 | 42% | -0.4 | 2900 | 30.5 | 65.8 | 543.8329 | 47.5 | 290.3611 | 253.4718 | 1.177 | 2.8023 | 4.1216
45618.3658 | On | Off | Off | Off | On | Normal Operation | 20 | 20 | 20 | 30.5 | 51 | 7.4 | 2 | 65.8 | 76.4 | 2.6 | 2.8 | 17 | 182 | 63 | 1.2 | 1.2 | 47.5 | 47.8 | 50.4 | 228 | 0 | 0 | 26.1 | 26 | 550 | 50 | Room | On | 28.3 | 47.8 | 50.4 | 49.1 | 1006.5615 | 4027.9921 | 2.6 | 4972.0725 | 1.4 | 40% | -0.4 | 2800 | 30.5 | 65.8 | 543.8329 | 47.5 | 290.3611 | 253.4718 | 1.177 | 2.9424 | 4.1216
45618.366 | On | Off | Off | Off | On | Normal Operation | 20 | 20 | 20 | 30.5 | 51 | 7.4 | 2 | 65.8 | 76.4 | 2.6 | 2.8 | 17 | 182 | 63 | 1.2 | 1.2 | 47.5 | 47.8 | 50.4 | 228 | 0 | 0 | 26.1 | 25.8 | 540 | 50 | Room | On | 28.3 | 47.8 | 50.4 | 49.1 | 1006.5615 | 4027.9921 | 2.6 | 4972.0725 | 1.4 | 40% | -0.4 | 2800 | 30.5 | 65.8 | 543.8329 | 47.5 | 290.3611 | 253.4718 | 1.177 | 2.9424 | 4.1216
45618.3661 | On | Off | Off | Off | On | Normal Operation | 20 | 20 | 20 | 30.6 | 51 | 7.5 | 2 | 65.8 | 76.4 | 2.6 | 2.8 | 17 | 182 | 63 | 1.3 | 1.2 | 47.5 | 48 | 50.4 | 228 | 0 | 0 | 26.1 | 25.8 | 550 | 50 | Room | On | 28.3 | 47.8 | 50.4 | 49.2 | 1006.5071 | 4027.9921 | 2.4 | 4589.3574 | 1.3 | 40% | -0.4 | 2800 | 30.6 | 65.8 | 543.6035 | 47.5 | 290.3751 | 253.2285 | 1.0874 | 2.7185 | 4.08
45618.3662 | On | Off | Off | Off | On | Normal Operation | 20 | 22 | 20 | 30.5 | 51 | 7.5 | 2 | 65.8 | 76.4 | 2.6 | 2.8 | 17 | 182 | 64 | 1.4 | 1.4 | 47.5 | 48 | 50.4 | 227 | 0 | 0 | 26.2 | 25.8 | 550 | 50 | Room | On | 28.1 | 48 | 50.4 | 49.2 | 1006.5071 | 4028.4624 | 2.4 | 4557.4558 | 1.2 | 40% | -0.4 | 2800 | 30.5 | 65.8 | 543.8329 | 47.5 | 290.3611 | 253.4718 | 1.0788 | 2.697 | 4.0667
45618.3663 | On | Off | Off | Off | On | Normal Operation | 20 | 22 | 20 | 30.4 | 51 | 7.5 | 2 | 65.8 | 76.4 | 2.6 | 2.8 | 17 | 182 | 64 | 1.5 | 1.4 | 47.5 | 47.8 | 50.4 | 227 | 0 | 0 | 26.2 | 25.7 | 550 | 50 | Room | On | 28.1 | 48 | 50.4 | 49.1 | 1006.5615 | 4028.4624 | 2.6 | 4937.5105 | 1.1 | 40% | -0.4 | 2800 | 30.4 | 65.8 | 544.0619 | 47.5 | 290.3471 | 253.7147 | 1.1677 | 2.9191 | 4.0533
45618.3664 | On | Off | Off | Off | On | Normal Operation | 21 | 22 | 21 | 30.5 | 51 | 7.5 | 2 | 65.7 | 76.2 | 2.6 | 2.9 | 16 | 182 | 63 | 1.6 | 1.5 | 47.5 | 47.8 | 50.2 | 227 | 0 | 0 | 26.2 | 25.7 | 550 | 50 | Room | On | 28.1 | 48 | 50.4 | 49 | 1006.6158 | 4028.4624 | 2.4 | 4557.948 | 1 | 42% | -0.2 | 2900 | 30.5 | 65.7 | 543.6445 | 47.5 | 290.3611 | 253.2834 | 1.0797 | 2.5708 | 4.0667
45618.3665 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.6 | 51 | 7.5 | 2 | 65.7 | 76.2 | 2.7 | 2.9 | 17 | 182 | 63 | 1.6 | 1.5 | 47.5 | 47.8 | 50.2 | 227 | 0 | 0 | 26.2 | 25.7 | 550 | 50 | Room | On | 28.1 | 48 | 50.4 | 49 | 1006.6158 | 4028.4624 | 2.4 | 4557.948 | 1.1 | 44% | -0.2 | 2900 | 30.6 | 65.7 | 543.4146 | 47.5 | 290.3751 | 253.0395 | 1.0808 | 2.4563 | 4.08
45618.3666 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.6 | 51 | 7.4 | 2 | 65.7 | 76.2 | 2.7 | 3 | 17 | 182 | 63 | 1.6 | 1.5 | 47.5 | 47.8 | 50.2 | 227 | 0 | 0 | 26.2 | 25.7 | 550 | 49.9 | Room | On | 28.1 | 47.8 | 50.2 | 49 | 1006.6158 | 4027.9921 | 2.4 | 4557.416 | 1.1 | 44% | -0.3 | 3000 | 30.6 | 65.7 | 543.4146 | 47.5 | 290.3751 | 253.0395 | 1.0806 | 2.456 | 4.1351
45618.3668 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.5 | 51 | 7.4 | 2 | 65.5 | 76.1 | 2.7 | 3 | 16 | 182 | 63 | 1.5 | 1.4 | 47.5 | 47.8 | 50.2 | 227 | 0 | 0 | 26.2 | 25.7 | 550 | 49.9 | Room | On | 28.1 | 47.8 | 50.2 | 49 | 1006.6158 | 4027.9921 | 2.4 | 4557.416 | 1.2 | 44% | -0.3 | 3000 | 30.5 | 65.5 | 543.2676 | 47.5 | 290.3611 | 252.9065 | 1.0812 | 2.4573 | 4.1216
45618.3669 | On | Off | Off | Off | On | Normal Operation | 22 | 21 | 22 | 30.7 | 51 | 7.4 | 2 | 65.5 | 76.1 | 2.8 | 3 | 17 | 182 | 63 | 1.4 | 1.3 | 47.5 | 47.8 | 50.4 | 227 | 0 | 0 | 26.2 | 25.7 | 540 | 49.9 | Room | On | 28.1 | 47.8 | 50.2 | 49.1 | 1006.5615 | 4027.9921 | 2.6 | 4936.9342 | 1.4 | 44% | -0.5 | 3000 | 30.7 | 65.5 | 542.8052 | 47.5 | 290.389 | 252.4162 | 1.1735 | 2.6671 | 4.1486
45618.367 | On | Off | Off | Off | On | Normal Operation | 21 | 21 | 22 | 30.6 | 51 | 7.4 | 2 | 65.5 | 76.1 | 2.8 | 3 | 17 | 182 | 63 | 1.4 | 1.3 | 47.5 | 47.8 | 50.4 | 227 | 0 | 0 | 26.2 | 25.6 | 550 | 49.9 | Room | On | 28.1 | 47.8 | 50.2 | 49.1 | 1006.5615 | 4027.9921 | 2.6 | 4936.9342 | 1.4 | 44% | -0.5 | 3000 | 30.6 | 65.5 | 543.0366 | 47.5 | 290.3751 | 252.6615 | 1.1724 | 2.6645 | 4.1351
45618.3671 | On | Off | Off | Off | On | Normal Operation | 21 | 21 | 21 | 30.5 | 51 | 7.4 | 2 | 65.5 | 76.1 | 2.8 | 2.9 | 17 | 181 | 63 | 1.4 | 1.3 | 47.5 | 47.8 | 50.4 | 227 | 0 | 0 | 26.2 | 25.6 | 550 | 49.9 | Room | On | 28.1 | 47.8 | 50.4 | 49.1 | 1006.5615 | 4027.9921 | 2.6 | 4936.9342 | 1.4 | 42% | -0.5 | 2900 | 30.5 | 65.5 | 543.2676 | 47.5 | 290.3611 | 252.9065 | 1.1712 | 2.7887 | 4.1216
45618.3672 | On | Off | Off | Off | On | Normal Operation | 21 | 21 | 21 | 30.4 | 51 | 7.4 | 2 | 65.5 | 76.1 | 2.8 | 2.9 | 17 | 181 | 63 | 1.3 | 1.3 | 47.5 | 47.8 | 50.4 | 226 | 0 | 0 | 26.2 | 25.6 | 550 | 49.9 | Room | On | 28.1 | 47.8 | 50.4 | 49.1 | 1006.5615 | 4027.9921 | 2.6 | 4936.9342 | 1.5 | 42% | -0.5 | 2900 | 30.4 | 65.5 | 543.4982 | 47.5 | 290.3471 | 253.1511 | 1.1701 | 2.786 | 4.1081
45618.3673 | On | Off | Off | Off | On | Normal Operation | 21 | 21 | 21 | 30.3 | 51 | 7.4 | 2 | 65.5 | 76.1 | 2.8 | 2.9 | 16 | 181 | 63 | 1.3 | 1.3 | 47.5 | 47.7 | 50.2 | 226 | 0 | 0 | 26.2 | 25.6 | 550 | 49.9 | Room | On | 28.1 | 47.8 | 50.4 | 48.95 | 1006.6429 | 4027.9921 | 2.5 | 4747.4363 | 1.5 | 42% | -0.3 | 2900 | 30.3 | 65.5 | 543.7284 | 47.5 | 290.3332 | 253.3952 | 1.1241 | 2.6765 | 4.0946
45618.3675 | On | Off | Off | Off | On | Normal Operation | 21 | 21 | 21 | 30.4 | 51 | 7.4 | 2 | 65.4 | 76.2 | 2.8 | 2.9 | 17 | 181 | 63 | 1.3 | 1.3 | 47.3 | 47.7 | 50.2 | 226 | 0 | 0 | 26.2 | 25.6 | 550 | 49.9 | Room | On | 28.1 | 47.8 | 50.4 | 48.95 | 1006.6429 | 4027.9921 | 2.5 | 4747.4363 | 1.5 | 42% | -0.3 | 2900 | 30.4 | 65.4 | 543.3103 | 47.3 | 289.9464 | 253.3639 | 1.1243 | 2.6768 | 4.1081
45618.3676 | On | Off | Off | Off | On | Normal Operation | 21 | 23 | 21 | 30.4 | 51 | 7.4 | 2 | 65.4 | 76.2 | 2.8 | 2.9 | 17 | 181 | 63 | 1.3 | 1.3 | 47.3 | 47.7 | 50.2 | 225 | 0 | 0 | 26.2 | 25.6 | 550 | 49.9 | Room | On | 28.3 | 47.7 | 50.2 | 48.95 | 1006.6429 | 4027.757 | 2.5 | 4780.9468 | 1.5 | 42% | -0.3 | 2900 | 30.4 | 65.4 | 543.3103 | 47.3 | 289.9464 | 253.3639 | 1.1322 | 2.6957 | 4.1081
45618.3677 | On | Off | Off | Off | On | Normal Operation | 22 | 23 | 21 | 30.4 | 51 | 7.4 | 2 | 65.4 | 76.2 | 2.7 | 2.9 | 17 | 181 | 63 | 1.3 | 1.3 | 47.3 | 47.7 | 50.2 | 225 | 0 | 0 | 26.2 | 25.6 | 550 | 49.9 | Room | On | 28.3 | 47.7 | 50.2 | 48.95 | 1006.6429 | 4027.757 | 2.5 | 4780.9468 | 1.4 | 42% | -0.3 | 2900 | 30.4 | 65.4 | 543.3103 | 47.3 | 289.9464 | 253.3639 | 1.1322 | 2.6957 | 4.1081
45618.3678 | On | Off | Off | Off | On | Normal Operation | 22 | 23 | 22 | 30.5 | 51 | 7.4 | 2 | 65.4 | 76.2 | 2.7 | 3 | 17 | 181 | 63 | 1.3 | 1.3 | 47.3 | 47.7 | 50.2 | 225 | 0 | 0 | 26.2 | 25.6 | 550 | 49.9 | Room | On | 28.3 | 47.7 | 50.2 | 48.95 | 1006.6429 | 4027.757 | 2.5 | 4780.9468 | 1.4 | 44% | -0.3 | 3000 | 30.5 | 65.4 | 543.0792 | 47.3 | 289.9602 | 253.1189 | 1.1333 | 2.5757 | 4.1216
45618.3679 | On | Off | Off | Off | On | Normal Operation | 23 | 23 | 23 | 30.6 | 51 | 7.4 | 2 | 65.4 | 76.2 | 2.7 | 3 | 17 | 181 | 63 | 1.3 | 1.3 | 47.3 | 47.8 | 50.2 | 225 | 0 | 0 | 26.1 | 25.6 | 550 | 49.9 | Room | On | 28.3 | 47.7 | 50.2 | 49 | 1006.6158 | 4027.757 | 2.4 | 4589.5852 | 1.4 | 46% | -0.3 | 3000 | 30.6 | 65.4 | 542.8476 | 47.3 | 289.974 | 252.8736 | 1.089 | 2.3674 | 4.1351
45618.368 | On | Off | Off | Off | On | Normal Operation | 23 | 23 | 23 | 30.6 | 51 | 7.4 | 2 | 65.4 | 76.2 | 2.7 | 3.1 | 17 | 181 | 63 | 1.3 | 1.3 | 47.3 | 47.8 | 50.4 | 225 | 0 | 0 | 26.1 | 25.5 | 550 | 49.9 | Room | On | 28.1 | 47.8 | 50.4 | 49.1 | 1006.5615 | 4027.9921 | 2.6 | 4936.9342 | 1.4 | 46% | -0.5 | 3100 | 30.6 | 65.4 | 542.8476 | 47.3 | 289.974 | 252.8736 | 1.1714 | 2.5465 | 4.1351
45618.3682 | On | Off | Off | Off | On | Normal Operation | 23 | 23 | 23 | 30.6 | 51 | 7.4 | 2 | 65.4 | 76.2 | 2.7 | 3.1 | 17 | 181 | 63 | 1.3 | 1.3 | 47.3 | 47.8 | 50.4 | 225 | 0 | 0 | 26.1 | 25.5 | 550 | 49.9 | Room | On | 28.1 | 47.8 | 50.4 | 49.1 | 1006.5615 | 4027.9921 | 2.6 | 4936.9342 | 1.4 | 46% | -0.5 | 3100 | 30.6 | 65.4 | 542.8476 | 47.3 | 289.974 | 252.8736 | 1.1714 | 2.5465 | 4.1351
45618.3683 | On | Off | Off | Off | On | Normal Operation | 23 | 20 | 23 | 30.6 | 51 | 7.4 | 2 | 65.4 | 76.2 | 2.7 | 3.1 | 16 | 181 | 63 | 1.3 | 1.2 | 47.3 | 47.8 | 50.4 | 225 | 0 | 0 | 26.1 | 25.5 | 550 | 49.9 | Room | On | 28.1 | 47.8 | 50.4 | 49.1 | 1006.5615 | 4027.9921 | 2.6 | 4936.9342 | 1.4 | 46% | -0.5 | 3100 | 30.6 | 65.4 | 542.8476 | 47.3 | 289.974 | 252.8736 | 1.1714 | 2.5465 | 4.1351
45618.3684 | On | Off | Off | Off | On | Normal Operation | 22 | 20 | 23 | 30.5 | 51 | 7.4 | 2 | 65.4 | 76.2 | 2.7 | 3.1 | 17 | 181 | 63 | 1.3 | 1.2 | 47.3 | 47.8 | 50.4 | 225 | 0 | 0 | 26.1 | 25.5 | 550 | 49.9 | Room | On | 28.1 | 47.8 | 50.4 | 49.1 | 1006.5615 | 4027.9921 | 2.6 | 4936.9342 | 1.4 | 46% | -0.5 | 3100 | 30.5 | 65.4 | 543.0792 | 47.3 | 289.9602 | 253.1189 | 1.1703 | 2.5441 | 4.1216
45618.3685 | On | Off | Off | Off | On | Normal Operation | 22 | 20 | 22 | 30.5 | 51 | 7.4 | 2 | 65.4 | 76.4 | 2.7 | 3 | 17 | 181 | 63 | 1.3 | 1.2 | 47.3 | 47.7 | 50.4 | 225 | 0 | 0 | 26.1 | 25.5 | 550 | 49.9 | Room | On | 28.3 | 47.7 | 50.4 | 49.05 | 1006.5886 | 4027.757 | 2.7 | 5163.144 | 1.4 | 44% | -0.5 | 3000 | 30.5 | 65.4 | 543.0792 | 47.3 | 289.9602 | 253.1189 | 1.2239 | 2.7816 | 4.1216
45618.3686 | On | Off | Off | Off | On | Normal Operation | 21 | 20 | 21 | 30.5 | 51 | 7.4 | 2 | 65.5 | 76.4 | 2.7 | 2.9 | 16 | 181 | 63 | 1.2 | 1.1 | 47.3 | 47.7 | 50.4 | 224 | 0 | 0 | 26.1 | 25.5 | 550 | 49.9 | Room | On | 28.3 | 47.7 | 50.4 | 49.05 | 1006.5886 | 4027.757 | 2.7 | 5163.144 | 1.5 | 42% | -0.5 | 2900 | 30.5 | 65.5 | 543.2676 | 47.3 | 289.9602 | 253.3074 | 1.223 | 2.9118 | 4.1216
45618.3687 | On | Off | Off | Off | On | Normal Operation | 20 | 20 | 21 | 30.4 | 51 | 7.4 | 2 | 65.5 | 76.5 | 2.7 | 2.9 | 16 | 182 | 63 | 1.2 | 1.1 | 47.3 | 47.7 | 50.2 | 224 | 0 | 0 | 26.1 | 25.5 | 550 | 49.9 | Room | On | 28.3 | 47.7 | 50.4 | 48.95 | 1006.6429 | 4027.757 | 2.5 | 4780.9468 | 1.5 | 42% | -0.3 | 2900 | 30.4 | 65.5 | 543.4982 | 47.3 | 289.9464 | 253.5518 | 1.1314 | 2.6937 | 4.1081
45618.3688 | On | Off | Off | Off | On | Normal Operation | 20 | 20 | 20 | 30.4 | 51 | 7.5 | 2 | 65.5 | 76.5 | 2.7 | 2.8 | 16 | 182 | 63 | 1.3 | 1.2 | 47.3 | 47.7 | 50.2 | 224 | 0 | 0 | 26.1 | 25.5 | 550 | 49.9 | Room | On | 28.3 | 47.7 | 50.4 | 48.95 | 1006.6429 | 4027.757 | 2.5 | 4780.9468 | 1.4 | 40% | -0.3 | 2800 | 30.4 | 65.5 | 543.4982 | 47.3 | 289.9464 | 253.5518 | 1.1314 | 2.8284 | 4.0533
45618.369 | On | Off | Off | Off | On | Normal Operation | 20 | 22 | 20 | 30.4 | 51 | 7.5 | 2 | 65.5 | 76.5 | 2.7 | 2.8 | 17 | 182 | 63 | 1.3 | 1.3 | 47.3 | 47.7 | 50.2 | 223 | 0 | 0 | 26.1 | 25.5 | 550 | 49.9 | Room | On | 27.9 | 47.7 | 50.2 | 48.95 | 1006.6429 | 4027.757 | 2.5 | 4713.3716 | 1.4 | 40% | -0.3 | 2800 | 30.4 | 65.5 | 543.4982 | 47.3 | 289.9464 | 253.5518 | 1.1154 | 2.7884 | 4.0533
45618.3691 | On | Off | Off | Off | On | Normal Operation | 20 | 22 | 20 | 30.3 | 51 | 7.5 | 2 | 65.4 | 76.5 | 2.7 | 2.8 | 16 | 182 | 63 | 1.4 | 1.4 | 47.3 | 47.7 | 50.2 | 223 | 0 | 0 | 26.1 | 25.5 | 550 | 49.9 | Room | On | 27.9 | 47.7 | 50.2 | 48.95 | 1006.6429 | 4027.757 | 2.5 | 4713.3716 | 1.3 | 40% | -0.3 | 2800 | 30.3 | 65.4 | 543.541 | 47.3 | 289.9326 | 253.6085 | 1.1151 | 2.7878 | 4.04
45618.3692 | On | Off | Off | Off | On | Normal Operation | 21 | 22 | 21 | 30.4 | 51 | 7.5 | 2 | 65.4 | 76.5 | 2.7 | 2.9 | 16 | 182 | 63 | 1.5 | 1.5 | 47.3 | 47.7 | 50.2 | 223 | 0 | 0 | 26 | 25.5 | 550 | 49.9 | Room | On | 27.9 | 47.7 | 50.2 | 48.95 | 1006.6429 | 4027.757 | 2.5 | 4713.3716 | 1.2 | 42% | -0.3 | 2900 | 30.4 | 65.4 | 543.3103 | 47.3 | 289.9464 | 253.3639 | 1.1162 | 2.6576 | 4.0533
45618.3693 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.4 | 51 | 7.5 | 2 | 65.4 | 76.5 | 2.7 | 2.9 | 16 | 182 | 63 | 1.5 | 1.5 | 47.3 | 47.7 | 50.2 | 222 | 0 | 0 | 26 | 25.5 | 550 | 49.9 | Room | On | 27.9 | 47.7 | 50.2 | 48.95 | 1006.6429 | 4027.757 | 2.5 | 4713.3716 | 1.2 | 44% | -0.3 | 2900 | 30.4 | 65.4 | 543.3103 | 47.3 | 289.9464 | 253.3639 | 1.1162 | 2.5368 | 4.0533
45618.3694 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.5 | 51 | 7.5 | 2 | 65.4 | 76.4 | 2.8 | 3 | 16 | 182 | 63 | 1.6 | 1.5 | 47.3 | 47.7 | 50.2 | 222 | 0 | 0 | 26 | 25.4 | 550 | 49.9 | Room | On | 28.1 | 47.7 | 50.2 | 48.95 | 1006.6429 | 4027.757 | 2.5 | 4747.1592 | 1.2 | 44% | -0.3 | 3000 | 30.5 | 65.4 | 543.0792 | 47.3 | 289.9602 | 253.1189 | 1.1253 | 2.5575 | 4.0667
45618.3695 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.5 | 51 | 7.4 | 2 | 65.2 | 76.4 | 2.8 | 3 | 16 | 182 | 63 | 1.5 | 1.4 | 47.3 | 47.7 | 50.2 | 222 | 0 | 0 | 26 | 25.4 | 550 | 49.9 | Room | On | 28.1 | 47.7 | 50.2 | 48.95 | 1006.6429 | 4027.757 | 2.5 | 4747.1592 | 1.3 | 44% | -0.3 | 3000 | 30.5 | 65.2 | 542.7023 | 47.3 | 289.9602 | 252.7421 | 1.127 | 2.5613 | 4.1216
45618.3697 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.5 | 51 | 7.4 | 2 | 65.2 | 76.4 | 2.8 | 3 | 17 | 182 | 63 | 1.4 | 1.4 | 47.3 | 47.7 | 50.2 | 223 | 0 | 0 | 26 | 25.4 | 550 | 49.9 | Room | On | 28.1 | 47.7 | 50.2 | 48.95 | 1006.6429 | 4027.757 | 2.5 | 4747.1592 | 1.4 | 44% | -0.3 | 3000 | 30.5 | 65.2 | 542.7023 | 47.3 | 289.9602 | 252.7421 | 1.127 | 2.5613 | 4.1216
45618.3698 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.4 | 51 | 7.4 | 2 | 65.2 | 76.2 | 2.8 | 3 | 17 | 182 | 63 | 1.4 | 1.3 | 47.3 | 47.7 | 50.2 | 223 | 0 | 0 | 26 | 25.4 | 550 | 49.9 | Room | On | 28.1 | 47.7 | 50.2 | 48.95 | 1006.6429 | 4027.757 | 2.5 | 4747.1592 | 1.4 | 44% | -0.3 | 3000 | 30.4 | 65.2 | 542.9345 | 47.3 | 289.9464 | 252.9881 | 1.1259 | 2.5588 | 4.1081
45618.3699 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.4 | 51 | 7.4 | 2 | 65.2 | 76.2 | 2.8 | 3 | 16 | 182 | 63 | 1.4 | 1.3 | 47.3 | 47.7 | 50.2 | 223 | 0 | 0 | 26 | 25.4 | 550 | 49.9 | Room | On | 28.1 | 47.7 | 50.2 | 48.95 | 1006.6429 | 4027.757 | 2.5 | 4747.1592 | 1.4 | 44% | -0.3 | 3000 | 30.4 | 65.2 | 542.9345 | 47.3 | 289.9464 | 252.9881 | 1.1259 | 2.5588 | 4.1081
45618.37 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.4 | 51 | 7.5 | 2 | 65.2 | 76.2 | 2.8 | 3 | 17 | 182 | 63 | 1.4 | 1.3 | 47.3 | 47.7 | 50.2 | 222 | 0 | 0 | 26 | 25.4 | 550 | 49.9 | Room | On | 28.1 | 47.7 | 50.2 | 48.95 | 1006.6429 | 4027.757 | 2.5 | 4747.1592 | 1.4 | 44% | -0.3 | 3000 | 30.4 | 65.2 | 542.9345 | 47.3 | 289.9464 | 252.9881 | 1.1259 | 2.5588 | 4.0533
45618.3701 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.4 | 51 | 7.5 | 2 | 65.2 | 76.2 | 2.8 | 3 | 17 | 182 | 63 | 1.4 | 1.3 | 47.3 | 47.7 | 50.2 | 222 | 0 | 0 | 26 | 25.4 | 550 | 49.9 | Room | On | 28.1 | 47.7 | 50.2 | 48.95 | 1006.6429 | 4027.757 | 2.5 | 4747.1592 | 1.4 | 44% | -0.3 | 3000 | 30.4 | 65.2 | 542.9345 | 47.3 | 289.9464 | 252.9881 | 1.1259 | 2.5588 | 4.0533
45618.3702 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.4 | 51 | 7.5 | 2 | 65.2 | 76.2 | 2.8 | 3 | 16 | 182 | 63 | 1.5 | 1.4 | 47.3 | 47.7 | 50.2 | 222 | 0 | 0 | 26 | 25.4 | 550 | 49.9 | Room | On | 28.1 | 47.7 | 50.2 | 48.95 | 1006.6429 | 4027.757 | 2.5 | 4747.1592 | 1.3 | 44% | -0.3 | 3000 | 30.4 | 65.2 | 542.9345 | 47.3 | 289.9464 | 252.9881 | 1.1259 | 2.5588 | 4.0533
45618.3704 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.5 | 51 | 7.5 | 2 | 65.4 | 76.2 | 2.9 | 3 | 16 | 180 | 63 | 1.6 | 1.5 | 47.3 | 47.7 | 50.2 | 223 | 0 | 0 | 26 | 25.4 | 550 | 49.8 | Room | On | 28.1 | 47.7 | 50.2 | 48.95 | 1006.6429 | 4027.757 | 2.5 | 4747.1592 | 1.3 | 44% | -0.4 | 3000 | 30.5 | 65.4 | 543.0792 | 47.3 | 289.9602 | 253.1189 | 1.1253 | 2.5575 | 4.0667
45618.3705 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.5 | 51 | 7.5 | 2 | 65.4 | 76.2 | 2.9 | 3 | 16 | 180 | 63 | 1.6 | 1.5 | 47.3 | 47.7 | 50.2 | 223 | 0 | 0 | 26 | 25.4 | 550 | 49.8 | Room | On | 28.1 | 47.7 | 50.2 | 48.95 | 1006.6429 | 4027.757 | 2.5 | 4747.1592 | 1.3 | 44% | -0.4 | 3000 | 30.5 | 65.4 | 543.0792 | 47.3 | 289.9602 | 253.1189 | 1.1253 | 2.5575 | 4.0667
45618.3706 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.5 | 51 | 7.5 | 2 | 65.4 | 76.2 | 2.9 | 3 | 17 | 180 | 63 | 1.6 | 1.5 | 47.3 | 47.7 | 50.2 | 223 | 0 | 0 | 26 | 25.4 | 550 | 49.8 | Room | On | 28.1 | 47.7 | 50.2 | 48.95 | 1006.6429 | 4027.757 | 2.5 | 4747.1592 | 1.3 | 44% | -0.4 | 3000 | 30.5 | 65.4 | 543.0792 | 47.3 | 289.9602 | 253.1189 | 1.1253 | 2.5575 | 4.0667
45618.3707 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.4 | 51 | 7.5 | 2 | 65.4 | 76.4 | 3 | 3 | 17 | 180 | 63 | 1.6 | 1.5 | 47.3 | 47.7 | 50.2 | 223 | 0 | 0 | 26 | 25.4 | 540 | 49.8 | Room | On | 28.1 | 47.7 | 50.2 | 48.95 | 1006.6429 | 4027.757 | 2.5 | 4747.1592 | 1.4 | 44% | -0.4 | 3000 | 30.4 | 65.4 | 543.3103 | 47.3 | 289.9464 | 253.3639 | 1.1242 | 2.555 | 4.0533
45618.3708 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.4 | 51 | 7.5 | 2 | 65.4 | 76.4 | 3 | 3 | 16 | 180 | 63 | 1.6 | 1.5 | 47.3 | 47.7 | 50.2 | 223 | 0 | 0 | 26 | 25.4 | 550 | 49.8 | Room | On | 28.1 | 47.7 | 50.2 | 48.95 | 1006.6429 | 4027.757 | 2.5 | 4747.1592 | 1.4 | 44% | -0.4 | 3000 | 30.4 | 65.4 | 543.3103 | 47.3 | 289.9464 | 253.3639 | 1.1242 | 2.555 | 4.0533
45618.3709 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.4 | 51 | 7.5 | 2 | 65.4 | 76.4 | 3 | 3 | 16 | 180 | 63 | 1.5 | 1.5 | 47.3 | 47.7 | 50.2 | 223 | 0 | 0 | 26 | 25.4 | 550 | 49.8 | Room | On | 28.1 | 47.7 | 50.2 | 48.95 | 1006.6429 | 4027.757 | 2.5 | 4747.1592 | 1.5 | 44% | -0.4 | 3000 | 30.4 | 65.4 | 543.3103 | 47.3 | 289.9464 | 253.3639 | 1.1242 | 2.555 | 4.0533
45618.371 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.4 | 51 | 7.5 | 2 | 65.4 | 76.4 | 3 | 3 | 16 | 180 | 63 | 1.5 | 1.5 | 47.3 | 47.7 | 50.2 | 222 | 0 | 0 | 26 | 25.4 | 550 | 49.8 | Room | On | 28.1 | 47.7 | 50.2 | 48.95 | 1006.6429 | 4027.757 | 2.5 | 4747.1592 | 1.5 | 44% | -0.4 | 3000 | 30.4 | 65.4 | 543.3103 | 47.3 | 289.9464 | 253.3639 | 1.1242 | 2.555 | 4.0533
45618.3712 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.4 | 51 | 7.5 | 2 | 65.4 | 76.4 | 3 | 3 | 16 | 180 | 63 | 1.5 | 1.4 | 47.3 | 47.6 | 50.2 | 222 | 0 | 0 | 26 | 25.4 | 550 | 49.8 | Room | On | 28.1 | 47.7 | 50.2 | 48.9 | 1006.6701 | 4027.757 | 2.6 | 4937.1786 | 1.5 | 44% | -0.4 | 3000 | 30.4 | 65.4 | 543.3103 | 47.3 | 289.9464 | 253.3639 | 1.1692 | 2.6573 | 4.0533
45618.3713 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.4 | 51 | 7.5 | 2 | 65.4 | 76.4 | 3 | 3 | 17 | 180 | 63 | 1.5 | 1.4 | 47.3 | 47.6 | 50.2 | 222 | 0 | 0 | 26 | 25.4 | 550 | 49.8 | Room | On | 28.1 | 47.7 | 50.2 | 48.9 | 1006.6701 | 4027.757 | 2.6 | 4937.1786 | 1.5 | 44% | -0.4 | 3000 | 30.4 | 65.4 | 543.3103 | 47.3 | 289.9464 | 253.3639 | 1.1692 | 2.6573 | 4.0533
45618.3714 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.4 | 51 | 7.5 | 2 | 65.4 | 76.4 | 3 | 3 | 17 | 180 | 63 | 1.5 | 1.4 | 47.3 | 47.6 | 50.2 | 221 | 0 | 0 | 25.8 | 25.4 | 550 | 49.8 | Room | On | 28.1 | 47.6 | 50.2 | 48.9 | 1006.6701 | 4027.5219 | 2.6 | 4936.8904 | 1.5 | 44% | -0.4 | 3000 | 30.4 | 65.4 | 543.3103 | 47.3 | 289.9464 | 253.3639 | 1.1691 | 2.6571 | 4.0533
45618.3715 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.3 | 51 | 7.5 | 2 | 65.4 | 76.4 | 3 | 3 | 16 | 180 | 63 | 1.6 | 1.4 | 47.3 | 47.6 | 50.2 | 221 | 0 | 0 | 25.8 | 25.4 | 550 | 49.8 | Room | On | 28.1 | 47.6 | 50.2 | 48.9 | 1006.6701 | 4027.5219 | 2.6 | 4936.8904 | 1.4 | 44% | -0.4 | 3000 | 30.3 | 65.4 | 543.541 | 47.3 | 289.9326 | 253.6085 | 1.168 | 2.6545 | 4.04
45618.3716 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.3 | 51 | 7.5 | 2 | 65.4 | 76.5 | 3 | 3 | 16 | 180 | 63 | 1.6 | 1.4 | 47.2 | 47.6 | 50 | 221 | 0 | 0 | 25.8 | 25.4 | 550 | 49.8 | Room | On | 28.1 | 47.6 | 50.2 | 48.8 | 1006.7243 | 4027.5219 | 2.4 | 4557.375 | 1.4 | 44% | -0.2 | 3000 | 30.3 | 65.4 | 543.541 | 47.2 | 289.7323 | 253.8088 | 1.0774 | 2.4485 | 4.04
45618.3717 | On | Off | Off | Off | On | Normal Operation | 22 | 24 | 22 | 30.4 | 51 | 7.5 | 2 | 65.4 | 76.5 | 3 | 3 | 17 | 180 | 63 | 1.6 | 1.5 | 47.2 | 47.6 | 50 | 220 | 0 | 0 | 25.8 | 25.4 | 550 | 49.8 | Room | On | 28.1 | 47.6 | 50.2 | 48.8 | 1006.7243 | 4027.5219 | 2.4 | 4557.375 | 1.4 | 44% | -0.2 | 3000 | 30.4 | 65.4 | 543.3103 | 47.2 | 289.746 | 253.5643 | 1.0784 | 2.4509 | 4.0533
45618.3719 | On | Off | Off | Off | On | Normal Operation | 22 | 24 | 22 | 30.2 | 51 | 7.5 | 2 | 65.2 | 76.5 | 3 | 3 | 16 | 180 | 63 | 1.5 | 1.4 | 47.2 | 47.6 | 50 | 220 | 0 | 0 | 25.8 | 25.4 | 540 | 49.8 | Room | On | 28.1 | 47.6 | 50 | 48.8 | 1006.7243 | 4027.5219 | 2.4 | 4557.375 | 1.5 | 44% | -0.2 | 3000 | 30.2 | 65.2 | 543.3977 | 47.2 | 289.7185 | 253.6792 | 1.0779 | 2.4498 | 4.0267
45618.372 | On | Off | Off | Off | On | Normal Operation | 23 | 24 | 23 | 30.2 | 51 | 7.5 | 2 | 65.2 | 76.5 | 3 | 3 | 17 | 180 | 63 | 1.5 | 1.4 | 47.2 | 47.5 | 50 | 220 | 0 | 0 | 25.8 | 25.4 | 550 | 49.8 | Room | On | 28.1 | 47.6 | 50 | 48.75 | 1006.7514 | 4027.5219 | 2.5 | 4747.3934 | 1.5 | 46% | -0.2 | 3000 | 30.2 | 65.2 | 543.3977 | 47.2 | 289.7185 | 253.6792 | 1.1228 | 2.441 | 4.0267
45618.3721 | On | Off | Off | Off | On | Normal Operation | 24 | 24 | 24 | 30.3 | 51 | 7.5 | 2 | 65.2 | 76.5 | 3 | 3.1 | 16 | 180 | 63 | 1.5 | 1.4 | 47.2 | 47.5 | 49.8 | 219 | 0 | 0 | 25.8 | 25.4 | 550 | 49.8 | Room | On | 28.1 | 47.6 | 50 | 48.65 | 1006.8055 | 4027.5219 | 2.3 | 4367.8367 | 1.5 | 48% | 0 | 3100 | 30.3 | 65.2 | 543.1663 | 47.2 | 289.7323 | 253.4341 | 1.0341 | 2.1543 | 4.04
45618.3722 | On | Off | Off | Off | On | Normal Operation | 24 | 24 | 24 | 30.5 | 51 | 7.5 | 2 | 65.2 | 76.5 | 3 | 3.2 | 17 | 180 | 63 | 1.5 | 1.4 | 47.2 | 47.5 | 50 | 219 | 0 | 0 | 25.8 | 25.4 | 550 | 49.8 | Room | On | 28.1 | 47.6 | 50 | 48.75 | 1006.7514 | 4027.5219 | 2.5 | 4747.3934 | 1.5 | 48% | -0.2 | 3200 | 30.5 | 65.2 | 542.7023 | 47.2 | 289.7598 | 252.9425 | 1.1261 | 2.3461 | 4.0667
45618.3723 | On | Off | Off | Off | On | Normal Operation | 24 | 24 | 24 | 30.5 | 51 | 7.5 | 2 | 65.2 | 76.5 | 3 | 3.2 | 16 | 180 | 63 | 1.5 | 1.4 | 47.2 | 47.6 | 50.2 | 219 | 0 | 0 | 25.8 | 25.4 | 540 | 49.8 | Room | On | 27.9 | 47.5 | 50 | 48.9 | 1006.6701 | 4027.2868 | 2.6 | 4901.4662 | 1.5 | 48% | -0.4 | 3200 | 30.5 | 65.2 | 542.7023 | 47.2 | 289.7598 | 252.9425 | 1.1627 | 2.4222 | 4.0667
45618.3724 | On | Off | Off | Off | On | Normal Operation | 24 | 22 | 24 | 30.5 | 51 | 7.5 | 2 | 65.2 | 76.5 | 3 | 3.2 | 16 | 180 | 63 | 1.6 | 1.4 | 47.2 | 47.6 | 50.2 | 219 | 0 | 0 | 25.8 | 25.4 | 550 | 49.8 | Room | On | 27.9 | 47.5 | 50 | 48.9 | 1006.6701 | 4027.2868 | 2.6 | 4901.4662 | 1.4 | 48% | -0.4 | 3200 | 30.5 | 65.2 | 542.7023 | 47.2 | 289.7598 | 252.9425 | 1.1627 | 2.4222 | 4.0667
45618.3726 | On | Off | Off | Off | On | Normal Operation | 24 | 22 | 24 | 30.5 | 51 | 7.5 | 2 | 65.2 | 76.5 | 3 | 3.2 | 16 | 180 | 63 | 1.6 | 1.4 | 47.2 | 47.6 | 50.2 | 219 | 0 | 0 | 25.8 | 25.4 | 550 | 49.8 | Room | On | 27.9 | 47.5 | 50 | 48.9 | 1006.6701 | 4027.2868 | 2.6 | 4901.4662 | 1.4 | 48% | -0.4 | 3200 | 30.5 | 65.2 | 542.7023 | 47.2 | 289.7598 | 252.9425 | 1.1627 | 2.4222 | 4.0667
45618.3727 | On | Off | Off | Off | On | Normal Operation | 23 | 22 | 23 | 30.3 | 51 | 7.5 | 2 | 65.2 | 76.5 | 3 | 3 | 16 | 180 | 63 | 1.5 | 1.4 | 47.2 | 47.6 | 50.2 | 219 | 0 | 0 | 25.7 | 25.4 | 550 | 49.8 | Room | On | 27.9 | 47.5 | 50 | 48.9 | 1006.6701 | 4027.2868 | 2.6 | 4901.4662 | 1.5 | 46% | -0.4 | 3000 | 30.3 | 65.2 | 543.1663 | 47.2 | 289.7323 | 253.4341 | 1.1604 | 2.5226 | 4.04
45618.3728 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.3 | 51 | 7.5 | 2 | 65.2 | 76.7 | 3 | 3 | 16 | 180 | 63 | 1.5 | 1.4 | 47.2 | 47.6 | 50.2 | 218 | 0 | 0 | 25.7 | 25.4 | 540 | 49.8 | Room | On | 28.1 | 47.6 | 50.2 | 48.9 | 1006.6701 | 4027.5219 | 2.6 | 4936.8904 | 1.5 | 44% | -0.4 | 3000 | 30.3 | 65.2 | 543.1663 | 47.2 | 289.7323 | 253.4341 | 1.1688 | 2.6564 | 4.04
45618.3729 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.3 | 51 | 7.5 | 2 | 65.2 | 76.7 | 3 | 3 | 17 | 180 | 63 | 1.5 | 1.4 | 47.2 | 47.5 | 50 | 218 | 0 | 0 | 25.7 | 25.4 | 550 | 49.8 | Room | On | 28.1 | 47.6 | 50.2 | 48.75 | 1006.7514 | 4027.5219 | 2.5 | 4747.3934 | 1.5 | 44% | -0.2 | 3000 | 30.3 | 65.2 | 543.1663 | 47.2 | 289.7323 | 253.4341 | 1.1239 | 2.5544 | 4.04
45618.373 | On | Off | Off | Off | On | Normal Operation | 22 | 22 | 22 | 30.2 | 51 | 7.5 | 2 | 65.4 | 76.7 | 3 | 3 | 16 | 180 | 63 | 1.5 | 1.4 | 47.2 | 47.5 | 50 | 218 | 0 | 0 | 25.7 | 25.4 | 550 | 49.8 | Room | On | 28.1 | 47.6 | 50.2 | 48.75 | 1006.7514 | 4027.5219 | 2.5 | 4747.3934 | 1.5 | 44% | -0.2 | 3000 | 30.2 | 65.4 | 543.7714 | 47.2 | 289.7185 | 254.0529 | 1.1212 | 2.5482 | 4.0267
45618.3731 | On | Off | Off | Off | On | Normal Operation | 22 | 24 | 22 | 30.1 | 50 | 7.5 | 2 | 65.4 | 76.8 | 3 | 2.9 | 16 | 180 | 63 | 1.5 | 1.4 | 47.2 | 47.3 | 49.8 | 217 | 0 | 0 | 25.7 | 25.4 | 550 | 49.8 | Room | On | 28.1 | 47.6 | 50.2 | 48.55 | 1006.8596 | 4027.5219 | 2.5 | 4747.9036 | 1.5 | 44% | 0 | 2900 | 30.1 | 65.4 | 544.0013 | 47.2 | 289.7048 | 254.2965 | 1.1202 | 2.546 | 4.0133
45618.3732 | On | Off | Off | Off | On | Normal Operation | 22 | 24 | 22 | 30.1 | 50 | 7.5 | 2 | 65.4 | 76.8 | 3 | 2.9 | 16 | 180 | 63 | 1.5 | 1.4 | 47.1 | 47.3 | 49.8 | 217 | 0 | 0 | 25.7 | 25.4 | 550 | 49.8 | Room | On | 28.1 | 47.3 | 49.8 | 48.55 | 1006.8596 | 4026.8165 | 2.5 | 4747.0721 | 1.5 | 44% | 0 | 2900 | 30.1 | 65.4 | 544.0013 | 47.1 | 289.5046 | 254.4967 | 1.1192 | 2.5436 | 4.0133
45618.3734 | On | Off | Off | Off | On | Normal Operation | 23 | 24 | 23 | 30.3 | 51 | 7.5 | 2 | 65.4 | 76.8 | 3.1 | 3 | 17 | 180 | 63 | 1.5 | 1.4 | 47.1 | 47.5 | 49.8 | 217 | 0 | 0 | 25.7 | 25.4 | 550 | 49.8 | Room | On | 28.1 | 47.3 | 49.8 | 48.65 | 1006.8055 | 4026.8165 | 2.3 | 4367.0717 | 1.6 | 46% | 0 | 3000 | 30.3 | 65.4 | 543.541 | 47.1 | 289.532 | 254.0091 | 1.0316 | 2.2425 | 4.04
45618.3735 | On | Off | Off | Off | On | Normal Operation | 24 | 24 | 24 | 30.2 | 51 | 7.5 | 2 | 65.4 | 76.8 | 3.1 | 3 | 16 | 180 | 63 | 1.5 | 1.4 | 47.1 | 47.5 | 49.8 | 218 | 0 | 0 | 25.7 | 25.4 | 550 | 49.8 | Room | On | 28.1 | 47.3 | 49.8 | 48.65 | 1006.8055 | 4026.8165 | 2.3 | 4367.0717 | 1.6 | 48% | 0 | 3000 | 30.2 | 65.4 | 543.7714 | 47.1 | 289.5183 | 254.2531 | 1.0306 | 2.147 | 4.0267
45618.3736 | On | Off | Off | Off | On | Normal Operation | 24 | 24 | 24 | 30.2 | 51 | 7.5 | 2 | 65.4 | 76.8 | 3.1 | 3.1 | 16 | 180 | 63 | 1.5 | 1.4 | 47.1 | 47.5 | 49.8 | 218 | 0 | 0 | 25.7 | 25.4 | 550 | 49.8 | Room | On | 28.1 | 47.3 | 49.8 | 48.65 | 1006.8055 | 4026.8165 | 2.3 | 4367.0717 | 1.6 | 48% | 0 | 3100 | 30.2 | 65.4 | 543.7714 | 47.1 | 289.5183 | 254.2531 | 1.0306 | 2.147 | 4.0267
45618.3737 | On | Off | Off | Off | On | Normal Operation | 24 | 24 | 24 | 30.3 | 51 | 7.5 | 2 | 65.2 | 76.8 | 3.1 | 3.1 | 16 | 180 | 63 | 1.5 | 1.4 | 47.1 | 47.5 | 49.8 | 218 | 0 | 0 | 25.7 | 25.4 | 540 | 49.7 | Room | On | 28.1 | 47.5 | 49.8 | 48.65 | 1006.8055 | 4027.2868 | 2.3 | 4367.5817 | 1.6 | 48% | -0.1 | 3100 | 30.3 | 65.2 | 543.1663 | 47.1 | 289.532 | 253.6343 | 1.0332 | 2.1525 | 4.04
45618.3738 | On | Off | Off | Off | On | Normal Operation | 24 | 24 | 24 | 30.3 | 51 | 7.5 | 2 | 65.2 | 76.7 | 3.1 | 3.1 | 16 | 180 | 63 | 1.5 | 1.4 | 47.1 | 47.5 | 49.8 | 219 | 0 | 0 | 25.7 | 25.4 | 550 | 49.7 | Room | On | 28.1 | 47.5 | 49.8 | 48.65 | 1006.8055 | 4027.2868 | 2.3 | 4367.5817 | 1.6 | 48% | -0.1 | 3100 | 30.3 | 65.2 | 543.1663 | 47.1 | 289.532 | 253.6343 | 1.0332 | 2.1525 | 4.04
45618.3739 | On | Off | Off | Off | On | Normal Operation | 24 | 24 | 24 | 30.3 | 51 | 7.5 | 2 | 65.2 | 76.7 | 3.1 | 3.2 | 16 | 180 | 63 | 1.5 | 1.4 | 47.1 | 47.5 | 50 | 219 | 0 | 0 | 25.7 | 25.4 | 550 | 49.7 | Room | On | 28.1 | 47.5 | 49.8 | 48.75 | 1006.7514 | 4027.2868 | 2.5 | 4747.1162 | 1.6 | 48% | -0.3 | 3200 | 30.3 | 65.2 | 543.1663 | 47.1 | 289.532 | 253.6343 | 1.123 | 2.3395 | 4.04
45618.3741 | On | Off | Off | Off | On | Normal Operation | 24 | 24 | 24 | 30.3 | 51 | 7.4 | 2 | 65.2 | 76.8 | 3.1 | 3.1 | 16 | 180 | 63 | 1.5 | 1.4 | 47.1 | 47.5 | 50 | 219 | 0 | 0 | 25.7 | 25.4 | 550 | 49.7 | Room | On | 28.1 | 47.5 | 49.8 | 48.75 | 1006.7514 | 4027.2868 | 2.5 | 4747.1162 | 1.6 | 48% | -0.3 | 3100 | 30.3 | 65.2 | 543.1663 | 47.1 | 289.532 | 253.6343 | 1.123 | 2.3395 | 4.0946
45618.3742 | On | Off | Off | Off | On | Normal Operation | 24 | 24 | 24 | 30.2 | 51 | 7.4 | 2 | 65.2 | 76.8 | 3.1 | 3.1 | 16 | 180 | 63 | 1.4 | 1.4 | 47.1 | 47.3 | 50 | 218 | 0 | 0 | 25.7 | 25.4 | 550 | 49.7 | Room | On | 27.9 | 47.5 | 50 | 48.65 | 1006.8055 | 4027.2868 | 2.7 | 5090.6689 | 1.7 | 48% | -0.3 | 3100 | 30.2 | 65.2 | 543.3977 | 47.1 | 289.5183 | 253.8794 | 1.2031 | 2.5064 | 4.0811
45618.3743 | On | Off | Off | Off | On | Normal Operation | 24 | 24 | 24 | 30.2 | 51 | 7.4 | 2 | 65.2 | 76.8 | 3.1 | 3.1 | 16 | 180 | 63 | 1.3 | 1.3 | 47.1 | 47.3 | 50 | 218 | 0 | 0 | 25.7 | 25.4 | 550 | 49.7 | Room | On | 27.9 | 47.5 | 50 | 48.65 | 1006.8055 | 4027.2868 | 2.7 | 5090.6689 | 1.8 | 48% | -0.3 | 3100 | 30.2 | 65.2 | 543.3977 | 47.1 | 289.5183 | 253.8794 | 1.2031 | 2.5064 | 4.0811
45618.3744 | On | Off | Off | Off | On | Normal Operation | 24 | 24 | 24 | 30.2 | 51 | 7.4 | 2 | 65.2 | 76.8 | 3.1 | 3.1 | 16 | 180 | 63 | 1.3 | 1.3 | 47.1 | 47.3 | 50 | 218 | 0 | 0 | 25.7 | 25.4 | 550 | 49.7 | Room | On | 27.9 | 47.5 | 50 | 48.65 | 1006.8055 | 4027.2868 | 2.7 | 5090.6689 | 1.8 | 48% | -0.3 | 3100 | 30.2 | 65.2 | 543.3977 | 47.1 | 289.5183 | 253.8794 | 1.2031 | 2.5064 | 4.0811
45618.3745 | On | Off | Off | Off | On | Normal Operation | 24 | 24 | 24 | 30.2 | 51 | 7.4 | 2 | 65.2 | 76.8 | 3.1 | 3.1 | 16 | 180 | 63 | 1.3 | 1.2 | 47.1 | 47.3 | 49.8 | 217 | 0 | 0 | 25.7 | 25.4 | 550 | 49.7 | Room | On | 27.9 | 47.5 | 50 | 48.55 | 1006.8596 | 4027.2868 | 2.5 | 4713.8355 | 1.8 | 48% | -0.1 | 3100 | 30.2 | 65.2 | 543.3977 | 47.1 | 289.5183 | 253.8794 | 1.114 | 2.3209 | 4.0811
45618.3746 | On | Off | Off | Off | On | Normal Operation | 24 | 24 | 24 | 30.2 | 51 | 7.4 | 2 | 65.2 | 77 | 3.1 | 3.1 | 16 | 180 | 63 | 1.3 | 1.2 | 47.1 | 47.3 | 49.8 | 217 | 0 | 0 | 25.7 | 25.4 | 550 | 49.7 | Room | On | 28.1 | 47.3 | 49.8 | 48.55 | 1006.8596 | 4026.8165 | 2.5 | 4747.0721 | 1.8 | 48% | -0.1 | 3100 | 30.2 | 65.2 | 543.3977 | 47.1 | 289.5183 | 253.8794 | 1.1219 | 2.3373 | 4.0811
45618.3748 | On | Off | Off | Off | On | Normal Operation | 24 | 24 | 24 | 30.1 | 50 | 7.4 | 2 | 65.4 | 77 | 3.1 | 3.1 | 16 | 180 | 63 | 1.4 | 1.3 | 47.1 | 47.2 | 49.8 | 217 | 0 | 0 | 25.6 | 25.4 | 550 | 49.7 | Room | On | 28.1 | 47.3 | 49.8 | 48.5 | 1006.8866 | 4026.8165 | 2.6 | 4937.0874 | 1.7 | 48% | -0.1 | 3100 | 30.1 | 65.4 | 544.0013 | 47.1 | 289.5046 | 254.4967 | 1.164 | 2.4249 | 4.0676
45618.3749 | On | Off | Off | Off | On | Normal Operation | 24 | 24 | 24 | 30.1 | 50 | 7.4 | 2 | 65.4 | 77 | 3.1 | 3.1 | 16 | 180 | 63 | 1.4 | 1.3 | 47.1 | 47.2 | 49.8 | 216 | 0 | 0 | 25.6 | 25.4 | 550 | 49.7 | Room | On | 28.1 | 47.3 | 49.8 | 48.5 | 1006.8866 | 4026.8165 | 2.6 | 4937.0874 | 1.7 | 48% | -0.1 | 3100 | 30.1 | 65.4 | 544.0013 | 47.1 | 289.5046 | 254.4967 | 1.164 | 2.4249 | 4.0676
45618.375 | On | Off | Off | Off | On | Normal Operation | 24 | 24 | 24 | 30.3 | 51 | 7.4 | 2 | 65.4 | 77.1 | 3 | 3.1 | 17 | 180 | 63 | 1.4 | 1.3 | 47 | 47.3 | 49.8 | 216 | 0 | 0 | 25.6 | 25.4 | 550 | 49.7 | Room | On | 28.1 | 47.3 | 49.8 | 48.55 | 1006.8596 | 4026.8165 | 2.5 | 4747.0721 | 1.6 | 48% | -0.1 | 3100 | 30.3 | 65.4 | 543.541 | 47 | 289.3317 | 254.2094 | 1.1204 | 2.3342 | 4.0946
45618.3751 | On | Off | Off | Off | On | Normal Operation | 24 | 24 | 24 | 30.2 | 51 | 7.5 | 2 | 65.4 | 77.1 | 3 | 3.1 | 16 | 182 | 63 | 1.4 | 1.3 | 47 | 47.3 | 49.8 | 216 | 0 | 0 | 25.6 | 25.4 | 550 | 49.8 | Room | On | 27.9 | 47.3 | 49.8 | 48.55 | 1006.8596 | 4026.8165 | 2.5 | 4713.2851 | 1.6 | 48% | 0 | 3100 | 30.2 | 65.4 | 543.7714 | 47 | 289.3181 | 254.4533 | 1.1114 | 2.3154 | 4.0267
45618.3752 | On | Off | Off | Off | On | Normal Operation | 24 | 26 | 24 | 30.2 | 51 | 7.5 | 2 | 65.4 | 77.1 | 3 | 3.1 | 16 | 182 | 63 | 1.5 | 1.4 | 47 | 47.3 | 49.8 | 215 | 0 | 0 | 25.6 | 25.4 | 550 | 49.8 | Room | On | 27.9 | 47.3 | 49.8 | 48.55 | 1006.8596 | 4026.8165 | 2.5 | 4713.2851 | 1.5 | 48% | 0 | 3100 | 30.2 | 65.4 | 543.7714 | 47 | 289.3181 | 254.4533 | 1.1114 | 2.3154 | 4.0267
45618.3753 | On | Off | Off | Off | On | Normal Operation | 24 | 26 | 24 | 30.2 | 51 | 7.5 | 2 | 65.4 | 77.1 | 3.1 | 3.1 | 16 | 182 | 63 | 1.5 | 1.4 | 47 | 47.3 | 49.8 | 215 | 0 | 0 | 25.6 | 25.4 | 550 | 49.8 | Room | On | 27.9 | 47.3 | 49.8 | 48.55 | 1006.8596 | 4026.8165 | 2.5 | 4713.2851 | 1.6 | 48% | 0 | 3100 | 30.2 | 65.4 | 543.7714 | 47 | 289.3181 | 254.4533 | 1.1114 | 2.3154 | 4.0267
45618.3754 | On | Off | Off | Off | On | Normal Operation | 25 | 26 | 25 | 30.2 | 51 | 7.5 | 2 | 65.4 | 77.1 | 3.1 | 3.2 | 16 | 182 | 63 | 1.5 | 1.4 | 47 | 47.2 | 49.8 | 215 | 0 | 0 | 25.6 | 25.4 | 550 | 49.8 | Room | On | 27.9 | 47.3 | 49.8 | 48.5 | 1006.8866 | 4026.8165 | 2.6 | 4901.948 | 1.6 | 50% | 0 | 3200 | 30.2 | 65.4 | 543.7714 | 47 | 289.3181 | 254.4533 | 1.1559 | 2.3118 | 4.0267
45618.3756 | On | Off | Off | Off | On | Normal Operation | 26 | 26 | 26 | 30.2 | 51 | 7.4 | 2 | 65.4 | 77.1 | 3.1 | 3.3 | 16 | 182 | 63 | 1.5 | 1.4 | 47 | 47.2 | 49.8 | 214 | 0 | 0 | 25.6 | 25.4 | 550 | 49.7 | Room | On | 28.1 | 47.2 | 49.8 | 48.5 | 1006.8866 | 4026.5814 | 2.6 | 4936.7991 | 1.6 | 52% | -0.1 | 3300 | 30.2 | 65.4 | 543.7714 | 47 | 289.3181 | 254.4533 | 1.1641 | 2.2386 | 4.0811
45618.3757 | On | Off | Off | Off | On | Normal Operation | 26 | 26 | 26 | 30.2 | 51 | 7.4 | 2 | 65.4 | 77.1 | 3.1 | 3.3 | 16 | 182 | 63 | 1.5 | 1.4 | 47 | 47.2 | 49.8 | 214 | 0 | 0 | 25.6 | 25.4 | 550 | 49.7 | Room | On | 28.1 | 47.2 | 49.8 | 48.5 | 1006.8866 | 4026.5814 | 2.6 | 4936.7991 | 1.6 | 52% | -0.1 | 3300 | 30.2 | 65.4 | 543.7714 | 47 | 289.3181 | 254.4533 | 1.1641 | 2.2386 | 4.0811
45618.3758 | On | Off | Off | Off | On | Normal Operation | 26 | 26 | 26 | 30.2 | 51 | 7.4 | 2 | 65.5 | 77.1 | 3.1 | 3.3 | 16 | 182 | 63 | 1.4 | 1.3 | 47 | 47.2 | 49.8 | 214 | 0 | 0 | 25.6 | 25.4 | 550 | 49.7 | Room | On | 28.1 | 47.2 | 49.8 | 48.5 | 1006.8866 | 4026.5814 | 2.6 | 4936.7991 | 1.7 | 52% | -0.1 | 3300 | 30.2 | 65.5 | 543.9582 | 47 | 289.3181 | 254.6401 | 1.1632 | 2.237 | 4.0811
45618.3759 | On | Off | Off | Off | On | Normal Operation | 26 | 26 | 26 | 30.1 | 50 | 7.4 | 2 | 65.5 | 77.2 | 3.1 | 3.3 | 16 | 182 | 63 | 1.4 | 1.2 | 47 | 47.1 | 49.8 | 213 | 0 | 0 | 25.6 | 25.4 | 550 | 49.7 | Room | On | 28.1 | 47.2 | 49.8 | 48.45 | 1006.9136 | 4026.5814 | 2.7 | 5126.8135 | 1.7 | 52% | -0.1 | 3300 | 30.1 | 65.5 | 544.1876 | 47 | 289.3045 | 254.8831 | 1.2069 | 2.3209 | 4.0676
45618.376 | On | Off | Off | Off | On | Normal Operation | 26 | 26 | 26 | 30.2 | 51 | 7.4 | 2 | 65.7 | 77.2 | 3.1 | 3.3 | 16 | 182 | 63 | 1.3 | 1.1 | 47 | 47.1 | 49.8 | 213 | 0 | 0 | 25.6 | 25.4 | 550 | 49.7 | Room | On | 28.1 | 47.1 | 49.8 | 48.45 | 1006.9136 | 4026.3462 | 2.7 | 5126.5141 | 1.8 | 52% | -0.1 | 3300 | 30.2 | 65.7 | 544.3318 | 47 | 289.3181 | 255.0137 | 1.2062 | 2.3196 | 4.0811
45618.3761 | On | Off | Off | Off | On | Normal Operation | 26 | 26 | 26 | 30.2 | 51 | 7.4 | 2 | 65.7 | 77.2 | 3.1 | 3.3 | 16 | 182 | 63 | 1.3 | 1.1 | 47 | 47.1 | 49.8 | 213 | 0 | 0 | 25.6 | 25.4 | 550 | 49.7 | Room | On | 28.1 | 47.1 | 49.8 | 48.45 | 1006.9136 | 4026.3462 | 2.7 | 5126.5141 | 1.8 | 52% | -0.1 | 3300 | 30.2 | 65.7 | 544.3318 | 47 | 289.3181 | 255.0137 | 1.2062 | 2.3196 | 4.0811
45618.3763 | On | Off | Off | Off | On | Normal Operation | 26 | 26 | 26 | 30.1 | 50 | 7.4 | 2 | 65.7 | 77.4 | 3.1 | 3.3 | 16 | 182 | 63 | 1.2 | 1 | 47 | 47.1 | 49.8 | 212 | 0 | 0 | 25.6 | 25.4 | 550 | 49.7 | Room | On | 28.1 | 47.1 | 49.8 | 48.45 | 1006.9136 | 4026.3462 | 2.7 | 5126.5141 | 1.9 | 52% | -0.1 | 3300 | 30.1 | 65.7 | 544.5602 | 47 | 289.3045 | 255.2557 | 1.205 | 2.3174 | 4.0676
45618.3764 | On | Off | Off | Off | On | Normal Operation | 26 | 26 | 26 | 30.1 | 50 | 7.4 | 2 | 65.8 | 77.4 | 3.1 | 3.3 | 16 | 182 | 63 | 1.2 | 1 | 46.8 | 47.1 | 49.8 | 212 | 0 | 0 | 25.6 | 25.4 | 550 | 49.7 | Room | On | 28.1 | 47.1 | 49.8 | 48.45 | 1006.9136 | 4026.3462 | 2.7 | 5126.5141 | 1.9 | 52% | -0.1 | 3300 | 30.1 | 65.8 | 544.7465 | 46.8 | 288.9042 | 255.8423 | 1.2023 | 2.3121 | 4.0676
45618.3765 | On | Off | Off | Off | On | Normal Operation | 26 | 26 | 26 | 30.2 | 51 | 7.4 | 2 | 65.8 | 77.4 | 3.1 | 3.3 | 16 | 182 | 63 | 1.3 | 1.1 | 46.8 | 47.1 | 49.8 | 212 | 0 | 0 | 25.6 | 25.4 | 560 | 49.7 | Room | On | 28.1 | 47.1 | 49.8 | 48.45 | 1006.9136 | 4026.3462 | 2.7 | 5126.5141 | 1.8 | 52% | -0.1 | 3300 | 30.2 | 65.8 | 544.5186 | 46.8 | 288.9176 | 255.601 | 1.2034 | 2.3142 | 4.0811
45618.3766 | On | Off | Off | Off | On | Normal Operation | 26 | 26 | 26 | 30.2 | 51 | 7.4 | 2 | 65.8 | 77.5 | 3.1 | 3.3 | 16 | 181 | 63 | 1.3 | 1.2 | 46.8 | 47.1 | 49.8 | 211 | 0 | 0 | 25.6 | 25.4 | 550 | 49.7 | Room | On | 28.1 | 47.1 | 49.8 | 48.45 | 1006.9136 | 4026.3462 | 2.7 | 5126.5141 | 1.8 | 52% | -0.1 | 3300 | 30.2 | 65.8 | 544.5186 | 46.8 | 288.9176 | 255.601 | 1.2034 | 2.3142 | 4.0811
45618.3767 | On | Off | Off | Off | On | Normal Operation | 26 | 26 | 26 | 30.2 | 51 | 7.4 | 2 | 66 | 77.7 | 3.1 | 3.3 | 16 | 181 | 63 | 1.4 | 1.2 | 46.8 | 47.1 | 49.8 | 211 | 0 | 0 | 25.5 | 25.4 | 550 | 49.7 | Room | On | 28.1 | 47.1 | 49.8 | 48.45 | 1006.9136 | 4026.3462 | 2.7 | 5126.5141 | 1.7 | 52% | -0.1 | 3300 | 30.2 | 66 | 544.8923 | 46.8 | 288.9176 | 255.9746 | 1.2016 | 2.3109 | 4.0811
45618.3768 | On | Off | Off | Off | On | Normal Operation | 26 | 26 | 26 | 30.2 | 51 | 7.4 | 2 | 66 | 77.7 | 3.1 | 3.3 | 16 | 181 | 63 | 1.4 | 1.2 | 46.8 | 47.1 | 49.8 | 211 | 0 | 0 | 25.5 | 25.4 | 550 | 49.7 | Room | On | 28.1 | 47.1 | 49.8 | 48.45 | 1006.9136 | 4026.3462 | 2.7 | 5126.5141 | 1.7 | 52% | -0.1 | 3300 | 30.2 | 66 | 544.8923 | 46.8 | 288.9176 | 255.9746 | 1.2016 | 2.3109 | 4.0811
45618.377 | On | Off | Off | Off | On | Normal Operation | 26 | 26 | 26 | 30.1 | 50 | 7.4 | 2 | 66.1 | 77.7 | 3.2 | 3.3 | 16 | 181 | 63 | 1.4 | 1.2 | 46.8 | 47.1 | 49.8 | 210 | 0 | 0 | 25.5 | 25.3 | 550 | 49.7 | Room | On | 27.9 | 47.1 | 49.8 | 48.45 | 1006.9136 | 4026.3462 | 2.7 | 5090.0265 | 1.8 | 52% | -0.1 | 3300 | 30.1 | 66.1 | 545.3053 | 46.8 | 288.9042 | 256.4011 | 1.1911 | 2.2906 | 4.0676
45618.3771 | On | Off | Off | Off | On | Normal Operation | 26 | 26 | 26 | 30.2 | 51 | 7.4 | 2 | 66.1 | 77.8 | 3.2 | 3.3 | 16 | 181 | 63 | 1.4 | 1.2 | 46.8 | 47.1 | 49.8 | 210 | 0 | 0 | 25.5 | 25.3 | 550 | 49.7 | Room | On | 27.9 | 47.1 | 49.8 | 48.45 | 1006.9136 | 4026.3462 | 2.7 | 5090.0265 | 1.8 | 52% | -0.1 | 3300 | 30.2 | 66.1 | 545.0791 | 46.8 | 288.9176 | 256.1615 | 1.1922 | 2.2927 | 4.0811
45618.3772 | On | Off | Off | Off | On | Normal Operation | 26 | 26 | 26 | 30.1 | 50 | 7.4 | 2 | 66.1 | 77.8 | 3.2 | 3.3 | 16 | 181 | 63 | 1.4 | 1.2 | 46.8 | 47.1 | 49.8 | 210 | 0 | 0 | 25.5 | 25.3 | 550 | 49.7 | Room | On | 27.9 | 47.1 | 49.8 | 48.45 | 1006.9136 | 4026.3462 | 2.7 | 5090.0265 | 1.8 | 52% | -0.1 | 3300 | 30.1 | 66.1 | 545.3053 | 46.8 | 288.9042 | 256.4011 | 1.1911 | 2.2906 | 4.0676
45618.3773 | On | Off | Off | Off | On | Normal Operation | 26 | 26 | 26 | 30.2 | 51 | 7.4 | 2 | 66.1 | 77.8 | 3.2 | 3.3 | 16 | 181 | 63 | 1.4 | 1.2 | 46.8 | 47.1 | 49.8 | 209 | 0 | 0 | 25.5 | 25.3 | 550 | 49.7 | Room | On | 27.9 | 47.1 | 49.8 | 48.45 | 1006.9136 | 4026.3462 | 2.7 | 5090.0265 | 1.8 | 52% | -0.1 | 3300 | 30.2 | 66.1 | 545.0791 | 46.8 | 288.9176 | 256.1615 | 1.1922 | 2.2927 | 4.0811
45618.3774 | On | Off | Off | Off | On | Normal Operation | 26 | 26 | 26 | 30 | 50 | 7.4 | 2 | 66.1 | 78 | 3.2 | 3.3 | 16 | 181 | 63 | 1.3 | 1.1 | 46.8 | 47.1 | 49.8 | 209 | 0 | 0 | 25.5 | 25.3 | 550 | 49.7 | Room | On | 28.1 | 47.1 | 49.8 | 48.45 | 1006.9136 | 4026.3462 | 2.7 | 5126.5141 | 1.9 | 52% | -0.1 | 3300 | 30 | 66.1 | 545.5311 | 46.8 | 288.8908 | 256.6403 | 1.1985 | 2.3049 | 4.0541
45618.3775 | On | Off | Off | Off | On | Normal Operation | 26 | 26 | 26 | 30.2 | 51 | 7.4 | 2 | 66.2 | 78 | 3.2 | 3.3 | 16 | 181 | 63 | 1.3 | 1.1 | 46.8 | 47.1 | 49.6 | 209 | 0 | 0 | 25.5 | 25.3 | 550 | 49.7 | Room | On | 28.1 | 47.1 | 49.8 | 48.35 | 1006.9676 | 4026.3462 | 2.5 | 4747.0267 | 1.9 | 52% | 0.1 | 3300 | 30.2 | 66.2 | 545.2659 | 46.8 | 288.9176 | 256.3483 | 1.1111 | 2.1367 | 4.0811
45618.3776 | On | Off | Off | Off | On | Normal Operation | 26 | 26 | 26 | 30.1 | 50 | 7.4 | 2 | 66.2 | 78 | 3.2 | 3.3 | 16 | 181 | 63 | 1.3 | 1.1 | 46.8 | 47.1 | 49.6 | 210 | 0 | 0 | 25.5 | 25.3 | 550 | 49.7 | Room | On | 28.1 | 47.1 | 49.8 | 48.35 | 1006.9676 | 4026.3462 | 2.5 | 4747.0267 | 1.9 | 52% | 0.1 | 3300 | 30.1 | 66.2 | 545.4916 | 46.8 | 288.9042 | 256.5874 | 1.11 | 2.1347 | 4.0676
45618.3778 | On | Off | Off | Off | On | Normal Operation | 26 | 26 | 26 | 30 | 50 | 7.4 | 2 | 66.2 | 78.1 | 3.2 | 3.3 | 16 | 181 | 63 | 1.3 | 1.1 | 46.8 | 47.1 | 49.6 | 210 | 0 | 0 | 25.4 | 25.3 | 550 | 49.7 | Room | On | 28.1 | 47.1 | 49.8 | 48.35 | 1006.9676 | 4026.3462 | 2.5 | 4747.0267 | 1.9 | 52% | 0.1 | 3300 | 30 | 66.2 | 545.7169 | 46.8 | 288.8908 | 256.8261 | 1.109 | 2.1327 | 4.0541
45618.3779 | On | Off | Off | Off | On | Normal Operation | 26 | 26 | 26 | 30 | 50 | 7.4 | 2 | 66.2 | 78.1 | 3.2 | 3.3 | 16 | 181 | 63 | 1.3 | 1.1 | 46.8 | 47.1 | 49.6 | 210 | 0 | 0 | 25.4 | 25.3 | 550 | 49.7 | Room | On | 28.5 | 47.1 | 49.6 | 48.35 | 1006.9676 | 4026.3462 | 2.5 | 4814.6001 | 1.9 | 52% | 0.1 | 3300 | 30 | 66.2 | 545.7169 | 46.8 | 288.8908 | 256.8261 | 1.1248 | 2.1631 | 4.0541
45618.378 | On | Off | Off | Off | On | Normal Operation | 26 | 28 | 26 | 30.1 | 50 | 7.4 | 2 | 66.2 | 78.1 | 3.2 | 3.3 | 16 | 181 | 63 | 1.4 | 1.2 | 46.8 | 47.1 | 49.6 | 209 | 0 | 0 | 25.4 | 25.3 | 550 | 49.7 | Room | On | 28.5 | 47.1 | 49.6 | 48.35 | 1006.9676 | 4026.3462 | 2.5 | 4814.6001 | 1.8 | 52% | 0.1 | 3300 | 30.1 | 66.2 | 545.4916 | 46.8 | 288.9042 | 256.5874 | 1.1258 | 2.1651 | 4.0676
45618.3781 | On | Off | Off | Off | On | Normal Operation | 26 | 28 | 26 | 30 | 50 | 7.4 | 2 | 66.4 | 78.2 | 3.2 | 3.3 | 16 | 181 | 63 | 1.4 | 1.2 | 46.6 | 47.1 | 49.6 | 209 | 0 | 0 | 25.4 | 25.3 | 550 | 49.7 | Room | On | 28.5 | 47.1 | 49.6 | 48.35 | 1006.9676 | 4026.3462 | 2.5 | 4814.6001 | 1.8 | 52% | 0.1 | 3300 | 30 | 66.4 | 546.0883 | 46.6 | 288.4906 | 257.5977 | 1.1214 | 2.1566 | 4.0541
45618.3782 | On | Off | Off | Off | On | Normal Operation | 27 | 28 | 27 | 30 | 50 | 7.4 | 2 | 66.4 | 78.2 | 3.2 | 3.3 | 16 | 181 | 63 | 1.4 | 1.2 | 46.6 | 47 | 49.6 | 209 | 0 | 0 | 25.4 | 25.3 | 550 | 49.7 | Room | On | 28.5 | 47.1 | 49.6 | 48.3 | 1006.9945 | 4026.3462 | 2.6 | 5007.3181 | 1.8 | 54% | 0.1 | 3300 | 30 | 66.4 | 546.0883 | 46.6 | 288.4906 | 257.5977 | 1.1663 | 2.1598 | 4.0541
45618.3783 | On | Off | Off | Off | On | Normal Operation | 28 | 28 | 28 | 30.1 | 50 | 7.4 | 2 | 66.4 | 78.2 | 3.2 | 3.4 | 16 | 181 | 63 | 1.3 | 1.2 | 46.6 | 47 | 49.6 | 208 | 0 | 0 | 25.4 | 25.3 | 550 | 49.7 | Room | On | 27.9 | 47 | 49.6 | 48.3 | 1006.9945 | 4026.1111 | 2.6 | 4901.6147 | 1.9 | 56% | 0.1 | 3400 | 30.1 | 66.4 | 545.8641 | 46.6 | 288.5039 | 257.3602 | 1.1427 | 2.0406 | 4.0676
45618.3785 | On | Off | Off | Off | On | Normal Operation | 28 | 28 | 28 | 30.2 | 51 | 7.3 | 1 | 66.4 | 78.2 | 3.2 | 3.5 | 16 | 181 | 63 | 1.2 | 1.1 | 46.6 | 47 | 49.6 | 208 | 0 | 0 | 25.4 | 25.3 | 550 | 49.7 | Room | On | 27.9 | 47 | 49.6 | 48.3 | 1006.9945 | 4026.1111 | 2.6 | 4901.6147 | 2 | 56% | 0.1 | 3500 | 30.2 | 66.4 | 545.6396 | 46.6 | 288.5172 | 257.1224 | 1.1438 | 2.0425 | 4.137
45618.3786 | On | Off | Off | Off | On | Normal Operation | 28 | 28 | 28 | 30.2 | 51 | 7.3 | 1 | 66.5 | 78.4 | 3.2 | 3.5 | 16 | 181 | 63 | 1.1 | 0.9 | 46.6 | 47 | 49.6 | 208 | 0 | 0 | 25.4 | 25.3 | 550 | 49.7 | Room | On | 27.9 | 47 | 49.6 | 48.3 | 1006.9945 | 4026.1111 | 2.6 | 4901.6147 | 2.1 | 56% | 0.1 | 3500 | 30.2 | 66.5 | 545.8264 | 46.6 | 288.5172 | 257.3092 | 1.143 | 2.041 | 4.137
45618.3787 | On | Off | Off | Off | On | Normal Operation | 28 | 26 | 28 | 30 | 50 | 7.3 | 1 | 66.5 | 78.4 | 3.2 | 3.5 | 16 | 181 | 63 | 1 | 0.8 | 46.6 | 47 | 49.8 | 207 | 0 | 0 | 25.3 | 25.3 | 550 | 49.7 | Room | On | 27.9 | 47 | 49.6 | 48.4 | 1006.9406 | 4026.1111 | 2.8 | 5278.3792 | 2.2 | 56% | -0.1 | 3500 | 30 | 66.5 | 546.2741 | 46.6 | 288.4906 | 257.7835 | 1.2286 | 2.1939 | 4.1096
45618.3788 | On | Off | Off | Off | On | Normal Operation | 28 | 26 | 28 | 30.1 | 50 | 7.3 | 1 | 66.7 | 78.5 | 3.1 | 3.5 | 16 | 181 | 63 | 0.9 | 0.8 | 46.5 | 47 | 49.8 | 207 | 0 | 0 | 25.3 | 25.3 | 550 | 49.7 | Room | On | 28.1 | 47 | 49.8 | 48.4 | 1006.9406 | 4026.1111 | 2.8 | 5316.2171 | 2.2 | 56% | -0.1 | 3500 | 30.1 | 66.7 | 546.423 | 46.5 | 288.3038 | 258.1192 | 1.2358 | 2.2067 | 4.1233
45618.3789 | On | Off | Off | Off | On | Normal Operation | 27 | 26 | 27 | 30.2 | 51 | 7.3 | 1 | 66.8 | 78.8 | 3.1 | 3.4 | 16 | 181 | 63 | 0.9 | 0.7 | 46.3 | 47 | 49.8 | 207 | 0 | 0 | 25.3 | 25.3 | 550 | 49.7 | Room | On | 28.1 | 47 | 49.8 | 48.4 | 1006.9406 | 4026.1111 | 2.8 | 5316.2171 | 2.2 | 54% | -0.1 | 3400 | 30.2 | 66.8 | 546.3868 | 46.3 | 287.9165 | 258.4703 | 1.2341 | 2.2853 | 4.137
45618.379 | On | Off | Off | Off | On | Normal Operation | 26 | 26 | 26 | 30.2 | 51 | 7.3 | 1 | 66.8 | 79 | 3.1 | 3.4 | 16 | 181 | 63 | 0.9 | 0.7 | 46.1 | 47.1 | 49.8 | 206 | 0 | 0 | 25.3 | 25.3 | 550 | 49.7 | Room | On | 28.1 | 47 | 49.8 | 48.45 | 1006.9136 | 4026.1111 | 2.7 | 5126.2148 | 2.2 | 52% | -0.1 | 3400 | 30.2 | 66.8 | 546.3868 | 46.1 | 287.5161 | 258.8707 | 1.1881 | 2.2849 | 4.137
45618.3792 | On | Off | Off | Off | On | Normal Operation | 26 | 26 | 26 | 30 | 50 | 7.3 | 1 | 67 | 79.1 | 3.1 | 3.3 | 16 | 181 | 63 | 1 | 0.9 | 46.1 | 47 | 49.6 | 206 | 0 | 0 | 25.3 | 25.3 | 550 | 49.7 | Room | On | 28.1 | 47 | 49.8 | 48.3 | 1006.9945 | 4026.1111 | 2.6 | 4936.7517 | 2.1 | 52% | 0.1 | 3300 | 30 | 67 | 547.2028 | 46.1 | 287.4903 | 259.7126 | 1.1405 | 2.1933 | 4.1096
45618.3793 | On | Off | Off | Off | On | Normal Operation | 26 | 26 | 26 | 29.9 | 50 | 7.4 | 2 | 67 | 79.1 | 3.1 | 3.3 | 16 | 181 | 63 | 1.1 | 0.9 | 46 | 46.8 | 49.4 | 206 | 0 | 0 | 25.3 | 25.3 | 550 | 49.7 | Room | On | 27.7 | 47 | 49.6 | 48.1 | 1007.1022 | 4026.1111 | 2.6 | 4866.9981 | 2 | 52% | 0.3 | 3300 | 29.9 | 67 | 547.4234 | 46 | 287.2774 | 260.1461 | 1.1225 | 2.1587 | 4.0405
45618.3794 | On | Off | Off | Off | On | Normal Operation | 26 | 29 | 26 | 30 | 50 | 7.4 | 2 | 67 | 79.2 | 3.1 | 3.3 | 16 | 181 | 63 | 1.1 | 0.9 | 45.8 | 46.8 | 49.4 | 205 | 0 | 0 | 25.3 | 25.2 | 550 | 49.7 | Room | On | 27.7 | 47 | 49.6 | 48.1 | 1007.1022 | 4026.1111 | 2.6 | 4866.9981 | 2 | 52% | 0.3 | 3300 | 30 | 67 | 547.2028 | 45.8 | 286.8901 | 260.3128 | 1.1218 | 2.1573 | 4.0541
45618.3795 | On | Off | Off | Off | On | Normal Operation | 26 | 29 | 26 | 30 | 50 | 7.4 | 2 | 67 | 79.2 | 3.1 | 3.3 | 16 | 181 | 62 | 1.2 | 1 | 45.6 | 47 | 49.4 | 205 | 0 | 0 | 25.3 | 25.2 | 550 | 49.7 | Room | On | 27.7 | 47 | 49.6 | 48.2 | 1007.0484 | 4026.1111 | 2.4 | 4492.3736 | 1.9 | 52% | 0.3 | 3300 | 30 | 67 | 547.2028 | 45.6 | 286.4899 | 260.7129 | 1.0339 | 1.9882 | 4.0541
45618.3796 | On | Off | Off | Off | On | Normal Operation | 27 | 29 | 27 | 30 | 50 | 7.4 | 2 | 67 | 79.2 | 3.1 | 3.3 | 16 | 181 | 62 | 1.2 | 1 | 45.6 | 47 | 49.4 | 205 | 0 | 0 | 25.3 | 25.2 | 550 | 49.7 | Room | On | 27.7 | 47 | 49.6 | 48.2 | 1007.0484 | 4026.1111 | 2.4 | 4492.3736 | 1.9 | 54% | 0.3 | 3300 | 30 | 67 | 547.2028 | 45.6 | 286.4899 | 260.7129 | 1.0339 | 1.9146 | 4.0541
45618.3797 | On | Off | Off | Off | On | Normal Operation | 28 | 29 | 28 | 30 | 50 | 7.4 | 2 | 67 | 79.2 | 3.2 | 3.4 | 16 | 180 | 62 | 1.3 | 1.1 | 45.6 | 47 | 49.6 | 204 | 0 | 0 | 25.2 | 25.2 | 550 | 49.7 | Room | On | 28.1 | 47 | 49.6 | 48.3 | 1006.9945 | 4026.1111 | 2.6 | 4936.7517 | 1.9 | 56% | 0.1 | 3400 | 30 | 67 | 547.2028 | 45.6 | 286.4899 | 260.7129 | 1.1361 | 2.0288 | 4.0541
45618.3798 | On | Off | Off | Off | On | Normal Operation | 28 | 29 | 28 | 30 | 50 | 7.4 | 2 | 67 | 79.2 | 3.2 | 3.5 | 16 | 180 | 62 | 1.3 | 1.1 | 45.8 | 47 | 49.6 | 204 | 0 | 0 | 25.2 | 25.2 | 550 | 49.7 | Room | On | 28.1 | 47 | 49.6 | 48.3 | 1006.9945 | 4026.1111 | 2.6 | 4936.7517 | 1.9 | 56% | 0.1 | 3500 | 30 | 67 | 547.2028 | 45.8 | 286.8901 | 260.3128 | 1.1379 | 2.0319 | 4.0541
45618.38 | On | Off | Off | Off | On | Normal Operation | 29 | 29 | 29 | 30 | 50 | 7.3 | 1 | 67 | 79.2 | 3.3 | 3.6 | 16 | 180 | 62 | 1.3 | 1.1 | 45.8 | 46.8 | 49.6 | 204 | 0 | 0 | 25.2 | 25.1 | 550 | 49.7 | Room | On | 28.1 | 47 | 49.6 | 48.2 | 1007.0484 | 4026.1111 | 2.8 | 5316.7863 | 2 | 58% | 0.1 | 3600 | 30 | 67 | 547.2028 | 45.8 | 286.8901 | 260.3128 | 1.2255 | 2.1129 | 4.1096
45618.3801 | On | Off | Off | Off | On | Normal Operation | 29 | 27 | 29 | 30.2 | 51 | 7.3 | 1 | 67.1 | 79.2 | 3.2 | 3.6 | 16 | 180 | 62 | 1.1 | 0.9 | 45.8 | 46.8 | 49.6 | 205 | 0 | 0 | 25.2 | 25.1 | 550 | 49.7 | Room | On | 28.1 | 47 | 49.6 | 48.2 | 1007.0484 | 4026.1111 | 2.8 | 5316.7863 | 2.1 | 58% | 0.1 | 3600 | 30.2 | 67.1 | 546.9473 | 45.8 | 286.9154 | 260.0318 | 1.2268 | 2.1152 | 4.137
45618.3802 | On | Off | Off | Off | On | Normal Operation | 29 | 27 | 29 | 30.2 | 51 | 7.3 | 1 | 67.2 | 79.3 | 3.3 | 3.6 | 16 | 180 | 62 | 1 | 0.8 | 45.6 | 46.8 | 49.6 | 205 | 0 | 0 | 25.1 | 25.1 | 550 | 49.6 | Room | On | 28.1 | 46.8 | 49.6 | 48.2 | 1007.0484 | 4025.6408 | 2.8 | 5316.1653 | 2.3 | 58% | 0 | 3600 | 30.2 | 67.2 | 547.1341 | 45.6 | 286.515 | 260.6191 | 1.2239 | 2.1102 | 4.137
45618.3803 | On | Off | Off | Off | On | Normal Operation | 28 | 27 | 28 | 30.2 | 51 | 7.3 | 1 | 67.4 | 79.3 | 3.3 | 3.5 | 16 | 180 | 63 | 1 | 0.8 | 45.5 | 46.8 | 49.6 | 205 | 0 | 0 | 25.1 | 25.1 | 550 | 49.6 | Room | On | 28.1 | 46.8 | 49.6 | 48.2 | 1007.0484 | 4025.6408 | 2.8 | 5316.1653 | 2.3 | 56% | 0 | 3500 | 30.2 | 67.4 | 547.5077 | 45.5 | 286.3148 | 261.193 | 1.2212 | 2.1807 | 4.137
45618.3804 | On | Off | Off | Off | On | Normal Operation | 27 | 27 | 27 | 30.2 | 51 | 7.3 | 1 | 67.4 | 79.5 | 3.3 | 3.5 | 16 | 180 | 63 | 1 | 0.7 | 45.3 | 46.8 | 49.6 | 205 | 0 | 0 | 25.1 | 25 | 550 | 49.6 | Room | On | 28.1 | 46.8 | 49.6 | 48.2 | 1007.0484 | 4025.6408 | 2.8 | 5316.1653 | 2.3 | 54% | 0 | 3500 | 30.2 | 67.4 | 547.5077 | 45.3 | 285.9143 | 261.5934 | 1.2193 | 2.258 | 4.137
45618.3805 | On | Off | Off | Off | On | Normal Operation | 27 | 27 | 27 | 30.1 | 50 | 7.3 | 1 | 67.5 | 79.6 | 3.3 | 3.4 | 16 | 180 | 63 | 1 | 0.7 | 45.3 | 46.8 | 49.6 | 205 | 0 | 0 | 25.1 | 25 | 550 | 49.6 | Room | On | 28.1 | 46.8 | 49.6 | 48.2 | 1007.0484 | 4025.6408 | 2.8 | 5316.1653 | 2.3 | 54% | 0 | 3400 | 30.1 | 67.5 | 547.9132 | 45.3 | 285.902 | 262.0112 | 1.2174 | 2.2544 | 4.1233
45618.3807 | On | Off | Off | Off | On | Normal Operation | 27 | 27 | 27 | 30 | 50 | 7.3 | 1 | 67.5 | 79.7 | 3.3 | 3.4 | 16 | 180 | 63 | 1 | 0.8 | 45.1 | 46.8 | 49.6 | 205 | 0 | 0 | 25 | 25 | 550 | 49.6 | Room | On | 28.1 | 46.8 | 49.6 | 48.2 | 1007.0484 | 4025.6408 | 2.8 | 5316.1653 | 2.3 | 54% | 0 | 3400 | 30 | 67.5 | 548.1315 | 45.1 | 285.4896 | 262.642 | 1.2145 | 2.249 | 4.1096
45618.3808 | On | Off | Off | Off | On | Normal Operation | 27 | 29 | 27 | 29.8 | 50 | 7.3 | 1 | 67.5 | 79.8 | 3.3 | 3.4 | 16 | 180 | 62 | 0.9 | 0.7 | 45.1 | 46.6 | 49.4 | 202 | 0 | 0 | 25 | 25 | 550 | 49.6 | Room | On | 27.9 | 46.8 | 49.6 | 48 | 1007.156 | 4025.6408 | 2.8 | 5278.8917 | 2.4 | 54% | 0.2 | 3400 | 29.8 | 67.5 | 548.5671 | 45.1 | 285.4653 | 263.1018 | 1.2038 | 2.2293 | 4.0822
-3.2
H=(0.000684*P^2+.01239*P+.87016)*T+(538.34-1.9179*P-0.0645*P^2)
H=(0.00756*P+1.7739)*T+(201.84-0.2194*P)

## Indoor 20.00.00
Time | Water Law Set Temp. ( ℃) | 3Way Valve | Water Pump | Flow Sensor | Water In ( ℃) | Water Out ( ℃)
45618.2915 | 50.3 | Room | Off | 0 | 18.8 | 20.4
45618.2916 | 50.3 | Room | Off | 0 | 18.8 | 20.4
45618.2918 | 50.3 | Room | Off | 0 | 18.8 | 20.4
45618.2919 | 50.3 | Room | Off | 0 | 18.8 | 20.4
45618.292 | 50.3 | Tank | On | 28.7 | 18.9 | 20.4
45618.2921 | 50.3 | Tank | On | 28.7 | 18.9 | 20.4
45618.2922 | 50.3 | Tank | On | 28.7 | 18.9 | 20.4
45618.2923 | 50.3 | Tank | On | 28.7 | 18.9 | 20.4
45618.2925 | 50.3 | Tank | On | 27.9 | 20.2 | 20.8
45618.2926 | 50.3 | Tank | On | 27.9 | 20.2 | 20.8
45618.2927 | 50.3 | Tank | On | 27.9 | 20.2 | 20.8
45618.2928 | 50.3 | Tank | On | 27.9 | 20.2 | 20.8
45618.2929 | 50.3 | Tank | On | 27.7 | 18.8 | 21
45618.293 | 50.3 | Tank | On | 27.7 | 18.8 | 21
45618.2931 | 50.3 | Tank | On | 27.7 | 18.8 | 21
45618.2933 | 50.3 | Tank | On | 27.7 | 18.8 | 21
45618.2934 | 50.4 | Tank | On | 27.5 | 18.2 | 20.7
45618.2935 | 50.4 | Tank | On | 27.5 | 18.2 | 20.7
45618.2936 | 50.4 | Tank | On | 27.5 | 18.2 | 20.7
45618.2937 | 50.4 | Tank | On | 27.5 | 18.2 | 20.7
45618.2938 | 50.4 | Tank | On | 27.5 | 18.2 | 20.7
45618.294 | 50.3 | Tank | On | 27.5 | 18.3 | 22.6
45618.2941 | 50.3 | Tank | On | 27.5 | 18.3 | 22.6
45618.2942 | 50.3 | Tank | On | 27.5 | 18.3 | 22.6
45618.2943 | 50.3 | Tank | On | 27.5 | 18.3 | 22.6
45618.2944 | 50.3 | Tank | On | 27.5 | 18.5 | 23
45618.2945 | 50.3 | Tank | On | 27.5 | 18.5 | 23
45618.2947 | 50.3 | Tank | On | 27.5 | 18.5 | 23
45618.2948 | 50.3 | Tank | On | 27.5 | 18.5 | 23
45618.2949 | 50.3 | Tank | On | 27.5 | 18.7 | 23.2
45618.295 | 50.3 | Tank | On | 27.5 | 18.7 | 23.2
45618.2951 | 50.3 | Tank | On | 27.5 | 18.7 | 23.2
45618.2952 | 50.3 | Tank | On | 27.5 | 18.7 | 23.2
45618.2953 | 50.3 | Tank | On | 27.7 | 19.2 | 23.7
45618.2955 | 50.3 | Tank | On | 27.7 | 19.2 | 23.7
45618.2956 | 50.3 | Tank | On | 27.7 | 19.2 | 23.7
45618.2957 | 50.3 | Tank | On | 27.7 | 19.2 | 23.7
45618.2958 | 50.3 | Tank | On | 27.7 | 19.7 | 24.3
45618.2959 | 50.3 | Tank | On | 27.7 | 19.7 | 24.3
45618.296 | 50.3 | Tank | On | 27.7 | 19.7 | 24.3
45618.2962 | 50.3 | Room | On | 27.7 | 19.7 | 24.3
45618.2963 | 50.3 | Room | On | 27.5 | 20.2 | 24.7
45618.2964 | 50.3 | Room | On | 27.5 | 20.2 | 24.7
45618.2965 | 50.3 | Room | On | 27.5 | 20.2 | 24.7
45618.2966 | 50.3 | Room | On | 27.5 | 20.2 | 24.7
45618.2967 | 50.3 | Room | On | 27.5 | 20.6 | 25.2
45618.2969 | 50.3 | Room | On | 27.5 | 20.6 | 25.2
45618.297 | 50.3 | Room | On | 27.5 | 20.6 | 25.2
45618.2971 | 50.3 | Room | On | 27.5 | 20.6 | 25.2
45618.2972 | 50.3 | Room | On | 27.7 | 21.2 | 25.7
45618.2973 | 50.3 | Room | On | 27.7 | 21.2 | 25.7
45618.2974 | 50.3 | Room | On | 27.7 | 21.2 | 25.7
45618.2975 | 50.3 | Room | On | 27.7 | 21.2 | 25.7
45618.2977 | 50.2 | Room | On | 27.5 | 21.7 | 26.3
45618.2978 | 50.2 | Room | On | 27.5 | 21.7 | 26.3
45618.2979 | 50.2 | Room | On | 27.5 | 21.7 | 26.3
45618.298 | 50.2 | Room | On | 27.5 | 21.7 | 26.3
45618.2981 | 50.2 | Room | On | 27.5 | 22.3 | 26.8
45618.2982 | 50.2 | Room | On | 27.5 | 22.3 | 26.8
45618.2984 | 50.2 | Room | On | 27.5 | 22.3 | 26.8
45618.2985 | 50.2 | Room | On | 27.5 | 22.3 | 26.8
45618.2986 | 50.3 | Room | On | 27.9 | 22.5 | 27.3
45618.2987 | 50.3 | Room | On | 27.9 | 22.5 | 27.3
45618.2988 | 50.3 | Room | On | 27.9 | 22.5 | 27.3
45618.2989 | 50.3 | Room | On | 27.9 | 22.5 | 27.3
45618.2991 | 50.3 | Room | On | 27.9 | 23.2 | 28.1
45618.2992 | 50.3 | Room | On | 27.9 | 23.2 | 28.1
45618.2993 | 50.3 | Room | On | 27.9 | 23.2 | 28.1
45618.2994 | 50.3 | Room | On | 27.9 | 23.2 | 28.1
45618.2995 | 50.3 | Room | On | 27.7 | 23.7 | 28.7
45618.2996 | 50.3 | Room | On | 27.7 | 23.7 | 28.7
45618.2997 | 50.3 | Room | On | 27.7 | 23.7 | 28.7
45618.2999 | 50.3 | Room | On | 27.7 | 23.7 | 28.7
45618.3 | 50.3 | Room | On | 27.9 | 24.4 | 29.5
45618.3001 | 50.3 | Room | On | 27.9 | 24.4 | 29.5
45618.3002 | 50.3 | Room | On | 27.9 | 24.4 | 29.5
45618.3003 | 50.3 | Room | On | 27.9 | 24.4 | 29.5
45618.3004 | 50.3 | Room | On | 27.7 | 24.6 | 29.7
45618.3006 | 50.3 | Room | On | 27.7 | 24.6 | 29.7
45618.3007 | 50.3 | Room | On | 27.7 | 24.6 | 29.7
45618.3008 | 50.3 | Room | On | 27.7 | 24.6 | 29.7
45618.3009 | 50.3 | Room | On | 27.7 | 25.3 | 30.4
45618.301 | 50.3 | Room | On | 27.7 | 25.3 | 30.4
45618.3011 | 50.3 | Room | On | 27.7 | 25.3 | 30.4
45618.3012 | 50.3 | Room | On | 27.7 | 25.3 | 30.4
45618.3014 | 50.3 | Room | On | 28.1 | 26 | 31
45618.3015 | 50.3 | Room | On | 28.1 | 26 | 31
45618.3016 | 50.3 | Room | On | 28.1 | 26 | 31
45618.3017 | 50.3 | Room | On | 28.1 | 26 | 31
45618.3018 | 50.3 | Room | On | 27.9 | 26.4 | 31.5
45618.3019 | 50.3 | Room | On | 27.9 | 26.4 | 31.5
45618.3021 | 50.3 | Room | On | 27.9 | 26.4 | 31.5
45618.3022 | 50.3 | Room | On | 27.9 | 26.4 | 31.5
45618.3023 | 50.3 | Room | On | 27.9 | 26.7 | 32
45618.3024 | 50.3 | Room | On | 27.9 | 26.7 | 32
45618.3025 | 50.3 | Room | On | 27.9 | 26.7 | 32
45618.3026 | 50.3 | Room | On | 27.9 | 26.7 | 32
45618.3028 | 50.3 | Room | On | 27.9 | 27.6 | 32.6
45618.3029 | 50.2 | Room | On | 27.7 | 27.6 | 32.6
45618.303 | 50.2 | Room | On | 27.7 | 27.6 | 32.6
45618.3031 | 50.2 | Room | On | 27.7 | 27.6 | 32.6
45618.3032 | 50.2 | Room | On | 27.7 | 27.6 | 32.6
45618.3033 | 50.2 | Room | On | 27.7 | 27.7 | 32.7
45618.3034 | 50.2 | Room | On | 27.7 | 27.7 | 32.7
45618.3036 | 50.2 | Room | On | 27.7 | 27.7 | 32.7
45618.3037 | 50.2 | Room | On | 27.7 | 27.7 | 32.7
45618.3038 | 50.3 | Room | On | 27.9 | 28.3 | 33.1
45618.3039 | 50.3 | Room | On | 27.9 | 28.3 | 33.1
45618.304 | 50.3 | Room | On | 27.9 | 28.3 | 33.1
45618.3041 | 50.3 | Room | On | 27.9 | 28.3 | 33.1
45618.3043 | 50.3 | Room | On | 27.9 | 28.8 | 33.6
45618.3044 | 50.3 | Room | On | 27.9 | 28.8 | 33.6
45618.3045 | 50.3 | Room | On | 27.9 | 28.8 | 33.6
45618.3046 | 50.3 | Room | On | 27.9 | 28.8 | 33.6
45618.3047 | 50.3 | Room | On | 27.7 | 29.3 | 34.7
45618.3048 | 50.3 | Room | On | 27.7 | 29.3 | 34.7
45618.305 | 50.3 | Room | On | 27.7 | 29.3 | 34.7
45618.3051 | 50.3 | Room | On | 27.7 | 29.3 | 34.7
45618.3052 | 50.3 | Room | On | 28.1 | 29.7 | 35
45618.3053 | 50.3 | Room | On | 28.1 | 29.7 | 35
45618.3054 | 50.3 | Room | On | 28.1 | 29.7 | 35
45618.3055 | 50.3 | Room | On | 28.1 | 29.7 | 35
45618.3056 | 50.4 | Room | On | 27.7 | 30.3 | 35.5
45618.3058 | 50.4 | Room | On | 27.7 | 30.3 | 35.5
45618.3059 | 50.4 | Room | On | 27.7 | 30.3 | 35.5
45618.306 | 50.4 | Room | On | 27.7 | 30.3 | 35.5
45618.3061 | 50.4 | Room | On | 27.9 | 30.6 | 36
45618.3062 | 50.4 | Room | On | 27.9 | 30.6 | 36
45618.3063 | 50.4 | Room | On | 27.9 | 30.6 | 36
45618.3065 | 50.4 | Room | On | 27.9 | 30.6 | 36
45618.3066 | 50.4 | Room | On | 27.7 | 31.1 | 36.4
45618.3067 | 50.4 | Room | On | 27.7 | 31.1 | 36.4
45618.3068 | 50.4 | Room | On | 27.7 | 31.1 | 36.4
45618.3069 | 50.4 | Room | On | 27.7 | 31.1 | 36.4
45618.307 | 50.4 | Room | On | 27.9 | 31.7 | 37
45618.3072 | 50.4 | Room | On | 27.9 | 31.7 | 37
45618.3073 | 50.4 | Room | On | 27.9 | 31.7 | 37
45618.3074 | 50.4 | Room | On | 27.9 | 31.7 | 37
45618.3075 | 50.4 | Room | On | 27.9 | 32.2 | 37.4
45618.3076 | 50.4 | Room | On | 27.9 | 32.2 | 37.4
45618.3077 | 50.4 | Room | On | 27.9 | 32.2 | 37.4
45618.3078 | 50.4 | Room | On | 27.9 | 32.2 | 37.4
45618.308 | 50.4 | Room | On | 28.1 | 32.6 | 38
45618.3081 | 50.4 | Room | On | 28.1 | 32.6 | 38
45618.3082 | 50.4 | Room | On | 28.1 | 32.6 | 38
45618.3083 | 50.4 | Room | On | 28.1 | 32.6 | 38
45618.3084 | 50.4 | Room | On | 28.1 | 33.1 | 38.2
45618.3085 | 50.4 | Room | On | 28.1 | 33.1 | 38.2
45618.3087 | 50.4 | Room | On | 28.1 | 33.1 | 38.2
45618.3088 | 50.4 | Room | On | 28.1 | 33.1 | 38.2
45618.3089 | 50.4 | Room | On | 28.1 | 33.6 | 38.7
45618.309 | 50.4 | Room | On | 28.1 | 33.6 | 38.7
45618.3091 | 50.4 | Room | On | 28.1 | 33.6 | 38.7
45618.3092 | 50.4 | Room | On | 28.1 | 33.6 | 38.7
45618.3094 | 50.5 | Room | On | 28.1 | 33.8 | 39.1
45618.3095 | 50.5 | Room | On | 28.1 | 33.8 | 39.1
45618.3096 | 50.5 | Room | On | 28.1 | 33.8 | 39.1
45618.3097 | 50.5 | Room | On | 28.1 | 33.8 | 39.1
45618.3098 | 50.5 | Room | On | 28.1 | 34.2 | 39.4
45618.3099 | 50.5 | Room | On | 28.1 | 34.2 | 39.4
45618.31 | 50.5 | Room | On | 28.1 | 34.2 | 39.4
45618.3102 | 50.5 | Room | On | 28.1 | 34.2 | 39.4
45618.3103 | 50.4 | Room | On | 28.1 | 35.1 | 40.1
45618.3104 | 50.4 | Room | On | 28.1 | 35.1 | 40.1
45618.3105 | 50.4 | Room | On | 28.1 | 35.1 | 40.1
45618.3106 | 50.4 | Room | On | 28.1 | 35.1 | 40.1
45618.3107 | 50.4 | Room | On | 28.1 | 35.2 | 40.3
45618.3109 | 50.4 | Room | On | 28.1 | 35.2 | 40.3
45618.311 | 50.4 | Room | On | 28.1 | 35.2 | 40.3
45618.3111 | 50.4 | Room | On | 28.1 | 35.2 | 40.3
45618.3112 | 50.4 | Room | On | 28.1 | 35.7 | 40.8
45618.3113 | 50.4 | Room | On | 27.9 | 35.7 | 40.8
45618.3114 | 50.4 | Room | On | 27.9 | 35.7 | 40.8
45618.3116 | 50.4 | Room | On | 27.9 | 35.7 | 40.8
45618.3117 | 50.4 | Room | On | 27.9 | 35.7 | 40.8
45618.3118 | 50.4 | Room | On | 27.9 | 36.1 | 41.1
45618.3119 | 50.4 | Room | On | 27.9 | 36.1 | 41.1
45618.312 | 50.4 | Room | On | 27.9 | 36.1 | 41.1
45618.3121 | 50.4 | Room | On | 27.9 | 36.1 | 41.1
45618.3122 | 50.4 | Room | On | 28.3 | 36.4 | 41.5
45618.3124 | 50.4 | Room | On | 28.3 | 36.4 | 41.5
45618.3125 | 50.4 | Room | On | 28.3 | 36.4 | 41.5
45618.3126 | 50.4 | Room | On | 28.3 | 36.4 | 41.5
45618.3127 | 50.4 | Room | On | 28.1 | 37 | 42.1
45618.3128 | 50.4 | Room | On | 28.1 | 37 | 42.1
45618.3129 | 50.4 | Room | On | 28.1 | 37 | 42.1
45618.3131 | 50.4 | Room | On | 28.1 | 37 | 42.1
45618.3132 | 50.4 | Room | On | 27.9 | 37.4 | 42.4
45618.3133 | 50.4 | Room | On | 27.9 | 37.4 | 42.4
45618.3134 | 50.4 | Room | On | 27.9 | 37.4 | 42.4
45618.3135 | 50.4 | Room | On | 27.9 | 37.4 | 42.4
45618.3136 | 50.4 | Room | On | 27.9 | 37.7 | 42.5
45618.3138 | 50.4 | Room | On | 27.9 | 37.7 | 42.5
45618.3139 | 50.4 | Room | On | 27.9 | 37.7 | 42.5
45618.314 | 50.4 | Room | On | 27.9 | 37.7 | 42.5
45618.3141 | 50.4 | Room | On | 27.5 | 38.1 | 43
45618.3142 | 50.4 | Room | On | 27.5 | 38.1 | 43
45618.3143 | 50.4 | Room | On | 27.5 | 38.1 | 43
45618.3144 | 50.4 | Room | On | 27.5 | 38.1 | 43
45618.3146 | 50.3 | Room | On | 27.9 | 38.5 | 43.5
45618.3147 | 50.3 | Room | On | 27.9 | 38.5 | 43.5
45618.3148 | 50.3 | Room | On | 27.9 | 38.5 | 43.5
45618.3149 | 50.3 | Room | On | 27.9 | 38.5 | 43.5
45618.315 | 50.4 | Room | On | 27.9 | 38.5 | 43.6
45618.3151 | 50.4 | Room | On | 27.9 | 38.5 | 43.6
45618.3153 | 50.4 | Room | On | 27.9 | 38.5 | 43.6
45618.3154 | 50.4 | Room | On | 27.9 | 38.5 | 43.6
45618.3155 | 50.3 | Room | On | 27.9 | 36.8 | 42.2
45618.3156 | 50.3 | Room | On | 27.9 | 36.8 | 42.2
45618.3157 | 50.3 | Room | On | 27.9 | 36.8 | 42.2
45618.3158 | 50.3 | Room | On | 27.9 | 36.8 | 42.2
45618.316 | 50.3 | Room | On | 27.9 | 37.1 | 42.2
45618.3161 | 50.3 | Room | On | 27.9 | 37.1 | 42.2
45618.3162 | 50.3 | Room | On | 27.9 | 37.1 | 42.2
45618.3163 | 50.3 | Room | On | 27.9 | 37.1 | 42.2
45618.3164 | 50.3 | Room | On | 27.9 | 37.8 | 42.8
45618.3165 | 50.3 | Room | On | 27.9 | 37.8 | 42.8
45618.3166 | 50.3 | Room | On | 27.9 | 37.8 | 42.8
45618.3168 | 50.3 | Room | On | 27.9 | 37.8 | 42.8
45618.3169 | 50.3 | Room | On | 28.1 | 38.4 | 43.3
45618.317 | 50.3 | Room | On | 28.1 | 38.4 | 43.3
45618.3171 | 50.3 | Room | On | 28.1 | 38.4 | 43.3
45618.3172 | 50.3 | Room | On | 28.1 | 38.4 | 43.3
45618.3173 | 50.3 | Room | On | 28.1 | 39.1 | 44
45618.3175 | 50.3 | Room | On | 28.1 | 39.1 | 44
45618.3176 | 50.3 | Room | On | 28.1 | 39.1 | 44
45618.3177 | 50.3 | Room | On | 28.1 | 39.1 | 44
45618.3178 | 50.3 | Room | On | 28.1 | 39.5 | 44.8
45618.3179 | 50.3 | Room | On | 28.1 | 39.5 | 44.8
45618.318 | 50.3 | Room | On | 28.1 | 39.5 | 44.8
45618.3182 | 50.3 | Room | On | 28.1 | 39.5 | 44.8
45618.3183 | 50.3 | Room | On | 27.9 | 40.3 | 45.3
45618.3184 | 50.3 | Room | On | 27.9 | 40.3 | 45.3
45618.3185 | 50.3 | Room | On | 27.9 | 40.3 | 45.3
45618.3186 | 50.3 | Room | On | 27.9 | 40.3 | 45.3
45618.3187 | 50.3 | Room | On | 27.9 | 40.8 | 45.8
45618.3188 | 50.3 | Room | On | 27.9 | 40.8 | 45.8
45618.319 | 50.3 | Room | On | 27.9 | 40.8 | 45.8
45618.3191 | 50.3 | Room | On | 27.9 | 40.8 | 45.8
45618.3192 | 50.3 | Room | On | 28.3 | 41.1 | 46.1
45618.3193 | 50.3 | Room | On | 28.3 | 41.1 | 46.1
45618.3194 | 50.3 | Room | On | 28.3 | 41.1 | 46.1
45618.3195 | 50.3 | Room | On | 28.3 | 41.1 | 46.1
45618.3197 | 50.3 | Room | On | 27.9 | 41.5 | 46.8
45618.3198 | 50.3 | Room | On | 27.9 | 41.5 | 46.8
45618.3199 | 50.3 | Room | On | 27.9 | 41.5 | 46.8
45618.32 | 50.3 | Room | On | 27.9 | 41.5 | 46.8
45618.3201 | 50.3 | Room | On | 27.9 | 41.5 | 46.8
45618.3202 | 50.2 | Room | On | 27.9 | 41.8 | 47.2
45618.3204 | 50.2 | Room | On | 27.9 | 41.8 | 47.2
45618.3205 | 50.2 | Room | On | 27.9 | 41.8 | 47.2
45618.3206 | 50.2 | Room | On | 27.9 | 41.8 | 47.2
45618.3207 | 50.2 | Room | On | 27.9 | 42.2 | 47.5
45618.3208 | 50.2 | Room | On | 27.9 | 42.2 | 47.5
45618.3209 | 50.2 | Room | On | 27.9 | 42.2 | 47.5
45618.321 | 50.2 | Room | On | 27.9 | 42.2 | 47.5
45618.3212 | 50.2 | Room | On | 28.1 | 42.7 | 47.5
45618.3213 | 50.2 | Room | On | 28.1 | 42.7 | 47.5
45618.3214 | 50.2 | Room | On | 28.1 | 42.7 | 47.5
45618.3215 | 50.2 | Room | On | 28.1 | 42.7 | 47.5
45618.3216 | 50.2 | Room | On | 28.1 | 42.8 | 47.6
45618.3217 | 50.2 | Room | On | 28.1 | 42.8 | 47.6
45618.3219 | 50.2 | Room | On | 28.1 | 42.8 | 47.6
45618.322 | 50.2 | Room | On | 28.1 | 42.8 | 47.6
45618.3221 | 50.2 | Room | On | 27.7 | 43.1 | 47.8
45618.3222 | 50.2 | Room | On | 27.7 | 43.1 | 47.8
45618.3223 | 50.2 | Room | On | 27.7 | 43.1 | 47.8
45618.3224 | 50.2 | Room | On | 27.7 | 43.1 | 47.8
45618.3226 | 50.2 | Room | On | 27.5 | 43.6 | 48.6
45618.3227 | 50.2 | Room | On | 27.5 | 43.6 | 48.6
45618.3228 | 50.2 | Room | On | 27.5 | 43.6 | 48.6
45618.3229 | 50.2 | Room | On | 27.5 | 43.6 | 48.6
45618.323 | 50.2 | Room | On | 27.9 | 42.7 | 47.6
45618.3231 | 50.2 | Room | On | 27.9 | 42.7 | 47.6
45618.3232 | 50.2 | Room | On | 27.9 | 42.7 | 47.6
45618.3234 | 50.2 | Room | On | 27.9 | 42.7 | 47.6
45618.3235 | 50.2 | Room | On | 27.9 | 42.5 | 47.3
45618.3236 | 50.2 | Room | On | 27.9 | 42.5 | 47.3
45618.3237 | 50.2 | Room | On | 27.9 | 42.5 | 47.3
45618.3238 | 50.2 | Room | On | 27.9 | 42.5 | 47.3
45618.3239 | 50.2 | Room | On | 27.9 | 42.1 | 47.1
45618.3241 | 50.2 | Room | On | 27.9 | 42.1 | 47.1
45618.3242 | 50.2 | Room | On | 27.9 | 42.1 | 47.1
45618.3243 | 50.2 | Room | On | 27.9 | 42.1 | 47.1
45618.3244 | 50.3 | Room | On | 27.9 | 42 | 47.3
45618.3245 | 50.3 | Room | On | 27.9 | 42 | 47.3
45618.3246 | 50.3 | Room | On | 27.9 | 42 | 47.3
45618.3248 | 50.3 | Room | On | 27.9 | 42 | 47.3
45618.3249 | 50.3 | Room | On | 27.7 | 42.4 | 47.6
45618.325 | 50.3 | Room | On | 27.7 | 42.4 | 47.6
45618.3251 | 50.3 | Room | On | 27.7 | 42.4 | 47.6
45618.3252 | 50.3 | Room | On | 27.7 | 42.4 | 47.6
45618.3253 | 50.2 | Room | On | 28.1 | 42.1 | 47.6
45618.3254 | 50.2 | Room | On | 28.1 | 42.1 | 47.6
45618.3256 | 50.2 | Room | On | 28.1 | 42.1 | 47.6
45618.3257 | 50.2 | Room | On | 28.1 | 42.1 | 47.6
45618.3258 | 50.2 | Room | On | 28.3 | 42.5 | 47.7
45618.3259 | 50.2 | Room | On | 28.3 | 42.5 | 47.7
45618.326 | 50.2 | Room | On | 28.3 | 42.5 | 47.7
45618.3261 | 50.2 | Room | On | 28.3 | 42.5 | 47.7
45618.3263 | 50.2 | Room | On | 28.3 | 42.8 | 48
45618.3264 | 50.2 | Room | On | 28.3 | 42.8 | 48
45618.3265 | 50.2 | Room | On | 28.3 | 42.8 | 48
45618.3266 | 50.2 | Room | On | 28.3 | 42.8 | 48
45618.3267 | 50.2 | Room | On | 28.1 | 43.3 | 48.6
45618.3268 | 50.2 | Room | On | 28.1 | 43.3 | 48.6
45618.3269 | 50.2 | Room | On | 28.1 | 43.3 | 48.6
45618.3271 | 50.2 | Room | On | 28.1 | 43.3 | 48.6
45618.3272 | 50.2 | Room | On | 28.1 | 43.6 | 49
45618.3273 | 50.2 | Room | On | 28.1 | 43.6 | 49
45618.3274 | 50.2 | Room | On | 28.1 | 43.6 | 49
45618.3275 | 50.2 | Room | On | 28.1 | 43.6 | 49
45618.3276 | 50.2 | Room | On | 28.1 | 43.8 | 48.6
45618.3277 | 50.2 | Room | On | 28.1 | 43.8 | 48.6
45618.3279 | 50.2 | Room | On | 28.1 | 43.8 | 48.6
45618.328 | 50.2 | Room | On | 28.1 | 43.8 | 48.6
45618.3281 | 50.2 | Room | On | 28.1 | 44.6 | 48.6
45618.3282 | 50.2 | Room | On | 28.1 | 44.6 | 48.6
45618.3283 | 50.2 | Room | On | 28.1 | 44.6 | 48.6
45618.3284 | 50.2 | Room | On | 28.1 | 44.6 | 48.6
45618.3286 | 50.2 | Room | On | 27.5 | 45 | 49
45618.3287 | 50.2 | Room | On | 27.5 | 45 | 49
45618.3288 | 50.2 | Room | On | 27.5 | 45 | 49
45618.3289 | 50.2 | Room | On | 27.5 | 45 | 49
45618.329 | 50.2 | Room | On | 27.5 | 45 | 49
45618.3291 | 50.2 | Room | On | 27.7 | 45.1 | 49.2
45618.3293 | 50.2 | Room | On | 27.7 | 45.1 | 49.2
45618.3294 | 50.2 | Room | On | 27.7 | 45.1 | 49.2
45618.3295 | 50.2 | Room | On | 27.7 | 45.1 | 49.2
45618.3296 | 50.3 | Room | On | 28.1 | 45.5 | 49.2
45618.3297 | 50.3 | Room | On | 28.1 | 45.5 | 49.2
45618.3298 | 50.3 | Room | On | 28.1 | 45.5 | 49.2
45618.3299 | 50.3 | Room | On | 28.1 | 45.5 | 49.2
45618.3301 | 50.2 | Room | On | 28.3 | 45.6 | 49
45618.3302 | 50.2 | Room | On | 28.3 | 45.6 | 49
45618.3303 | 50.2 | Room | On | 28.3 | 45.6 | 49
45618.3304 | 50.2 | Room | On | 28.3 | 45.6 | 49
45618.3305 | 50.2 | Room | On | 28.1 | 45.8 | 49.4
45618.3306 | 50.2 | Room | On | 28.1 | 45.8 | 49.4
45618.3308 | 50.2 | Room | On | 28.1 | 45.8 | 49.4
45618.3309 | 50.2 | Room | On | 28.1 | 45.8 | 49.4
45618.331 | 50.2 | Room | On | 28.1 | 45.8 | 49.2
45618.3311 | 50.2 | Room | On | 28.1 | 45.8 | 49.2
45618.3312 | 50.2 | Room | On | 28.1 | 45.8 | 49.2
45618.3313 | 50.2 | Room | On | 28.1 | 45.8 | 49.2
45618.3315 | 50.2 | Room | On | 28.1 | 45.8 | 49.4
45618.3316 | 50.2 | Room | On | 28.1 | 45.8 | 49.4
45618.3317 | 50.2 | Room | On | 28.1 | 45.8 | 49.4
45618.3318 | 50.2 | Room | On | 28.1 | 45.8 | 49.4
45618.3319 | 50.2 | Room | On | 28.1 | 46 | 49.4
45618.332 | 50.2 | Room | On | 28.1 | 46 | 49.4
45618.3321 | 50.2 | Room | On | 28.1 | 46 | 49.4
45618.3323 | 50.2 | Room | On | 28.1 | 46 | 49.4
45618.3324 | 50.2 | Room | On | 27.9 | 46.1 | 49.6
45618.3325 | 50.2 | Room | On | 27.9 | 46.1 | 49.6
45618.3326 | 50.2 | Room | On | 27.9 | 46.1 | 49.6
45618.3327 | 50.2 | Room | On | 27.9 | 46.1 | 49.6
45618.3328 | 50.2 | Room | On | 28.1 | 46.1 | 49.8
45618.333 | 50.2 | Room | On | 28.1 | 46.1 | 49.8
45618.3331 | 50.2 | Room | On | 28.1 | 46.1 | 49.8
45618.3332 | 50.2 | Room | On | 28.1 | 46.1 | 49.8
45618.3333 | 50.3 | Room | On | 28.1 | 46.1 | 49.6
45618.3334 | 50.3 | Room | On | 28.1 | 46.1 | 49.6
45618.3335 | 50.3 | Room | On | 28.1 | 46.1 | 49.6
45618.3337 | 50.3 | Room | On | 28.1 | 46.1 | 49.6
45618.3338 | 50.3 | Room | On | 27.9 | 46.3 | 49.6
45618.3339 | 50.3 | Room | On | 27.9 | 46.3 | 49.6
45618.334 | 50.3 | Room | On | 27.9 | 46.3 | 49.6
45618.3341 | 50.3 | Room | On | 27.9 | 46.3 | 49.6
45618.3342 | 50.3 | Room | On | 28.1 | 46.5 | 49.8
45618.3343 | 50.3 | Room | On | 28.1 | 46.5 | 49.8
45618.3345 | 50.3 | Room | On | 28.1 | 46.5 | 49.8
45618.3346 | 50.3 | Room | On | 28.1 | 46.5 | 49.8
45618.3347 | 50.3 | Room | On | 28.1 | 46.5 | 49.8
45618.3348 | 50.3 | Room | On | 28.1 | 46.5 | 49.8
45618.3349 | 50.3 | Room | On | 28.1 | 46.5 | 49.8
45618.335 | 50.3 | Room | On | 28.1 | 46.5 | 49.8
45618.3352 | 50.3 | Room | On | 27.9 | 46.6 | 49.8
45618.3353 | 50.3 | Room | On | 27.9 | 46.6 | 49.8
45618.3354 | 50.3 | Room | On | 27.9 | 46.6 | 49.8
45618.3355 | 50.3 | Room | On | 27.9 | 46.6 | 49.8
45618.3356 | 50.2 | Room | On | 28.1 | 46.6 | 49.8
45618.3357 | 50.2 | Room | On | 28.1 | 46.6 | 49.8
45618.3359 | 50.2 | Room | On | 28.1 | 46.6 | 49.8
45618.336 | 50.2 | Room | On | 28.1 | 46.6 | 49.8
45618.3361 | 50.3 | Room | On | 28.1 | 46.6 | 50
45618.3362 | 50.3 | Room | On | 28.1 | 46.6 | 50
45618.3363 | 50.3 | Room | On | 28.1 | 46.6 | 50
45618.3364 | 50.3 | Room | On | 28.1 | 46.6 | 50
45618.3365 | 50.3 | Room | On | 28.1 | 46.8 | 50.2
45618.3367 | 50.3 | Room | On | 28.1 | 46.8 | 50.2
45618.3368 | 50.3 | Room | On | 28.1 | 46.8 | 50.2
45618.3369 | 50.3 | Room | On | 28.1 | 46.8 | 50.2
45618.337 | 50.3 | Room | On | 28.1 | 46.8 | 50.2
45618.3371 | 50.2 | Room | On | 27.9 | 46.8 | 50
45618.3372 | 50.2 | Room | On | 27.9 | 46.8 | 50
45618.3374 | 50.2 | Room | On | 27.9 | 46.8 | 50
45618.3375 | 50.2 | Room | On | 27.9 | 46.8 | 50
45618.3376 | 50.2 | Room | On | 28.3 | 47 | 50.2
45618.3377 | 50.2 | Room | On | 28.3 | 47 | 50.2
45618.3378 | 50.2 | Room | On | 28.3 | 47 | 50.2
45618.3379 | 50.2 | Room | On | 28.3 | 47 | 50.2
45618.3381 | 50.2 | Room | On | 27.9 | 47 | 50.2
45618.3382 | 50.2 | Room | On | 27.9 | 47 | 50.2
45618.3383 | 50.2 | Room | On | 27.9 | 47 | 50.2
45618.3384 | 50.2 | Room | On | 27.9 | 47 | 50.2
45618.3385 | 50.2 | Room | On | 27.9 | 47 | 50.2
45618.3386 | 50.2 | Room | On | 27.9 | 47 | 50.2
45618.3387 | 50.2 | Room | On | 27.9 | 47 | 50.2
45618.3389 | 50.2 | Room | On | 27.9 | 47 | 50.2
45618.339 | 50.3 | Room | On | 28.1 | 47.1 | 50.4
45618.3391 | 50.3 | Room | On | 28.1 | 47.1 | 50.4
45618.3392 | 50.3 | Room | On | 28.1 | 47.1 | 50.4
45618.3393 | 50.3 | Room | On | 28.1 | 47.1 | 50.4
45618.3394 | 50.3 | Room | On | 28.1 | 47.1 | 50.2
45618.3396 | 50.3 | Room | On | 28.1 | 47.1 | 50.2
45618.3397 | 50.3 | Room | On | 28.1 | 47.1 | 50.2
45618.3398 | 50.3 | Room | On | 28.1 | 47.1 | 50.2
45618.3399 | 50.3 | Room | On | 27.9 | 47.1 | 50.4
45618.34 | 50.3 | Room | On | 27.9 | 47.1 | 50.4
45618.3401 | 50.3 | Room | On | 27.9 | 47.1 | 50.4
45618.3403 | 50.3 | Room | On | 27.9 | 47.1 | 50.4
45618.3404 | 50.2 | Room | On | 27.9 | 47.1 | 50.4
45618.3405 | 50.2 | Room | On | 27.9 | 47.1 | 50.4
45618.3406 | 50.2 | Room | On | 27.9 | 47.1 | 50.4
45618.3407 | 50.2 | Room | On | 27.9 | 47.1 | 50.4
45618.3408 | 50.2 | Room | On | 28.1 | 47.2 | 50.4
45618.3409 | 50.2 | Room | On | 28.1 | 47.2 | 50.4
45618.3411 | 50.2 | Room | On | 28.1 | 47.2 | 50.4
45618.3412 | 50.2 | Room | On | 28.1 | 47.2 | 50.4
45618.3413 | 50.2 | Room | On | 28.1 | 47.2 | 50.6
45618.3414 | 50.2 | Room | On | 28.1 | 47.2 | 50.6
45618.3415 | 50.2 | Room | On | 28.1 | 47.2 | 50.6
45618.3416 | 50.2 | Room | On | 28.1 | 47.2 | 50.6
45618.3418 | 50.2 | Room | On | 28.3 | 47.2 | 50.6
45618.3419 | 50.2 | Room | On | 28.3 | 47.2 | 50.6
45618.342 | 50.2 | Room | On | 28.3 | 47.2 | 50.6
45618.3421 | 50.2 | Room | On | 28.3 | 47.2 | 50.6
45618.3422 | 50.2 | Room | On | 28.1 | 47.3 | 50.6
45618.3423 | 50.2 | Room | On | 28.1 | 47.3 | 50.6
45618.3425 | 50.2 | Room | On | 28.1 | 47.3 | 50.6
45618.3426 | 50.2 | Room | On | 28.1 | 47.3 | 50.6
45618.3427 | 50.2 | Room | On | 28.1 | 47.5 | 50.6
45618.3428 | 50.2 | Room | On | 28.1 | 47.5 | 50.6
45618.3429 | 50.2 | Room | On | 28.1 | 47.5 | 50.6
45618.343 | 50.2 | Room | On | 28.1 | 47.5 | 50.6
45618.3431 | 50.2 | Room | On | 27.9 | 47.3 | 50.8
45618.3433 | 50.2 | Room | On | 27.9 | 47.3 | 50.8
45618.3434 | 50.2 | Room | On | 27.9 | 47.3 | 50.8
45618.3435 | 50.2 | Room | On | 27.9 | 47.3 | 50.8
45618.3436 | 50.2 | Room | On | 28.1 | 47.6 | 51
45618.3437 | 50.2 | Room | On | 28.1 | 47.6 | 51
45618.3438 | 50.2 | Room | On | 28.1 | 47.6 | 51
45618.344 | 50.2 | Room | On | 28.1 | 47.6 | 51
45618.3441 | 50.2 | Room | On | 27.7 | 47.6 | 50.8
45618.3442 | 50.2 | Room | On | 27.7 | 47.6 | 50.8
45618.3443 | 50.2 | Room | On | 27.7 | 47.6 | 50.8
45618.3444 | 50.2 | Room | On | 27.7 | 47.6 | 50.8
45618.3445 | 50.2 | Room | On | 28.1 | 47.6 | 50.6
45618.3447 | 50.2 | Room | On | 28.1 | 47.6 | 50.6
45618.3448 | 50.2 | Room | On | 28.1 | 47.6 | 50.6
45618.3449 | 50.2 | Room | On | 28.1 | 47.6 | 50.6
45618.345 | 50.2 | Room | On | 27.9 | 47.7 | 50.6
45618.3451 | 50.2 | Room | On | 27.9 | 47.7 | 50.6
45618.3452 | 50.2 | Room | On | 27.9 | 47.7 | 50.6
45618.3453 | 50.2 | Room | On | 27.9 | 47.7 | 50.6
45618.3455 | 50.2 | Room | On | 27.9 | 47.7 | 50.6
45618.3456 | 50.2 | Room | On | 27.9 | 47.7 | 50.6
45618.3457 | 50.2 | Room | On | 27.9 | 47.7 | 50.6
45618.3458 | 50.2 | Room | On | 27.9 | 47.7 | 50.6
45618.3459 | 50.2 | Room | On | 27.9 | 47.7 | 50.6
45618.346 | 50.2 | Room | On | 28.1 | 47.7 | 50.6
45618.3462 | 50.2 | Room | On | 28.1 | 47.7 | 50.6
45618.3463 | 50.2 | Room | On | 28.1 | 47.7 | 50.6
45618.3464 | 50.2 | Room | On | 28.1 | 47.7 | 50.6
45618.3465 | 50.2 | Room | On | 28.1 | 47.7 | 50.6
45618.3466 | 50.2 | Room | On | 28.1 | 47.7 | 50.6
45618.3467 | 50.2 | Room | On | 28.1 | 47.7 | 50.6
45618.3469 | 50.2 | Room | On | 28.1 | 47.7 | 50.6
45618.347 | 50.2 | Room | On | 28.3 | 47.8 | 50.6
45618.3471 | 50.2 | Room | On | 28.3 | 47.8 | 50.6
45618.3472 | 50.2 | Room | On | 28.3 | 47.8 | 50.6
45618.3473 | 50.2 | Room | On | 28.3 | 47.8 | 50.6
45618.3474 | 50.2 | Room | On | 28.5 | 47.7 | 50.6
45618.3475 | 50.2 | Room | On | 28.5 | 47.7 | 50.6
45618.3477 | 50.2 | Room | On | 28.5 | 47.7 | 50.6
45618.3478 | 50.2 | Room | On | 28.5 | 47.7 | 50.6
45618.3479 | 50.2 | Room | On | 27.9 | 47.8 | 50.6
45618.348 | 50.2 | Room | On | 27.9 | 47.8 | 50.6
45618.3481 | 50.2 | Room | On | 27.9 | 47.8 | 50.6
45618.3482 | 50.2 | Room | On | 27.9 | 47.8 | 50.6
45618.3484 | 50.2 | Room | On | 28.1 | 47.8 | 50.6
45618.3485 | 50.2 | Room | On | 28.1 | 47.8 | 50.6
45618.3486 | 50.2 | Room | On | 28.1 | 47.8 | 50.6
45618.3487 | 50.2 | Room | On | 28.1 | 47.8 | 50.6
45618.3488 | 50.2 | Room | On | 27.9 | 47.8 | 50.8
45618.3489 | 50.2 | Room | On | 27.9 | 47.8 | 50.8
45618.3491 | 50.2 | Room | On | 27.9 | 47.8 | 50.8
45618.3492 | 50.2 | Room | On | 27.9 | 47.8 | 50.8
45618.3493 | 50.2 | Room | On | 27.9 | 47.7 | 50.6
45618.3494 | 50.2 | Room | On | 27.9 | 47.7 | 50.6
45618.3495 | 50.2 | Room | On | 27.9 | 47.7 | 50.6
45618.3496 | 50.2 | Room | On | 27.9 | 47.7 | 50.6
45618.3497 | 50.2 | Room | On | 27.7 | 47.8 | 50.6
45618.3499 | 50.2 | Room | On | 27.7 | 47.8 | 50.6
45618.35 | 50.2 | Room | On | 27.7 | 47.8 | 50.6
45618.3501 | 50.2 | Room | On | 27.7 | 47.8 | 50.6
45618.3502 | 50.2 | Room | On | 27.9 | 47.8 | 50.6
45618.3503 | 50.2 | Room | On | 27.9 | 47.8 | 50.6
45618.3504 | 50.2 | Room | On | 27.9 | 47.8 | 50.6
45618.3506 | 50.2 | Room | On | 27.9 | 47.8 | 50.6
45618.3507 | 50.1 | Room | On | 27.9 | 48 | 50.8
45618.3508 | 50.1 | Room | On | 27.9 | 48 | 50.8
45618.3509 | 50.1 | Room | On | 27.9 | 48 | 50.8
45618.351 | 50.1 | Room | On | 27.9 | 48 | 50.8
45618.3511 | 50.1 | Room | On | 28.3 | 47.8 | 50.6
45618.3512 | 50.1 | Room | On | 28.3 | 47.8 | 50.6
45618.3514 | 50.1 | Room | On | 28.3 | 47.8 | 50.6
45618.3515 | 50.1 | Room | On | 28.3 | 47.8 | 50.6
45618.3516 | 50.1 | Room | On | 28.1 | 47.7 | 50.4
45618.3517 | 50.1 | Room | On | 28.1 | 47.7 | 50.4
45618.3518 | 50.1 | Room | On | 28.1 | 47.7 | 50.4
45618.3519 | 50.1 | Room | On | 28.1 | 47.7 | 50.4
45618.3521 | 50.1 | Room | On | 28.1 | 47.8 | 50.6
45618.3522 | 50.1 | Room | On | 28.1 | 47.8 | 50.6
45618.3523 | 50.1 | Room | On | 28.1 | 47.8 | 50.6
45618.3524 | 50.1 | Room | On | 28.1 | 47.8 | 50.6
45618.3525 | 50.1 | Room | On | 27.9 | 47.8 | 50.8
45618.3526 | 50.1 | Room | On | 27.9 | 47.8 | 50.8
45618.3528 | 50.1 | Room | On | 27.9 | 47.8 | 50.8
45618.3529 | 50.1 | Room | On | 27.9 | 47.8 | 50.8
45618.353 | 50.1 | Room | On | 28.3 | 47.8 | 50.6
45618.3531 | 50.1 | Room | On | 28.3 | 47.8 | 50.6
45618.3532 | 50.1 | Room | On | 28.3 | 47.8 | 50.6
45618.3533 | 50.1 | Room | On | 28.3 | 47.8 | 50.6
45618.3534 | 50.1 | Room | On | 28.1 | 47.8 | 50.6
45618.3536 | 50.1 | Room | On | 28.1 | 47.8 | 50.6
45618.3537 | 50.1 | Room | On | 28.1 | 47.8 | 50.6
45618.3538 | 50.1 | Room | On | 28.1 | 47.8 | 50.6
45618.3539 | 50.2 | Room | On | 28.1 | 47.8 | 50.6
45618.354 | 50.2 | Room | On | 28.3 | 47.8 | 50.6
45618.3541 | 50.2 | Room | On | 28.3 | 47.8 | 50.6
45618.3543 | 50.2 | Room | On | 28.3 | 47.8 | 50.6
45618.3544 | 50.2 | Room | On | 28.3 | 47.8 | 50.6
45618.3545 | 50.2 | Room | On | 28.3 | 47.8 | 50.6
45618.3546 | 50.2 | Room | On | 28.3 | 47.8 | 50.6
45618.3547 | 50.2 | Room | On | 28.3 | 47.8 | 50.6
45618.3548 | 50.2 | Room | On | 28.3 | 47.8 | 50.6
45618.355 | 50.2 | Room | On | 28.1 | 47.8 | 50.8
45618.3551 | 50.2 | Room | On | 28.1 | 47.8 | 50.8
45618.3552 | 50.2 | Room | On | 28.1 | 47.8 | 50.8
45618.3553 | 50.2 | Room | On | 28.1 | 47.8 | 50.8
45618.3554 | 50.2 | Room | On | 27.9 | 48 | 51
45618.3555 | 50.2 | Room | On | 27.9 | 48 | 51
45618.3556 | 50.2 | Room | On | 27.9 | 48 | 51
45618.3558 | 50.2 | Room | On | 27.9 | 48 | 51
45618.3559 | 50.2 | Room | On | 28.3 | 48 | 50.8
45618.356 | 50.2 | Room | On | 28.3 | 48 | 50.8
45618.3561 | 50.2 | Room | On | 28.3 | 48 | 50.8
45618.3562 | 50.2 | Room | On | 28.3 | 48 | 50.8
45618.3563 | 50.2 | Room | On | 28.1 | 48 | 50.8
45618.3565 | 50.2 | Room | On | 28.1 | 48 | 50.8
45618.3566 | 50.2 | Room | On | 28.1 | 48 | 50.8
45618.3567 | 50.2 | Room | On | 28.1 | 48 | 50.8
45618.3568 | 50.2 | Room | On | 28.1 | 48.3 | 50.8
45618.3569 | 50.2 | Room | On | 28.1 | 48.3 | 50.8
45618.357 | 50.2 | Room | On | 28.1 | 48.3 | 50.8
45618.3572 | 50.2 | Room | On | 28.1 | 48.3 | 50.8
45618.3573 | 50.1 | Room | On | 27.9 | 48 | 50.8
45618.3574 | 50.1 | Room | On | 27.9 | 48 | 50.8
45618.3575 | 50.1 | Room | On | 27.9 | 48 | 50.8
45618.3576 | 50.1 | Room | On | 27.9 | 48 | 50.8
45618.3577 | 50.1 | Room | On | 27.9 | 48 | 50.8
45618.3578 | 50.1 | Room | On | 27.9 | 48 | 50.8
45618.358 | 50.1 | Room | On | 27.9 | 48 | 50.8
45618.3581 | 50.1 | Room | On | 27.9 | 48 | 50.8
45618.3582 | 50.1 | Room | On | 28.1 | 48.3 | 50.8
45618.3583 | 50.1 | Room | On | 28.1 | 48.3 | 50.8
45618.3584 | 50.1 | Room | On | 28.1 | 48.3 | 50.8
45618.3585 | 50.1 | Room | On | 28.1 | 48.3 | 50.8
45618.3587 | 50.1 | Room | On | 27.9 | 48.3 | 50.8
45618.3588 | 50.1 | Room | On | 27.9 | 48.3 | 50.8
45618.3589 | 50.1 | Room | On | 27.9 | 48.3 | 50.8
45618.359 | 50.1 | Room | On | 27.9 | 48.3 | 50.8
45618.3591 | 50 | Room | On | 28.1 | 48.3 | 50.8
45618.3592 | 50 | Room | On | 28.1 | 48.3 | 50.8
45618.3594 | 50 | Room | On | 28.1 | 48.3 | 50.8
45618.3595 | 50 | Room | On | 28.1 | 48.3 | 50.8
45618.3596 | 50 | Room | On | 28.1 | 48.3 | 50.6
45618.3597 | 50 | Room | On | 28.1 | 48.3 | 50.6
45618.3598 | 50 | Room | On | 28.1 | 48.3 | 50.6
45618.3599 | 50 | Room | On | 28.1 | 48.3 | 50.6
45618.36 | 50 | Room | On | 27.9 | 48.3 | 50.6
45618.3602 | 50 | Room | On | 27.9 | 48.3 | 50.6
45618.3603 | 50 | Room | On | 27.9 | 48.3 | 50.6
45618.3604 | 50 | Room | On | 27.9 | 48.3 | 50.6
45618.3605 | 50 | Room | On | 28.3 | 48.3 | 50.6
45618.3606 | 50 | Room | On | 28.3 | 48.3 | 50.6
45618.3607 | 50 | Room | On | 28.3 | 48.3 | 50.6
45618.3609 | 50 | Room | On | 28.3 | 48.3 | 50.6
45618.361 | 50 | Room | On | 28.1 | 48.3 | 50.6
45618.3611 | 50 | Room | On | 28.1 | 48.3 | 50.6
45618.3612 | 50 | Room | On | 28.1 | 48.3 | 50.6
45618.3613 | 50 | Room | On | 28.1 | 48.3 | 50.6
45618.3614 | 50 | Room | On | 28.1 | 48 | 50.4
45618.3616 | 50 | Room | On | 28.1 | 48 | 50.4
45618.3617 | 50 | Room | On | 28.1 | 48 | 50.4
45618.3618 | 50 | Room | On | 28.1 | 48 | 50.4
45618.3619 | 50 | Room | On | 28.3 | 48.3 | 50.6
45618.362 | 50 | Room | On | 28.3 | 48.3 | 50.6
45618.3621 | 50 | Room | On | 28.3 | 48.3 | 50.6
45618.3622 | 50 | Room | On | 28.3 | 48.3 | 50.6
45618.3624 | 50 | Room | On | 28.1 | 48.3 | 50.6
45618.3625 | 50 | Room | On | 28.1 | 48.3 | 50.6
45618.3626 | 50 | Room | On | 28.1 | 48.3 | 50.6
45618.3627 | 50 | Room | On | 28.1 | 48.3 | 50.6
45618.3628 | 50 | Room | On | 28.1 | 48.3 | 50.6
45618.3629 | 50 | Room | On | 28.1 | 48 | 50.4
45618.3631 | 50 | Room | On | 28.1 | 48 | 50.4
45618.3632 | 50 | Room | On | 28.1 | 48 | 50.4
45618.3633 | 50 | Room | On | 28.1 | 48 | 50.4
45618.3634 | 50 | Room | On | 27.9 | 48 | 50.4
45618.3635 | 50 | Room | On | 27.9 | 48 | 50.4
45618.3636 | 50 | Room | On | 27.9 | 48 | 50.4
45618.3638 | 50 | Room | On | 27.9 | 48 | 50.4
45618.3639 | 50 | Room | On | 28.3 | 48 | 50.4
45618.364 | 50 | Room | On | 28.3 | 48 | 50.4
45618.3641 | 50 | Room | On | 28.3 | 48 | 50.4
45618.3642 | 50 | Room | On | 28.3 | 48 | 50.4
45618.3643 | 50 | Room | On | 28.5 | 48 | 50.6
45618.3644 | 50 | Room | On | 28.5 | 48 | 50.6
45618.3646 | 50 | Room | On | 28.5 | 48 | 50.6
45618.3647 | 50 | Room | On | 28.5 | 48 | 50.6
45618.3648 | 50 | Room | On | 27.9 | 48 | 50.4
45618.3649 | 50 | Room | On | 27.9 | 48 | 50.4
45618.365 | 50 | Room | On | 27.9 | 48 | 50.4
45618.3651 | 50 | Room | On | 27.9 | 48 | 50.4
45618.3653 | 50 | Room | On | 28.1 | 47.8 | 50.2
45618.3654 | 50 | Room | On | 28.1 | 47.8 | 50.2
45618.3655 | 50 | Room | On | 28.1 | 47.8 | 50.2
45618.3656 | 50 | Room | On | 28.1 | 47.8 | 50.2
45618.3657 | 50 | Room | On | 28.3 | 47.8 | 50.4
45618.3658 | 50 | Room | On | 28.3 | 47.8 | 50.4
45618.366 | 50 | Room | On | 28.3 | 47.8 | 50.4
45618.3661 | 50 | Room | On | 28.3 | 47.8 | 50.4
45618.3662 | 50 | Room | On | 28.1 | 48 | 50.4
45618.3663 | 50 | Room | On | 28.1 | 48 | 50.4
45618.3664 | 50 | Room | On | 28.1 | 48 | 50.4
45618.3665 | 50 | Room | On | 28.1 | 48 | 50.4
45618.3666 | 49.9 | Room | On | 28.1 | 47.8 | 50.2
45618.3668 | 49.9 | Room | On | 28.1 | 47.8 | 50.2
45618.3669 | 49.9 | Room | On | 28.1 | 47.8 | 50.2
45618.367 | 49.9 | Room | On | 28.1 | 47.8 | 50.2
45618.3671 | 49.9 | Room | On | 28.1 | 47.8 | 50.4
45618.3672 | 49.9 | Room | On | 28.1 | 47.8 | 50.4
45618.3673 | 49.9 | Room | On | 28.1 | 47.8 | 50.4
45618.3675 | 49.9 | Room | On | 28.1 | 47.8 | 50.4
45618.3676 | 49.9 | Room | On | 28.3 | 47.7 | 50.2
45618.3677 | 49.9 | Room | On | 28.3 | 47.7 | 50.2
45618.3678 | 49.9 | Room | On | 28.3 | 47.7 | 50.2
45618.3679 | 49.9 | Room | On | 28.3 | 47.7 | 50.2
45618.368 | 49.9 | Room | On | 28.1 | 47.8 | 50.4
45618.3682 | 49.9 | Room | On | 28.1 | 47.8 | 50.4
45618.3683 | 49.9 | Room | On | 28.1 | 47.8 | 50.4
45618.3684 | 49.9 | Room | On | 28.1 | 47.8 | 50.4
45618.3685 | 49.9 | Room | On | 28.3 | 47.7 | 50.4
45618.3686 | 49.9 | Room | On | 28.3 | 47.7 | 50.4
45618.3687 | 49.9 | Room | On | 28.3 | 47.7 | 50.4
45618.3688 | 49.9 | Room | On | 28.3 | 47.7 | 50.4
45618.369 | 49.9 | Room | On | 27.9 | 47.7 | 50.2
45618.3691 | 49.9 | Room | On | 27.9 | 47.7 | 50.2
45618.3692 | 49.9 | Room | On | 27.9 | 47.7 | 50.2
45618.3693 | 49.9 | Room | On | 27.9 | 47.7 | 50.2
45618.3694 | 49.9 | Room | On | 28.1 | 47.7 | 50.2
45618.3695 | 49.9 | Room | On | 28.1 | 47.7 | 50.2
45618.3697 | 49.9 | Room | On | 28.1 | 47.7 | 50.2
45618.3698 | 49.9 | Room | On | 28.1 | 47.7 | 50.2
45618.3699 | 49.9 | Room | On | 28.1 | 47.7 | 50.2
45618.37 | 49.9 | Room | On | 28.1 | 47.7 | 50.2
45618.3701 | 49.9 | Room | On | 28.1 | 47.7 | 50.2
45618.3702 | 49.9 | Room | On | 28.1 | 47.7 | 50.2
45618.3704 | 49.8 | Room | On | 28.1 | 47.7 | 50.2
45618.3705 | 49.8 | Room | On | 28.1 | 47.7 | 50.2
45618.3706 | 49.8 | Room | On | 28.1 | 47.7 | 50.2
45618.3707 | 49.8 | Room | On | 28.1 | 47.7 | 50.2
45618.3708 | 49.8 | Room | On | 28.1 | 47.7 | 50.2
45618.3709 | 49.8 | Room | On | 28.1 | 47.7 | 50.2
45618.371 | 49.8 | Room | On | 28.1 | 47.7 | 50.2
45618.3712 | 49.8 | Room | On | 28.1 | 47.7 | 50.2
45618.3713 | 49.8 | Room | On | 28.1 | 47.7 | 50.2
45618.3714 | 49.8 | Room | On | 28.1 | 47.6 | 50.2
45618.3715 | 49.8 | Room | On | 28.1 | 47.6 | 50.2
45618.3716 | 49.8 | Room | On | 28.1 | 47.6 | 50.2
45618.3717 | 49.8 | Room | On | 28.1 | 47.6 | 50.2
45618.3719 | 49.8 | Room | On | 28.1 | 47.6 | 50
45618.372 | 49.8 | Room | On | 28.1 | 47.6 | 50
45618.3721 | 49.8 | Room | On | 28.1 | 47.6 | 50
45618.3722 | 49.8 | Room | On | 28.1 | 47.6 | 50
45618.3723 | 49.8 | Room | On | 27.9 | 47.5 | 50
45618.3724 | 49.8 | Room | On | 27.9 | 47.5 | 50
45618.3726 | 49.8 | Room | On | 27.9 | 47.5 | 50
45618.3727 | 49.8 | Room | On | 27.9 | 47.5 | 50
45618.3728 | 49.8 | Room | On | 28.1 | 47.6 | 50.2
45618.3729 | 49.8 | Room | On | 28.1 | 47.6 | 50.2
45618.373 | 49.8 | Room | On | 28.1 | 47.6 | 50.2
45618.3731 | 49.8 | Room | On | 28.1 | 47.6 | 50.2
45618.3732 | 49.8 | Room | On | 28.1 | 47.3 | 49.8
45618.3734 | 49.8 | Room | On | 28.1 | 47.3 | 49.8
45618.3735 | 49.8 | Room | On | 28.1 | 47.3 | 49.8
45618.3736 | 49.8 | Room | On | 28.1 | 47.3 | 49.8
45618.3737 | 49.7 | Room | On | 28.1 | 47.5 | 49.8
45618.3738 | 49.7 | Room | On | 28.1 | 47.5 | 49.8
45618.3739 | 49.7 | Room | On | 28.1 | 47.5 | 49.8
45618.3741 | 49.7 | Room | On | 28.1 | 47.5 | 49.8
45618.3742 | 49.7 | Room | On | 27.9 | 47.5 | 50
45618.3743 | 49.7 | Room | On | 27.9 | 47.5 | 50
45618.3744 | 49.7 | Room | On | 27.9 | 47.5 | 50
45618.3745 | 49.7 | Room | On | 27.9 | 47.5 | 50
45618.3746 | 49.7 | Room | On | 28.1 | 47.3 | 49.8
45618.3748 | 49.7 | Room | On | 28.1 | 47.3 | 49.8
45618.3749 | 49.7 | Room | On | 28.1 | 47.3 | 49.8
45618.375 | 49.7 | Room | On | 28.1 | 47.3 | 49.8
45618.3751 | 49.8 | Room | On | 27.9 | 47.3 | 49.8
45618.3752 | 49.8 | Room | On | 27.9 | 47.3 | 49.8
45618.3753 | 49.8 | Room | On | 27.9 | 47.3 | 49.8
45618.3754 | 49.8 | Room | On | 27.9 | 47.3 | 49.8
45618.3756 | 49.7 | Room | On | 28.1 | 47.2 | 49.8
45618.3757 | 49.7 | Room | On | 28.1 | 47.2 | 49.8
45618.3758 | 49.7 | Room | On | 28.1 | 47.2 | 49.8
45618.3759 | 49.7 | Room | On | 28.1 | 47.2 | 49.8
45618.376 | 49.7 | Room | On | 28.1 | 47.1 | 49.8
45618.3761 | 49.7 | Room | On | 28.1 | 47.1 | 49.8
45618.3763 | 49.7 | Room | On | 28.1 | 47.1 | 49.8
45618.3764 | 49.7 | Room | On | 28.1 | 47.1 | 49.8
45618.3765 | 49.7 | Room | On | 28.1 | 47.1 | 49.8
45618.3766 | 49.7 | Room | On | 28.1 | 47.1 | 49.8
45618.3767 | 49.7 | Room | On | 28.1 | 47.1 | 49.8
45618.3768 | 49.7 | Room | On | 28.1 | 47.1 | 49.8
45618.377 | 49.7 | Room | On | 27.9 | 47.1 | 49.8
45618.3771 | 49.7 | Room | On | 27.9 | 47.1 | 49.8
45618.3772 | 49.7 | Room | On | 27.9 | 47.1 | 49.8
45618.3773 | 49.7 | Room | On | 27.9 | 47.1 | 49.8
45618.3774 | 49.7 | Room | On | 28.1 | 47.1 | 49.8
45618.3775 | 49.7 | Room | On | 28.1 | 47.1 | 49.8
45618.3776 | 49.7 | Room | On | 28.1 | 47.1 | 49.8
45618.3778 | 49.7 | Room | On | 28.1 | 47.1 | 49.8
45618.3779 | 49.7 | Room | On | 28.5 | 47.1 | 49.6
45618.378 | 49.7 | Room | On | 28.5 | 47.1 | 49.6
45618.3781 | 49.7 | Room | On | 28.5 | 47.1 | 49.6
45618.3782 | 49.7 | Room | On | 28.5 | 47.1 | 49.6
45618.3783 | 49.7 | Room | On | 27.9 | 47 | 49.6
45618.3785 | 49.7 | Room | On | 27.9 | 47 | 49.6
45618.3786 | 49.7 | Room | On | 27.9 | 47 | 49.6
45618.3787 | 49.7 | Room | On | 27.9 | 47 | 49.6
45618.3788 | 49.7 | Room | On | 28.1 | 47 | 49.8
45618.3789 | 49.7 | Room | On | 28.1 | 47 | 49.8
45618.379 | 49.7 | Room | On | 28.1 | 47 | 49.8
45618.3792 | 49.7 | Room | On | 28.1 | 47 | 49.8
45618.3793 | 49.7 | Room | On | 27.7 | 47 | 49.6
45618.3794 | 49.7 | Room | On | 27.7 | 47 | 49.6
45618.3795 | 49.7 | Room | On | 27.7 | 47 | 49.6
45618.3796 | 49.7 | Room | On | 27.7 | 47 | 49.6
45618.3797 | 49.7 | Room | On | 28.1 | 47 | 49.6
45618.3798 | 49.7 | Room | On | 28.1 | 47 | 49.6
45618.38 | 49.7 | Room | On | 28.1 | 47 | 49.6
45618.3801 | 49.7 | Room | On | 28.1 | 47 | 49.6
45618.3802 | 49.6 | Room | On | 28.1 | 46.8 | 49.6
45618.3803 | 49.6 | Room | On | 28.1 | 46.8 | 49.6
45618.3804 | 49.6 | Room | On | 28.1 | 46.8 | 49.6
45618.3805 | 49.6 | Room | On | 28.1 | 46.8 | 49.6
45618.3807 | 49.6 | Room | On | 28.1 | 46.8 | 49.6
45618.3808 | 49.6 | Room | On | 27.9 | 46.8 | 49.6