## Outdoor 10.00.00
Time | Elapsed Time (min) | Model | Compressor | 4Way Valve | Hot Gas Valve | Liquid Valve | EVI Bypass | Operation Mode | Operation Status | Error Code | Target Frequency1 | Order Frequency1 | Current Frequency1 | High Pressure ( kPa) | Low Pressure ( kPa) | Saturated T_Pd ( ℃) | Saturated T_Ps ( ℃) | Discharge1 ( ℃) | Comp Top1 ( ℃) | Outdoor Temp. ( ℃) | Total Pwr Consump'n (W) ( kW) | Compressor Current1 ( ℃) | OCT1 ( ℃) | DC Link1 ( ℃) | IPM1 Temp ( ℃) | CondOut Temp. ( ℃) | Suction1 Temp. ( ℃) | R32 temp ex cond’r ( ℃) | Water In(Tw1) ( ℃) | Water Out(Tw2) ( ℃) | Main EEV1 | EVI EEV | EVI SOL EEV | EVI IN ( ℃) | EVI OUT ( ℃) | Fan1 RPM | Base Heater | PHE Heater | Waterout type | Location | Serial Number | Main Micom | Inverter1 Micom | EEPROM Version | Current Limit | Defrost | Fan Calibration | Night Silence | Channel Address | Snow Accumulation Prevention Control | Base Heater(option) | Water Law Set Temp. ( ℃) | Flow Sensor | Ave Glycol Temp (degC) | Glycol deltaT(degC) | Density (kg/m3) | Specific Heat (J/kg/K) | Duty (W) | Energy Consumed (W) | CoP | Pressure Ratio | Evap Superheat (degC) | Cond Subcool (degC) | LWT target approach (degC) | Steady State Heat Loss | Defrost deltaT and heat reversal | Cumulative power consump (kWh) | Incremental duty (Wh) | CoP x 10 | Rolling Average CoP
46023.2865 | 0.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Safety Start | Heat | 0 | 50 | 50 | 50 | 1480.8 | 598.2 | 22.6 | -4.6 | 28.5 | 31.2 | 0 | 1696 | 3.3 | 9 | - | 36 | -3.4 | -4.2 | 21.2 | 18.6 | 23.1 | 500 | 0 | 0 | 8 | 8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.5 | 20.85 | 4.5 | 1019.6825 | 4067.2863 | 8553.8897 | 1696 | 5.0436 | 2.4754 | 0.4 | 1.4 | 27.5 |  | 3.4 | 0 | 0 | 50.4357
46023.2868 | 1 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Safety Start | Heat | 0 | 50 | 50 | 50 | 1490.6 | 598.2 | 22.8 | -4.6 | 28.5 | 32 | 0 | 1696 | 3.3 | 9 | 180 | 36 | -3.4 | -4.2 | 21.2 | 18.6 | 23.1 | 500 | 0 | 0 | 8.5 | 8.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.7 | 20.85 | 4.5 | 1019.6825 | 4067.2863 | 8616.0998 | 1696 | 5.0802 | 2.4918 | 0.4 | 1.6 | 27.5 |  | 3.4 | 0.014133 | 0.071801 | 50.8025
46023.2872 | 1.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Safety Start | Heat | 0 | 50 | 50 | 50 | 1500.4 | 598.2 | 23 | -4.6 | 29 | 33 | 0 | 1693 | 3.3 | 9 | 180 | 37 | -3.5 | -4.3 | 21.3 | 18.8 | 23.3 | 500 | 0 | 0 | 9.1 | 8.8 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.7 | 21.05 | 4.5 | 1019.6053 | 4067.4713 | 8615.8395 | 1693 | 5.0891 | 2.5082 | 0.3 | 1.7 | 27.3 |  | 3.5 | 0.028242 | 0.1436 | 50.891
46023.2875 | 2 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Safety Start | Heat | 0 | 50 | 50 | 50 | 1500.4 | 598.2 | 23 | -4.6 | 29.2 | 33.7 | 0 | 1693 | 3.4 | 9 | 180 | 37 | -3.5 | -4.3 | 21.5 | 19.1 | 23.6 | 500 | 0 | 0 | 9.6 | 9 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.5 | 21.35 | 4.5 | 1019.4891 | 4067.7488 | 8553.24 | 1693 | 5.0521 | 2.5082 | 0.3 | 1.5 | 27 |  | 3.5 | 0.04235 | 0.21488 | 50.5212
46023.2879 | 2.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Safety Start | Heat | 0 | 50 | 50 | 50 | 1529.8 | 598.2 | 23.7 | -4.6 | 29.6 | 34.2 | 0 | 1703 | 3.4 | 9 | 180 | 37 | -3.5 | -4.3 | 21.8 | 19.5 | 24 | 500 | 0 | 0 | 10.1 | 9.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.5 | 21.75 | 4.5 | 1019.3334 | 4068.1188 | 8552.7115 | 1703 | 5.0221 | 2.5573 | 0.3 | 1.9 | 26.6 |  | 3.5 | 0.056542 | 0.28615 | 50.2214
46023.2882 | 3 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Safety Start | Heat | 0 | 50 | 50 | 50 | 1539.6 | 598.2 | 23.9 | -4.6 | 29.6 | 34.6 | 0 | 1703 | 3.4 | 9 | 179 | 37 | -3.5 | -4.3 | 22.2 | 19.8 | 24.3 | 500 | 0 | 0 | 10.6 | 9.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.5 | 22.05 | 4.5 | 1019.216 | 4068.3962 | 8552.31 | 1703 | 5.0219 | 2.5737 | 0.3 | 1.7 | 26.3 |  | 3.5 | 0.070733 | 0.35742 | 50.2191
46023.2886 | 3.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 50 | 50 | 50 | 1549.4 | 598.2 | 24.1 | -4.6 | 29.6 | 35 | 0 | 1731 | 3.5 | 9 | 179 | 38 | -3.4 | -4.3 | 22.4 | 20 | 24.5 | 500 | 0 | 0 | 10.8 | 9.8 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.5 | 22.25 | 4.5 | 1019.1375 | 4068.5813 | 8552.04 | 1731 | 4.9405 | 2.5901 | 0.3 | 1.7 | 26.1 |  | 3.4 | 0.085158 | 0.42869 | 49.4052
46023.2889 | 4 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 50 | 50 | 50 | 1569.1 | 598.2 | 24.6 | -4.6 | 29.6 | 35.4 | 0 | 1731 | 3.5 | 9 | 179 | 38 | -3.5 | -4.4 | 22.7 | 20.4 | 25 | 500 | 0 | 0 | 11.1 | 10 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.5 | 22.7 | 4.6 | 1018.96 | 4068.9975 | 8741.4569 | 1731 | 5.0499 | 2.623 | 0.2 | 1.9 | 25.6 |  | 3.5 | 0.099583 | 0.50153 | 50.4995
46023.2893 | 4.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 52 | 52 | 52 | 1598.5 | 588.4 | 25.2 | -5.1 | 30 | 36 | 0 | 1758 | 3.7 | 10 | 179 | 38 | -3.6 | -4.5 | 23.2 | 20.8 | 25.4 | 498 | 0 | 0 | 11.4 | 10.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.7 | 23.1 | 4.6 | 1018.8012 | 4069.3675 | 8804.46 | 1758 | 5.0082 | 2.7167 | 0.6 | 2 | 25.2 |  | 3.6 | 0.11423 | 0.5749 | 50.0823
46023.2896 | 5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 52 | 52 | 52 | 1618.1 | 588.4 | 25.6 | -5.1 | 30.7 | 36.5 | 0 | 1758 | 3.7 | 10 | 179 | 39 | -3.7 | -4.6 | 23.6 | 21.3 | 25.7 | 498 | 0 | 0 | 11.6 | 10.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.7 | 23.5 | 4.4 | 1018.6416 | 4069.7375 | 8421.1034 | 1758 | 4.7902 | 2.75 | 0.5 | 2 | 24.9 |  | 3.7 | 0.12888 | 0.64508 | 47.9016 | 49.6215
46023.29 | 5.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 54 | 54 | 54 | 1627.9 | 578.6 | 25.9 | -5.5 | 31.5 | 37.4 | 0 | 1841 | 3.9 | 10 | 179 | 39 | -3.8 | -4.8 | 24.1 | 21.5 | 26.3 | 497 | 0 | 0 | 11.8 | 10.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.5 | 23.9 | 4.8 | 1018.4811 | 4070.1075 | 9119.7204 | 1841 | 4.9537 | 2.8135 | 0.7 | 1.8 | 24.3 |  | 3.8 | 0.14422 | 0.72107 | 49.5368 | 49.4851
46023.2903 | 6 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 54 | 54 | 54 | 1637.7 | 578.6 | 26.1 | -5.5 | 32.2 | 38 | 0 | 1841 | 3.9 | 10 | 179 | 39 | -4 | -5 | 24.3 | 21.7 | 26.5 | 497 | 0 | 0 | 12 | 10.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.3 | 24.1 | 4.8 | 1018.4005 | 4070.2925 | 9053.0902 | 1841 | 4.9175 | 2.8305 | 0.5 | 1.8 | 24.1 |  | 4 | 0.15957 | 0.79652 | 49.1749 | 49.439
46023.2907 | 6.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 56 | 56 | 56 | 1657.3 | 578.6 | 26.5 | -5.5 | 32.8 | 39 | 0 | 1957 | 4.1 | 10 | 179 | 40 | -4 | -5.1 | 24.6 | 22.1 | 27 | 446 | 0 | 0 | 12.1 | 10.9 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.5 | 24.55 | 4.9 | 1018.2183 | 4070.7087 | 9308.6876 | 1957 | 4.7566 | 2.8643 | 0.4 | 1.9 | 23.6 |  | 4 | 0.17588 | 0.87409 | 47.5661 | 48.8523
46023.291 | 7 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 56 | 56 | 56 | 1676.9 | 568.8 | 26.9 | -5.9 | 33.2 | 40 | 0 | 1957 | 4.2 | 10 | 179 | 40 | -4 | -5.2 | 24.8 | 22.5 | 27.3 | 446 | 0 | 0 | 12.3 | 11 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.5 | 24.9 | 4.8 | 1018.0758 | 4071.0325 | 9118.1636 | 1957 | 4.6593 | 2.9481 | 0.7 | 2.1 | 23.3 |  | 4 | 0.19218 | 0.95007 | 46.5926 | 48.1544
46023.2914 | 7.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 58 | 58 | 58 | 1696.5 | 568.8 | 27.3 | -5.9 | 33.7 | 41 | 0 | 2065 | 4.3 | 10 | 180 | 41 | -4 | -5.4 | 25.2 | 22.7 | 27.8 | 432 | 0 | 0 | 12.4 | 11.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.5 | 25.25 | 5.1 | 1017.9327 | 4071.3562 | 9687.4568 | 2065 | 4.6913 | 2.9826 | 0.5 | 2.1 | 22.8 |  | 4 | 0.20939 | 1.0308 | 46.9126 | 47.9566
46023.2917 | 8 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 58 | 58 | 58 | 1716.2 | 559 | 27.7 | -6.4 | 34.4 | 42 | 0 | 2065 | 4.4 | 11 | 180 | 41 | -4 | -5.5 | 25.5 | 23.1 | 28.2 | 432 | 0 | 0 | 12.6 | 11.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.5 | 25.65 | 5.1 | 1017.7682 | 4071.7263 | 9686.7721 | 2065 | 4.6909 | 3.0701 | 0.9 | 2.2 | 22.4 |  | 4 | 0.2266 | 1.1115 | 46.9093 | 47.4311
46023.2921 | 8.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 1726 | 559 | 27.9 | -6.4 | 34.8 | 42.8 | 0 | 2173 | 4.6 | 11 | 180 | 41 | -4.1 | -5.7 | 25.7 | 23.2 | 28.5 | 422 | 0 | 0 | 12.7 | 11.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.9 | 25.85 | 5.3 | 1017.6857 | 4071.9113 | 10212.7049 | 2173 | 4.6998 | 3.0877 | 0.7 | 2.2 | 22.1 |  | 4.1 | 0.24471 | 1.1966 | 46.9982 | 46.9958
46023.2924 | 9 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 1755.4 | 559 | 28.6 | -6.4 | 35.4 | 43.6 | 0 | 2173 | 4.6 | 11 | 180 | 42 | -4.3 | -5.9 | 25.7 | 23.6 | 29 | 422 | 0 | 0 | 12.8 | 11.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.9 | 26.3 | 5.4 | 1017.4991 | 4072.3275 | 10404.5533 | 2173 | 4.7881 | 3.1403 | 0.5 | 2.9 | 21.6 |  | 4.3 | 0.26282 | 1.2833 | 47.8811 | 47.0587
46023.2927 | 9.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 1765.2 | 549.2 | 28.8 | -6.8 | 36.5 | 44.8 | 0 | 2288 | 4.6 | 11 | 180 | 42 | -4.4 | -6 | 25.6 | 23.8 | 29.2 | 410 | 0 | 0 | 12.9 | 11.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.5 | 26.5 | 5.4 | 1017.4158 | 4072.5125 | 10255.0104 | 2288 | 4.4821 | 3.2141 | 0.8 | 3.2 | 21.4 |  | 4.4 | 0.28188 | 1.3688 | 44.8208 | 46.7044
46023.2931 | 10 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 1784.8 | 539.4 | 29.2 | -7.2 | 37.2 | 45.6 | 0 | 2288 | 4.7 | 11 | 181 | 42 | -4.7 | -6.3 | 24.8 | 24.2 | 29.5 | 410 | 0 | 0 | 13 | 11.9 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.5 | 26.85 | 5.3 | 1017.2695 | 4072.8362 | 10064.4556 | 2288 | 4.3988 | 3.3089 | 0.9 | 4.4 | 21.1 |  | 4.7 | 0.30095 | 1.4527 | 43.988 | 46.1195
46023.2934 | 10.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 1794.6 | 539.4 | 29.4 | -7.2 | 37.8 | 46.4 | -0.1 | 2348 | 4.7 | 11 | 181 | 42 | -4.8 | -6.4 | 24.6 | 24.4 | 29.8 | 401 | 0 | 0 | 13.1 | 11.9 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.7 | 27.1 | 27.1 | 5.4 | 1017.1646 | 4073.0675 | 10104.7283 | 2348 | 4.3035 | 3.327 | 0.8 | 4.8 | 20.9 |  | 4.7 | 0.32052 | 1.5369 | 43.0355 | 45.3447
46023.2938 | 11 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 1824 | 549.2 | 30 | -6.8 | 38.4 | 47.3 | -0.1 | 2383 | 4.7 | 11 | 181 | 42 | -4.7 | -6.4 | 24.5 | 24.7 | 30.1 | 401 | 0 | 0 | 13.1 | 12 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.7 | 27.1 | 27.4 | 5.4 | 1017.0382 | 4073.345 | 10104.1614 | 2383 | 4.2401 | 3.3212 | 0.4 | 5.5 | 20.6 |  | 4.6 | 0.34037 | 1.6211 | 42.401 | 44.4253
46023.2941 | 11.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 1833.8 | 549.2 | 30.1 | -6.8 | 39.2 | 48.1 | -0.1 | 2383 | 4.8 | 11 | 181 | 42 | -4.6 | -6.3 | 24.4 | 25.1 | 30.4 | 391 | 0 | 0 | 13.1 | 12 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.7 | 27.5 | 27.75 | 5.3 | 1016.8902 | 4073.6687 | 10062.7591 | 2383 | 4.2227 | 3.339 | 0.5 | 5.7 | 20.3 |  | 4.5 | 0.36023 | 1.7049 | 42.2273 | 43.2945
46023.2945 | 12 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 1853.4 | 549.2 | 30.5 | -6.8 | 40.1 | 49 | -0.1 | 2425 | 4.8 | 12 | 181 | 42 | -4.7 | -6.4 | 24.3 | 25.4 | 30.7 | 391 | 0 | 0 | 13.1 | 12 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.7 | 27.3 | 28.05 | 5.3 | 1016.7627 | 4073.9462 | 9989.0038 | 2425 | 4.1192 | 3.3747 | 0.4 | 6.2 | 20 |  | 4.6 | 0.38044 | 1.7882 | 41.1918 | 42.5687
46023.2948 | 12.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 1882.9 | 539.4 | 31.1 | -7.2 | 40.8 | 50 | -0.1 | 2425 | 4.9 | 12 | 182 | 42 | -4.8 | -6.4 | 24.3 | 25.7 | 31 | 382 | 0 | 0 | 13.1 | 12 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.7 | 27.3 | 28.35 | 5.3 | 1016.6348 | 4074.2238 | 9988.427 | 2425 | 4.1189 | 3.4907 | 0.8 | 6.8 | 19.7 |  | 4.7 | 0.40065 | 1.8714 | 41.1894 | 42.009
46023.2952 | 13 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 1892.7 | 539.4 | 31.3 | -7.2 | 41.4 | 50.5 | -0.1 | 2467 | 4.9 | 12 | 182 | 42 | -4.9 | -6.6 | 24.4 | 25.8 | 31.1 | 382 | 0 | 0 | 13.1 | 12 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.7 | 27.3 | 28.45 | 5.3 | 1016.592 | 4074.3162 | 9988.2336 | 2467 | 4.0487 | 3.5089 | 0.6 | 6.9 | 19.6 |  | 4.8 | 0.42121 | 1.9546 | 40.4874 | 41.4994
46023.2955 | 13.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 1922.1 | 539.4 | 31.9 | -7.2 | 42.8 | 51.7 | -0.1 | 2467 | 4.9 | 12 | 182 | 42 | -5 | -6.7 | 24.7 | 26.3 | 31.5 | 376 | 0 | 0 | 13 | 12 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.7 | 27.7 | 28.9 | 5.2 | 1016.3989 | 4074.7325 | 9942.4895 | 2467 | 4.0302 | 3.5634 | 0.5 | 7.2 | 19.2 |  | 4.9 | 0.44177 | 2.0375 | 40.3019 | 41.0795
46023.2959 | 14 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 1931.9 | 539.4 | 32.1 | -7.2 | 43.6 | 53 | 0 | 2506 | 5 | 12 | 182 | 42 | -4.9 | -6.6 | 25 | 26.5 | 31.8 | 376 | 0 | 0 | 13 | 11.9 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.5 | 29.15 | 5.3 | 1016.2911 | 4074.9637 | 10060.0278 | 2506 | 4.0144 | 3.5816 | 0.6 | 7.1 | 18.8 |  | 4.9 | 0.46265 | 2.1213 | 40.1438 | 40.6628
46023.2962 | 14.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 1941.7 | 539.4 | 32.3 | -7.2 | 44.8 | 54.1 | 0 | 2506 | 5 | 12 | 183 | 43 | -4.9 | -6.7 | 25.3 | 26.8 | 32.1 | 417 | 0 | 0 | 13 | 11.9 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.5 | 29.45 | 5.3 | 1016.1613 | 4075.2413 | 10059.4279 | 2506 | 4.0141 | 3.5997 | 0.5 | 7 | 18.5 |  | 4.9 | 0.48353 | 2.2052 | 40.1414 | 40.4528
46023.2966 | 15 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 1931.9 | 539.4 | 32.1 | -7.2 | 45.5 | 55.1 | 0 | 2533 | 5 | 12 | 183 | 43 | -4.8 | -6.7 | 25.6 | 27.1 | 32.3 | 417 | 0 | 0 | 13 | 11.9 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.3 | 29.7 | 5.2 | 1016.0527 | 4075.4725 | 9797.3575 | 2533 | 3.8679 | 3.5816 | 0.5 | 6.5 | 18.3 |  | 4.8 | 0.50464 | 2.2868 | 38.6789 | 39.9507
46023.2969 | 15.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 1941.7 | 539.4 | 32.3 | -7.2 | 45.8 | 55.5 | 0 | 2533 | 5 | 12 | 183 | 43 | -4.7 | -6.7 | 26.3 | 27.5 | 32.7 | 411 | 0 | 0 | 13 | 11.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.5 | 30.1 | 5.2 | 1015.8783 | 4075.8425 | 9868.3347 | 2533 | 3.8959 | 3.5997 | 0.5 | 6 | 17.9 |  | 4.7 | 0.52575 | 2.369 | 38.9591 | 39.645
46023.2973 | 16 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 1951.5 | 539.4 | 32.4 | -7.2 | 46 | 55.6 | 0 | 2540 | 5 | 12 | 183 | 43 | -4.8 | -6.8 | 28.5 | 27.8 | 32.8 | 411 | 0 | 0 | 13 | 11.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.3 | 30.3 | 5 | 1015.7908 | 4076.0275 | 9419.3898 | 2540 | 3.7084 | 3.6179 | 0.4 | 3.9 | 17.8 |  | 4.8 | 0.54692 | 2.4475 | 37.0842 | 39.0015
46023.2976 | 16.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 1961.3 | 539.4 | 32.6 | -7.2 | 46 | 55.5 | -0.1 | 2540 | 5 | 12 | 183 | 44 | -4.9 | -6.9 | 30.1 | 28.1 | 33.1 | 406 | 0 | 0 | 13 | 11.9 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.3 | 30.6 | 5 | 1015.659 | 4076.305 | 9418.8094 | 2540 | 3.7082 | 3.6361 | 0.3 | 2.5 | 17.5 |  | 4.8 | 0.56808 | 2.526 | 37.0819 | 38.3891
46023.298 | 17 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 1980.9 | 539.4 | 33 | -7.2 | 45.8 | 55.1 | -0.1 | 2551 | 5 | 12 | 183 | 45 | -5 | -6.9 | 30.5 | 28.3 | 33.3 | 406 | 0 | 0 | 13 | 12 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.7 | 27.5 | 30.8 | 5 | 1015.5709 | 4076.49 | 9487.4192 | 2551 | 3.7191 | 3.6724 | 0.3 | 2.5 | 17.4 |  | 4.9 | 0.58934 | 2.6051 | 37.191 | 37.799
46023.2983 | 17.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 1980.9 | 529.6 | 33 | -7.7 | 45.8 | 55 | -0.2 | 2551 | 5.2 | 13 | 183 | 46 | -5.5 | -7.1 | 30.7 | 28.6 | 33.5 | 405 | 80 | 700 | 13.1 | 12.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.7 | 27.5 | 31.05 | 4.9 | 1015.4605 | 4076.7213 | 9297.187 | 2551 | 3.6445 | 3.7404 | 0.6 | 2.3 | 17.2 |  | 5.3 | 0.6106 | 2.6826 | 36.4453 | 37.3523
46023.2987 | 18 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 1980.9 | 529.6 | 33 | -7.7 | 46 | 55 | -0.2 | 2618 | 5.6 | 14 | 183 | 46 | -5.4 | -7.1 | 31.4 | 28.7 | 33.7 | 405 | 150 | 2000 | 7.5 | 19.7 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.8 | 27.9 | 31.2 | 5 | 1015.394 | 4076.86 | 9624.6151 | 2618 | 3.6763 | 3.7404 | 0.6 | 1.6 | 17.1 |  | 5.2 | 0.63242 | 2.7628 | 36.7632 | 36.9131
46023.299 | 18.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2000.5 | 539.4 | 33.4 | -7.2 | 47.3 | 55.6 | -0.1 | 2618 | 5.7 | 14 | 183 | 47 | -5.1 | -6.8 | 31.8 | 29.1 | 33.8 | 397 | 150 | 2000 | 8.3 | 27.8 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.8 | 27.9 | 31.45 | 4.7 | 1015.283 | 4077.0912 | 9046.6622 | 2618 | 3.4556 | 3.7088 | 0.4 | 1.6 | 17 |  | 5 | 0.65423 | 2.8382 | 34.5556 | 36.4074
46023.2993 | 19 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2010.4 | 539.4 | 33.6 | -7.2 | 47.8 | 56.1 | 0 | 2858 | 5.7 | 14 | 180 | 47 | -5.3 | -6.8 | 32.2 | 29.3 | 34.1 | 397 | 150 | 2000 | 8.6 | 29.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.7 | 27.5 | 31.7 | 4.8 | 1015.1717 | 4077.3225 | 9106.2012 | 2858 | 3.1862 | 3.7271 | 0.4 | 1.4 | 16.6 |  | 5.3 | 0.67805 | 2.914 | 31.8621 | 35.3634
46023.2997 | 19.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2020.2 | 539.4 | 33.7 | -7.2 | 48 | 56.5 | -0.1 | 2858 | 5.7 | 14 | 180 | 48 | -5.4 | -7 | 32.3 | 29.6 | 34.4 | 396 | 150 | 2000 | 8.6 | 30 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.7 | 27.5 | 32 | 4.8 | 1015.0376 | 4077.6 | 9105.6181 | 2858 | 3.186 | 3.7453 | 0.2 | 1.4 | 16.3 |  | 5.3 | 0.70187 | 2.9899 | 31.8601 | 34.2973
46023.3 | 20 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2039.8 | 539.4 | 33.9 | -7.2 | 48.3 | 56.8 | -0.1 | 2896 | 5.7 | 14 | 180 | 48 | -5.5 | -7 | 32.6 | 30 | 34.5 | 396 | 150 | 2000 | 8.5 | 30.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.7 | 27.5 | 32.25 | 4.5 | 1014.9255 | 4077.8313 | 8536.0581 | 2896 | 2.9475 | 3.7816 | 0.2 | 1.3 | 16.2 |  | 5.4 | 0.726 | 3.0611 | 29.4753 | 32.9033
46023.3004 | 20.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2049.6 | 529.6 | 34.3 | -7.7 | 48.5 | 57.1 | 0 | 2896 | 5.8 | 14 | 180 | 48 | -5.6 | -7.1 | 32.7 | 30.1 | 34.7 | 405 | 150 | 2000 | 8.4 | 30.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.7 | 27.5 | 32.4 | 4.6 | 1014.858 | 4077.97 | 8725.4653 | 2896 | 3.0129 | 3.8701 | 0.6 | 1.6 | 16 |  | 5.6 | 0.75013 | 3.1338 | 30.1294 | 31.5765
46023.3007 | 21 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2059.4 | 529.6 | 34.5 | -7.7 | 49 | 57.5 | 0 | 2936 | 5.8 | 14 | 180 | 49 | -5.8 | -7.3 | 33 | 30.3 | 35 | 405 | 150 | 2000 | 8.9 | 30.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.7 | 32.65 | 4.7 | 1014.7453 | 4078.2013 | 8979.4988 | 2936 | 3.0584 | 3.8886 | 0.4 | 1.5 | 15.6 |  | 5.8 | 0.7746 | 3.2086 | 30.5841 | 30.7822
46023.3011 | 21.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2069.2 | 519.7 | 34.6 | -8.2 | 49.3 | 58 | -0.1 | 2936 | 5.9 | 14 | 182 | 49 | -5.9 | -7.5 | 33.2 | 30.5 | 35.2 | 404 | 150 | 2000 | 8.9 | 30.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.7 | 27.3 | 32.85 | 4.7 | 1014.6549 | 4078.3863 | 8849.444 | 2936 | 3.0141 | 3.9815 | 0.7 | 1.4 | 15.5 |  | 5.8 | 0.79907 | 3.2823 | 30.1412 | 30.438
46023.3014 | 22 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2088.8 | 529.6 | 35 | -7.7 | 49.8 | 58.5 | 0 | 2977 | 5.9 | 14 | 182 | 49 | -6 | -7.5 | 33.5 | 30.7 | 35.5 | 404 | 150 | 2000 | 8.8 | 31.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.7 | 33.1 | 4.8 | 1014.5416 | 4078.6175 | 9169.6468 | 2977 | 3.0802 | 3.9441 | 0.2 | 1.5 | 15.1 |  | 6 | 0.82388 | 3.3588 | 30.8016 | 30.2263
46023.3018 | 22.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2098.6 | 519.7 | 35.2 | -8.2 | 50.1 | 59 | 0 | 2977 | 6 | 14 | 182 | 49 | -6.1 | -7.6 | 33.6 | 31 | 35.8 | 404 | 160 | 2000 | 9.2 | 31.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.7 | 33.4 | 4.8 | 1014.4052 | 4078.895 | 9169.0374 | 2977 | 3.08 | 4.0381 | 0.6 | 1.6 | 14.8 |  | 6.1 | 0.84868 | 3.4352 | 30.7996 | 30.4912
46023.3021 | 23 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2098.6 | 519.7 | 35.2 | -8.2 | 50.3 | 59.2 | 0 | 3012 | 6 | 15 | 182 | 50 | -6.3 | -7.7 | 33.8 | 31.1 | 36 | 404 | 169 | 2000 | 9.7 | 31.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.5 | 33.55 | 4.9 | 1014.3368 | 4079.0338 | 9292.1668 | 3012 | 3.085 | 4.0381 | 0.5 | 1.4 | 14.6 |  | 6.3 | 0.87378 | 3.5126 | 30.8505 | 30.6354
46023.3025 | 23.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2108.4 | 519.7 | 35.4 | -8.2 | 50.7 | 59.7 | 0.1 | 3012 | 6 | 15 | 183 | 50 | -6.4 | -7.9 | 34 | 31.4 | 36.1 | 403 | 169 | 2000 | 10.5 | 31.4 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.7 | 33.75 | 4.7 | 1014.2454 | 4079.2188 | 8977.3138 | 3012 | 2.9805 | 4.057 | 0.3 | 1.4 | 14.5 |  | 6.5 | 0.89888 | 3.5874 | 29.8052 | 30.4796
46023.3028 | 24 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2128 | 509.9 | 35.7 | -8.6 | 51.2 | 60.3 | 0.1 | 3012 | 6.1 | 15 | 183 | 50 | -6.7 | -8.1 | 34.1 | 31.7 | 36.4 | 403 | 177 | 2000 | 10.8 | 31.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.7 | 34.05 | 4.7 | 1014.1078 | 4079.4963 | 8976.7071 | 3012 | 2.9803 | 4.1734 | 0.5 | 1.6 | 14.2 |  | 6.8 | 0.92398 | 3.6622 | 29.8031 | 30.412
46023.3032 | 24.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2128 | 509.9 | 35.7 | -8.6 | 52 | 61 | 0.1 | 3059 | 6.1 | 15 | 183 | 50 | -6.9 | -8.2 | 34.4 | 31.8 | 36.5 | 402 | 186 | 2000 | 10.9 | 31.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.7 | 34.15 | 4.7 | 1014.0619 | 4079.5887 | 8976.5039 | 3059 | 2.9345 | 4.1734 | 0.4 | 1.3 | 14.1 |  | 7 | 0.94948 | 3.737 | 29.3446 | 30.1206
46023.3035 | 25 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2147.6 | 500.1 | 35.9 | -9.1 | 52.5 | 61.4 | 0 | 3059 | 6.2 | 15 | 183 | 50 | -7.1 | -8.5 | 34.4 | 32.1 | 36.7 | 402 | 195 | 2000 | 10.9 | 31.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.7 | 34.4 | 4.6 | 1013.9468 | 4079.82 | 8785.0149 | 3059 | 2.8719 | 4.2943 | 0.6 | 1.5 | 13.9 |  | 7.1 | 0.97497 | 3.8102 | 28.7186 | 29.7044
46023.3039 | 25.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2147.6 | 500.1 | 36.1 | -9.1 | 53 | 61.8 | 0 | 3100 | 6.2 | 15 | 183 | 51 | -7.2 | -8.6 | 34.7 | 32.3 | 36.8 | 401 | 195 | 2000 | 11 | 31.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.5 | 34.55 | 4.5 | 1013.8775 | 4079.9587 | 8531.6929 | 3100 | 2.7522 | 4.2943 | 0.5 | 1.4 | 13.8 |  | 7.2 | 1.0008 | 3.8813 | 27.5216 | 29.0386
46023.3042 | 26 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2157.5 | 490.3 | 36.2 | -9.6 | 53.2 | 62.4 | 0 | 3100 | 6.2 | 15 | 180 | 51 | -7.5 | -8.9 | 34.8 | 32.6 | 37.1 | 401 | 204 | 2000 | 11.1 | 31.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.5 | 34.85 | 4.5 | 1013.7386 | 4080.2362 | 8531.1045 | 3100 | 2.752 | 4.4004 | 0.7 | 1.4 | 13.5 |  | 7.5 | 1.0266 | 3.9524 | 27.5197 | 28.5815
46023.3046 | 26.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2177.1 | 490.3 | 36.6 | -9.6 | 53.7 | 63 | -0.2 | 3138 | 6.3 | 15 | 180 | 51 | -7.7 | -9.1 | 35.1 | 32.8 | 37.2 | 398 | 213 | 2000 | 10.8 | 32.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.5 | 35 | 4.4 | 1013.669 | 4080.375 | 8341.2351 | 3138 | 2.6581 | 4.4403 | 0.5 | 1.5 | 13.4 |  | 7.5 | 1.0528 | 4.0219 | 26.5814 | 27.9372
46023.3049 | 27 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2177.1 | 480.5 | 36.6 | -10.1 | 54.1 | 63.7 | -0.1 | 3138 | 6.3 | 15 | 180 | 51 | -7.9 | -9.3 | 35.2 | 33 | 37.4 | 398 | 223 | 2000 | 10.8 | 32.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.8 | 27.3 | 35.2 | 4.4 | 1013.576 | 4080.56 | 8280.187 | 3138 | 2.6387 | 4.5309 | 0.8 | 1.4 | 13.4 |  | 7.8 | 1.0789 | 4.0909 | 26.3868 | 27.3456
46023.3052 | 27.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2177.1 | 480.5 | 36.6 | -10.1 | 54.5 | 64 | -0.2 | 3169 | 6.3 | 15 | 180 | 51 | -8.2 | -9.5 | 35.2 | 33 | 37.5 | 400 | 223 | 2000 | 10.9 | 32.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.8 | 27.7 | 35.25 | 4.5 | 1013.5527 | 4080.6062 | 8592.3517 | 3169 | 2.7114 | 4.5309 | 0.6 | 1.4 | 13.3 |  | 8 | 1.1053 | 4.1625 | 27.1138 | 27.0246
46023.3056 | 28 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2186.9 | 470.7 | 36.8 | -10.5 | 54.8 | 64.5 | -0.4 | 3169 | 6.3 | 15 | 179 | 51 | -8.4 | -9.7 | 35.4 | 33.2 | 37.7 | 400 | 232 | 2000 | 10.6 | 32.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.8 | 27.7 | 35.45 | 4.5 | 1013.4594 | 4080.7913 | 8591.9502 | 3169 | 2.7112 | 4.6461 | 0.8 | 1.4 | 13.1 |  | 8 | 1.1318 | 4.2341 | 27.1125 | 26.9428
46023.3059 | 28.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2196.7 | 470.7 | 36.9 | -10.5 | 55.3 | 65 | -0.5 | 3196 | 6.3 | 16 | 179 | 52 | -8.6 | -10 | 35.5 | 33.3 | 37.8 | 396 | 242 | 2000 | 10.3 | 32.5 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.9 | 27.5 | 35.55 | 4.5 | 1013.4126 | 4080.8837 | 8529.7144 | 3196 | 2.6689 | 4.6669 | 0.5 | 1.4 | 13.1 |  | 8.1 | 1.1584 | 4.3052 | 26.6887 | 26.7766
46023.3063 | 29 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2206.5 | 460.9 | 37.1 | -11 | 55.8 | 65.5 | -0.6 | 3196 | 6.4 | 16 | 179 | 52 | -8.8 | -10.2 | 35.7 | 33.6 | 38 | 396 | 252 | 2000 | 10.3 | 32.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 51.1 | 27.5 | 35.8 | 4.4 | 1013.2955 | 4081.115 | 8339.6741 | 3196 | 2.6094 | 4.7874 | 0.8 | 1.4 | 13.1 |  | 8.2 | 1.185 | 4.3747 | 26.0941 | 26.6792
46023.3066 | 29.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2206.5 | 460.9 | 37.1 | -11 | 56.1 | 66 | -0.7 | 3212 | 6.4 | 16 | 179 | 52 | -9.1 | -10.4 | 35.8 | 33.7 | 38 | 395 | 252 | 2000 | 10.4 | 32.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 51.1 | 27.3 | 35.85 | 4.3 | 1013.2721 | 4081.1613 | 8090.7667 | 3212 | 2.5189 | 4.7874 | 0.6 | 1.3 | 13.1 |  | 8.4 | 1.2118 | 4.4421 | 25.1892 | 26.4397
46023.307 | 30 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2226.1 | 460.9 | 37.4 | -11 | 56.4 | 66.2 | -0.7 | 3212 | 6.4 | 16 | 179 | 52 | -9.2 | -10.6 | 35.8 | 33.8 | 38.1 | 395 | 262 | 2000 | 10.5 | 32.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 51.1 | 27.3 | 35.95 | 4.3 | 1013.2251 | 4081.2537 | 8090.5751 | 3212 | 2.5189 | 4.8299 | 0.4 | 1.6 | 13 |  | 8.5 | 1.2385 | 4.5096 | 25.1886 | 26.0546
46023.3073 | 30.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2235.9 | 460.9 | 37.6 | -11 | 56.7 | 66.8 | -0.6 | 3241 | 6.5 | 16 | 179 | 52 | -9.3 | -10.7 | 36 | 34 | 38.2 | 394 | 272 | 2000 | 10.5 | 32.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 51.1 | 27.1 | 36.1 | 4.2 | 1013.1546 | 4081.3925 | 7844.2494 | 3241 | 2.4203 | 4.8512 | 0.3 | 1.6 | 12.9 |  | 8.7 | 1.2656 | 4.5749 | 24.2032 | 25.4728
46023.3077 | 31 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2226.1 | 451.1 | 37.4 | -11.5 | 57.1 | 67.2 | -0.4 | 3241 | 6.5 | 16 | 179 | 52 | -9.5 | -10.8 | 36.1 | 34.1 | 38.4 | 394 | 282 | 2000 | 10.8 | 33 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 51 | 27.3 | 36.25 | 4.3 | 1013.0839 | 4081.5312 | 8089.9974 | 3241 | 2.4961 | 4.9348 | 0.7 | 1.3 | 12.6 |  | 9.1 | 1.2926 | 4.6423 | 24.9614 | 25.1273
46023.308 | 31.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2245.7 | 441.3 | 37.8 | -12.1 | 57.5 | 67.7 | -0.4 | 3269 | 6.5 | 16 | 179 | 52 | -9.7 | -11.2 | 36.2 | 34.4 | 38.5 | 393 | 282 | 2000 | 10.7 | 33 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.9 | 27.7 | 36.45 | 4.1 | 1012.9894 | 4081.7162 | 7826.3651 | 3269 | 2.3941 | 5.0888 | 0.9 | 1.6 | 12.4 |  | 9.3 | 1.3198 | 4.7076 | 23.9412 | 24.6967
46023.3084 | 32 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2255.5 | 441.3 | 37.9 | -12.1 | 57.8 | 68.1 | -0.6 | 3269 | 6.5 | 16 | 179 | 53 | -9.9 | -11.4 | 36.4 | 34.7 | 38.8 | 393 | 292 | 2000 | 10.4 | 33.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.9 | 27.7 | 36.75 | 4.1 | 1012.8474 | 4081.9938 | 7825.7995 | 3269 | 2.3939 | 5.111 | 0.7 | 1.5 | 12.1 |  | 9.3 | 1.347 | 4.7728 | 23.9394 | 24.4468
46023.3087 | 32.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2255.5 | 441.3 | 37.9 | -12.1 | 58.1 | 68.7 | -0.6 | 3293 | 6.6 | 16 | 178 | 53 | -10.1 | -11.6 | 36.5 | 34.7 | 38.8 | 391 | 303 | 2000 | 10.4 | 33.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 51.1 | 27.7 | 36.75 | 4.1 | 1012.8474 | 4081.9938 | 7825.7995 | 3293 | 2.3765 | 5.111 | 0.5 | 1.4 | 12.3 |  | 9.5 | 1.3745 | 4.838 | 23.765 | 24.162
46023.3091 | 33 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2265.3 | 431.5 | 38.1 | -12.6 | 58.5 | 69.1 | -0.6 | 3293 | 6.6 | 16 | 178 | 53 | -10.2 | -11.8 | 36.5 | 34.8 | 38.8 | 391 | 312 | 2000 | 10.6 | 33.3 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 51.1 | 27.7 | 36.8 | 4 | 1012.8236 | 4082.04 | 7634.834 | 3293 | 2.3185 | 5.2498 | 0.8 | 1.6 | 12.3 |  | 9.6 | 1.4019 | 4.9016 | 23.185 | 23.9584
46023.3094 | 33.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2265.3 | 431.5 | 38.1 | -12.6 | 58.8 | 69.7 | -0.5 | 3321 | 6.6 | 16 | 178 | 53 | -10.3 | -11.9 | 36.7 | 34.8 | 39 | 387 | 312 | 2000 | 10.7 | 33.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 51.1 | 27.7 | 36.9 | 4.2 | 1012.7762 | 4082.1325 | 8016.3814 | 3321 | 2.4138 | 5.2498 | 0.7 | 1.4 | 12.1 |  | 9.8 | 1.4296 | 4.9684 | 24.1385 | 23.7938
46023.3098 | 34 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2265.3 | 431.5 | 38.1 | -12.6 | 59.2 | 70 | -0.4 | 3321 | 6.6 | 16 | 178 | 53 | -10.6 | -12 | 36.7 | 35 | 39 | 387 | 312 | 2000 | 10.7 | 33.2 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 51 | 27.9 | 37 | 4 | 1012.7286 | 4082.225 | 7689.586 | 3321 | 2.3154 | 5.2498 | 0.6 | 1.4 | 12 |  | 10.2 | 1.4573 | 5.0325 | 23.1544 | 23.6365
46023.3101 | 34.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2275.1 | 421.7 | 38.3 | -13.1 | 59.5 | 70.4 | -0.4 | 3341 | 6.7 | 17 | 178 | 53 | -10.6 | -12.3 | 36.8 | 35.2 | 39.2 | 367 | 312 | 2000 | 11.1 | 33.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.9 | 27.5 | 37.2 | 4 | 1012.6333 | 4082.41 | 7578.9714 | 3341 | 2.2685 | 5.3951 | 0.8 | 1.5 | 11.7 |  | 10.2 | 1.4851 | 5.0957 | 22.6847 | 23.3855
46023.3105 | 35 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2284.9 | 421.7 | 38.4 | -13.1 | 59.8 | 70.7 | -0.3 | 3341 | 6.9 | 17 | 181 | 53 | -10.8 | -12.5 | 37 | 35.4 | 39.4 | 348 | 312 | 2000 | 11.9 | 33.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.8 | 27.7 | 37.4 | 4 | 1012.5378 | 4082.595 | 7633.7172 | 3341 | 2.2849 | 5.4183 | 0.6 | 1.4 | 11.4 |  | 10.5 | 1.513 | 5.1593 | 22.8486 | 23.2023
46023.3108 | 35.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2294.7 | 421.7 | 38.6 | -13.1 | 60.3 | 71.1 | -0.2 | 3383 | 7 | 17 | 181 | 54 | -10.9 | -12.7 | 37.1 | 35.5 | 39.5 | 330 | 312 | 2000 | 14.4 | 31.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.8 | 27.7 | 37.5 | 4 | 1012.49 | 4082.6875 | 7633.5296 | 3383 | 2.2564 | 5.4415 | 0.4 | 1.5 | 11.3 |  | 10.7 | 1.5412 | 5.2229 | 22.5644 | 23.0781
46023.3112 | 36 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2294.7 | 411.9 | 38.6 | -13.6 | 60.6 | 71.2 | -0.1 | 3510 | 7 | 17 | 181 | 54 | -11.2 | -12.8 | 37.1 | 35.5 | 39.5 | 313 | 312 | 2000 | 15.5 | 30.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.8 | 27.5 | 37.5 | 4 | 1012.49 | 4082.6875 | 7578.4138 | 3510 | 2.1591 | 5.571 | 0.8 | 1.5 | 11.3 |  | 11.1 | 1.5704 | 5.286 | 21.5909 | 22.5686
46023.3115 | 36.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2304.6 | 411.9 | 38.8 | -13.6 | 61 | 71.4 | 0 | 3510 | 7.1 | 17 | 181 | 54 | -11.3 | -13 | 37.2 | 35.7 | 39.7 | 297 | 312 | 2000 | 15.7 | 30.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.7 | 27.5 | 37.7 | 4 | 1012.3942 | 4082.8725 | 7578.0399 | 3510 | 2.159 | 5.595 | 0.6 | 1.6 | 11 |  | 11.3 | 1.5997 | 5.3492 | 21.5899 | 22.2557
46023.3118 | 37 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2304.6 | 411.9 | 38.8 | -13.6 | 61.4 | 71.7 | 0 | 3562 | 7.1 | 17 | 181 | 54 | -11.4 | -13.2 | 37.4 | 35.8 | 39.8 | 296 | 312 | 2000 | 15.8 | 30 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.7 | 37.8 | 4 | 1012.3462 | 4082.965 | 7632.9639 | 3562 | 2.1429 | 5.595 | 0.4 | 1.4 | 10.8 |  | 11.4 | 1.6293 | 5.4128 | 21.4289 | 22.0045
46023.3122 | 37.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2314.4 | 402.1 | 38.9 | -14.2 | 61.5 | 71.8 | 0 | 3562 | 7.1 | 17 | 181 | 54 | -11.5 | -13.3 | 37.5 | 36 | 40 | 296 | 312 | 2000 | 15.8 | 30.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.7 | 38 | 4 | 1012.25 | 4083.15 | 7632.5847 | 3562 | 2.1428 | 5.7558 | 0.9 | 1.4 | 10.6 |  | 11.5 | 1.659 | 5.4764 | 21.4278 | 21.7204
46023.3125 | 38 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2314.4 | 402.1 | 38.9 | -14.2 | 62 | 72.2 | 0 | 3587 | 7.1 | 17 | 181 | 54 | -11.7 | -13.5 | 37.7 | 36.1 | 40.1 | 292 | 312 | 2000 | 15.7 | 30.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.3 | 38.1 | 4 | 1012.2018 | 4083.2425 | 7522.1793 | 3587 | 2.0971 | 5.7558 | 0.7 | 1.2 | 10.5 |  | 11.7 | 1.6889 | 5.5391 | 20.9707 | 21.4016
46023.3129 | 38.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2324.2 | 392.3 | 39.1 | -14.7 | 62.4 | 72.7 | 0 | 3587 | 7.1 | 17 | 181 | 55 | -11.9 | -13.7 | 37.7 | 36.2 | 40.1 | 292 | 312 | 2000 | 15.7 | 30.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.5 | 38.15 | 3.9 | 1012.1777 | 4083.2888 | 7387.7624 | 3587 | 2.0596 | 5.9245 | 1 | 1.4 | 10.5 |  | 11.9 | 1.7188 | 5.6007 | 20.5959 | 21.2026
46023.3132 | 39 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2334 | 392.3 | 39.3 | -14.7 | 62.8 | 73.1 | 0 | 3612 | 7.1 | 17 | 181 | 55 | -12 | -13.9 | 37.8 | 36.4 | 40.3 | 293 | 312 | 2000 | 15.7 | 30.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.3 | 38.35 | 3.9 | 1012.0812 | 4083.4738 | 7333.6658 | 3612 | 2.0304 | 5.9495 | 0.8 | 1.5 | 10.3 |  | 12 | 1.7489 | 5.6618 | 20.3036 | 20.9454
46023.3136 | 39.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2334 | 392.3 | 39.3 | -14.7 | 63.1 | 73.4 | 0 | 3612 | 7.2 | 18 | 181 | 55 | -12 | -13.9 | 37.8 | 36.5 | 40.3 | 293 | 312 | 2000 | 15.7 | 30.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.3 | 38.4 | 3.8 | 1012.057 | 4083.52 | 7145.5333 | 3612 | 1.9783 | 5.9495 | 0.8 | 1.5 | 10.3 |  | 12 | 1.779 | 5.7213 | 19.7828 | 20.6162
46023.3139 | 40 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2343.8 | 392.3 | 39.4 | -14.7 | 63.4 | 73.8 | 0.1 | 3629 | 7.2 | 18 | 181 | 55 | -12.3 | -14 | 38 | 36.5 | 40.5 | 290 | 312 | 2000 | 15.7 | 30.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.3 | 38.5 | 4 | 1012.0086 | 4083.6125 | 7521.4248 | 3629 | 2.0726 | 5.9745 | 0.7 | 1.4 | 10.1 |  | 12.4 | 1.8092 | 5.784 | 20.7259 | 20.4758
46023.3143 | 40.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2343.8 | 392.3 | 39.4 | -14.7 | 63.7 | 74.2 | 0.2 | 3629 | 7.2 | 18 | 181 | 55 | -12.4 | -14.3 | 38 | 36.5 | 40.5 | 290 | 312 | 2000 | 15.7 | 30.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.5 | 27.5 | 38.5 | 4 | 1012.0086 | 4083.6125 | 7576.5268 | 3629 | 2.0878 | 5.9745 | 0.4 | 1.4 | 10 |  | 12.6 | 1.8395 | 5.8471 | 20.8777 | 20.4572
46023.3146 | 0 | EHS MONO LOWTEMP | On | Off | On | Off | On | Defrost | Heat | 0 | 20 | 20 | 20 | 2128 | 451.1 | 35.7 | -11.5 | 64 | 74.5 | 0.1 | 3642 | 2.8 | 14 | 181 | 55 | -12.4 | -14.2 | 38 | 36.7 | 39.7 | 1000 | 0 | 0 | 15.6 | 30.5 | 550 | On | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.3 | 38.2 | 3 | 1012.1536 | 4083.335 | 5641.4935 | 3642 | 1.549 | 4.7174 | -2.7 | -2.3 | 10.9 |  |  | 1.8698 | 5.8941
46023.315 | 0.5 | EHS MONO LOWTEMP | On | On | Off | Off | On | Defrost | Heat | 0 | 26 | 40 | 24 | 617.8 | 500.1 | -3.8 | -9.1 | 61.2 | 73.7 | 0.1 | 3642 | 0.5 | 3 | 181 | 48 | -3.9 | -5.2 | 32.3 | 36.8 | 37.1 | 2000 | 0 | 0 | 12.1 | 29.7 | 10 | On | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.3 | 36.95 | 0.3 | 1012.7524 | 4082.1788 | 564.3232 | 3642 | 0.15495 | 1.2354 | 3.9 | -36.1 | 13.5 |  |  | 1.9002 | 5.8988
46023.3153 | 1 | EHS MONO LOWTEMP | On | On | Off | Off | On | Defrost | Heat | 0 | 50 | 50 | 50 | 706.1 | 490.3 | -0.2 | -9.6 | 56.2 | 70.5 | 0.1 | 967 | 1.2 | 4 | 181 | 39 | -0.7 | 3.8 | 25.1 | 36.7 | 36.8 | 2000 | 0 | 0 | 9.1 | 28.3 | 0 | On | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.6 | 27.5 | 36.75 | 0.1 | 1012.8474 | 4081.9938 | 189.495 | 967 | 0.19596 | 1.4401 | 13.4 | -25.3 | 13.8 |  |  | 1.9082 | 5.9004
46023.3157 | 1.5 | EHS MONO LOWTEMP | On | On | Off | Off | On | Defrost | Heat | 0 | 50 | 50 | 50 | 745.3 | 657 | 1.3 | -2.2 | 45.3 | 62 | 0.2 | 967 | 1.1 | 3 | 181 | 28 | -0.1 | 21.3 | 1.8 | 36.1 | 32 | 2000 | 0 | 0 | 5.3 | 26.5 | 0 | On | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.5 | 27.7 | 34.05 | -4.1 | 1014.1078 | 4079.4963 | -7830.7445 | 967 | -8.098 | 1.1344 | 23.5 | -0.5 | 18.5 |  | -65.2562 | 1.9163 | 5.8352
46023.316 | 2 | EHS MONO LOWTEMP | On | On | Off | Off | On | Defrost | Heat | 0 | 50 | 50 | 50 | 784.5 | 706.1 | 2.7 | -0.2 | 34.6 | 50.2 | 0.3 | 601 | 1 | 3 | 181 | 24 | 0 | 25.7 | -0.7 | 35.5 | 30.7 | 2000 | 0 | 0 | 4 | 24.8 | 0 | On | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.4 | 27.5 | 33.1 | -4.8 | 1014.5416 | 4078.6175 | -9103.44 | 601 | -15.1472 | 1.111 | 25.9 | 3.4 | 19.7 |  | -75.862 | 1.9213 | 5.7593
46023.3164 | 2.5 | EHS MONO LOWTEMP | On | On | Off | Off | On | Defrost | Heat | 0 | 50 | 50 | 50 | 843.4 | 774.7 | 4.8 | 2.3 | 27.7 | 39.2 | 0.3 | 601 | 1.1 | 3 | 181 | 23 | 0.8 | 25.3 | 0.3 | 34.7 | 29.3 | 2000 | 0 | 0 | 3.6 | 23.1 | 0 | On | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.4 | 27.5 | 32 | -5.4 | 1015.0376 | 4077.6 | -10243.8204 | 601 | -17.0446 | 1.0887 | 23 | 4.5 | 21.1 |  | -85.3652 | 1.9263 | 5.6739
46023.3167 | 3 | EHS MONO LOWTEMP | On | On | Off | Off | On | Defrost | Heat | 0 | 50 | 50 | 50 | 970.9 | 882.6 | 9.8 | 6.7 | 25 | 32.8 | 0.4 | 601 | 1.2 | 3 | 180 | 23 | 2.7 | 24.5 | 1.5 | 33.8 | 27.6 | 2000 | 0 | 0 | 3.6 | 21.8 | 0 | On | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.4 | 27.3 | 30.7 | -6.2 | 1015.615 | 4076.3975 | -11679.0824 | 601 | -19.4327 | 1.1 | 17.8 | 8.3 | 22.8 |  | -97.3257 | 1.9313 | 5.5766
46023.3171 | 3.5 | EHS MONO LOWTEMP | On | On | Off | Off | On | Defrost | Heat | 0 | 50 | 50 | 50 | 1167 | 1029.7 | 14.6 | 10.7 | 23.2 | 25.7 | 0.5 | 581 | 1.4 | 4 | 180 | 23 | 3 | 22.7 | 3 | 32.8 | 25.7 | 2000 | 0 | 0 | 4.2 | 20 | 0 | On | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.3 | 27.3 | 29.25 | -7.1 | 1016.2479 | 4075.0563 | -13378.3639 | 581 | -23.0264 | 1.1333 | 12 | 11.6 | 24.6 |  | -111.4864 | 1.9362 | 5.4651
46023.3174 | 4 | EHS MONO LOWTEMP | On | On | Off | Off | On | Defrost | Heat | 0 | 22 | 20 | 29 | 1833.8 | 1372.9 | 30.1 | 20 | 24.5 | 23.5 | 0.7 | 581 | 2.2 | 6 | 180 | 25 | 13.6 | 20.6 | 6.6 | 31.8 | 22 | 2000 | 0 | 0 | 4.3 | 18.1 | 0 | On | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.3 | 27.3 | 26.9 | -9.8 | 1017.2486 | 4072.8825 | -18474.2337 | 581 | -31.7973 | 1.3357 | 0.6 | 23.5 | 28.3 |  | -153.9519 | 1.941 | 5.3112
46023.3177 | 4.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Defrost | Heat | 0 | 50 | 50 | 50 | 2128 | 882.6 | 35.7 | 6.1 | 31.5 | 29.2 | 1 | 783 | 4.2 | 12 | 180 | 33 | 18.9 | 23 | 24.8 | 30.3 | 35.1 | 464 | 0 | 0 | 4.2 | 23.7 | 430 | On | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.1 | 27.5 | 32.7 | 4.8 | 1014.7228 | 4078.2475 | 9104.2393 | 783 | 11.6274 | 2.4111 | 16.9 | 10.9 | 15 |  | -589.2474 | 1.9475 | 5.387
46023.3181 | 5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Defrost | Heat | 0 | 50 | 50 | 50 | 2030 | 637.4 | 33.9 | -3 | 37.2 | 34.6 | 1 | 783 | 4.3 | 12 | 180 | 38 | 2.1 | 5.3 | 30.2 | 30.2 | 34.8 | 465 | 0 | 0 | 4.9 | 24.2 | 530 | On | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.5 | 32.5 | 4.6 | 1014.813 | 4078.0625 | 8725.276 | 783 | 11.1434 | 3.1848 | 8.3 | 3.7 | 15.1 |  |  | 1.9541 | 5.4598
46023.3184 | 0 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 47 | 47 | 47 | 2049.6 | 657 | 34.3 | -2.2 | 42.8 | 43 | 0.9 | 1483 | 4.1 | 12 | 180 | 43 | -1.4 | -1.2 | 31.7 | 30.4 | 34.8 | 286 | 80 | 700 | 4.5 | 24.3 | 550 | On | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50 | 27.5 | 32.6 | 4.4 | 1014.7679 | 4078.155 | 8345.7347 | 1483 | 5.6276 | 3.1196 | 1 | 2.6 | 15.2 |  |  | 1.9664 | 5.5293
46023.3188 | 0.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 47 | 47 | 47 | 2098.6 | 637.4 | 35.2 | -3 | 44.8 | 48.1 | 0.8 | 1483 | 4.7 | 14 | 180 | 44 | -0.9 | -0.9 | 32.5 | 30.6 | 35.5 | 286 | 312 | 2000 | 9.7 | 25.2 | 550 | On | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50 | 27.5 | 33.05 | 4.9 | 1014.5643 | 4078.5712 | 9293.1974 | 1483 | 6.2665 | 3.2924 | 2.1 | 2.7 | 14.5 |  |  | 1.9788 | 5.6067
46023.3191 | 1 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 49 | 49 | 49 | 2128 | 637.4 | 35.7 | -3 | 43.6 | 49.6 | 0.8 | 2186 | 5 | 14 | 180 | 44 | -1.5 | 0.7 | 33.7 | 31.1 | 36.2 | 286 | 269 | 2000 | 17.1 | 19.5 | 550 | On | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.1 | 27.5 | 33.65 | 5.1 | 1014.2911 | 4079.1262 | 9671.2227 | 2186 | 4.4242 | 3.3386 | 3.7 | 2 | 13.9 |  |  | 1.997 | 5.6873
46023.3195 | 1.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 49 | 49 | 49 | 2137.8 | 637.4 | 35.9 | -3 | 43.1 | 49.1 | 0.7 | 2186 | 5.1 | 15 | 180 | 44 | -1.9 | 0.7 | 34.2 | 31.5 | 36.5 | 286 | 255 | 2000 | 17.4 | 18.7 | 540 | On | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.1 | 27.1 | 34 | 5 | 1014.1308 | 4079.45 | 9342.9416 | 2186 | 4.274 | 3.3539 | 3.7 | 1.7 | 13.6 |  |  | 2.0152 | 5.7652 | 42.7399
46023.3198 | 2 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 51 | 51 | 51 | 2186.9 | 627.6 | 36.8 | -3.4 | 42.8 | 48.3 | 0.7 | 2524 | 5.3 | 15 | 179 | 44 | -2.2 | -2.4 | 35 | 32.1 | 37.2 | 285 | 255 | 2000 | 17.2 | 17.8 | 550 | On | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.1 | 27.5 | 34.65 | 5.1 | 1013.8313 | 4080.0512 | 9669.0302 | 2524 | 3.8308 | 3.4845 | 1 | 1.8 | 12.9 |  |  | 2.0362 | 5.8458 | 38.3084
46023.3202 | 2.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 51 | 51 | 51 | 2216.3 | 617.8 | 37.3 | -3.8 | 43.6 | 48.6 | 0.7 | 2524 | 5.4 | 15 | 179 | 44 | -2.5 | -3 | 35.7 | 32.6 | 37.7 | 285 | 242 | 2000 | 16.8 | 17.3 | 550 | On | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.1 | 27.5 | 35.15 | 5.1 | 1013.5992 | 4080.5138 | 9667.9132 | 2524 | 3.8304 | 3.5874 | 0.8 | 1.6 | 12.4 |  |  | 2.0573 | 5.9263 | 38.3039
46023.3205 | 3 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 53 | 53 | 53 | 2265.3 | 608 | 38.1 | -4.2 | 44.4 | 49.6 | 0.7 | 2698 | 5.7 | 15 | 179 | 44 | -2.7 | -3.3 | 36.2 | 33.1 | 38.4 | 285 | 229 | 2000 | 16.6 | 17 | 550 | On | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.1 | 27.9 | 35.75 | 5.3 | 1013.319 | 4081.0687 | 10191.7534 | 2698 | 3.7775 | 3.7258 | 0.9 | 1.9 | 11.7 |  |  | 2.0798 | 6.0113 | 37.7752
46023.3209 | 3.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 53 | 53 | 53 | 2284.9 | 608 | 38.4 | -4.2 | 45.3 | 50.6 | 0.6 | 2698 | 5.7 | 15 | 179 | 44 | -2.9 | -3.6 | 36.8 | 33.5 | 38.8 | 285 | 217 | 2000 | 16 | 16.4 | 550 | On | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.1 | 27.5 | 36.15 | 5.3 | 1013.131 | 4081.4387 | 10044.6823 | 2698 | 3.723 | 3.7581 | 0.6 | 1.6 | 11.3 |  |  | 2.1022 | 6.095 | 37.2301
46023.3212 | 4 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 55 | 55 | 55 | 2314.4 | 608 | 38.9 | -4.2 | 45.5 | 50.8 | 0.6 | 2864 | 6 | 16 | 179 | 44 | -2.9 | -3.6 | 37.1 | 33.7 | 39.2 | 285 | 217 | 2000 | 15.8 | 16.2 | 550 | On | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.2 | 27.5 | 36.45 | 5.5 | 1012.9894 | 4081.7162 | 10422.979 | 2864 | 3.6393 | 3.8066 | 0.6 | 1.8 | 11 |  |  | 2.1261 | 6.1818 | 36.3931
46023.3216 | 4.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 55 | 55 | 55 | 2334 | 608 | 39.3 | -4.2 | 46 | 51.7 | 0.6 | 2864 | 6 | 16 | 181 | 44 | -3.1 | -3.7 | 37.7 | 34.1 | 39.7 | 285 | 206 | 2000 | 15.4 | 15.8 | 550 | On | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.2 | 27.5 | 36.9 | 5.6 | 1012.7762 | 4082.1325 | 10611.3352 | 2864 | 3.7051 | 3.8388 | 0.5 | 1.6 | 10.5 |  |  | 2.15 | 6.2703 | 37.0508
46023.3219 | 5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 57 | 57 | 57 | 2373.2 | 598.2 | 39.9 | -4.6 | 46 | 52.1 | 0.6 | 3020 | 6.3 | 16 | 181 | 44 | -3.1 | -3.9 | 38 | 34.4 | 40.3 | 285 | 195 | 2000 | 15.2 | 15.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.2 | 27.3 | 37.35 | 5.9 | 1012.5617 | 4082.5487 | 11097.2736 | 3020 | 3.6746 | 3.9672 | 0.7 | 1.9 | 9.9 |  |  | 2.1751 | 6.3627 | 36.7459
46023.3223 | 5.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 57 | 57 | 57 | 2383 | 598.2 | 40.1 | -4.6 | 46.2 | 52.1 | 0.7 | 3020 | 6.3 | 16 | 181 | 44 | -3.4 | -4 | 38.1 | 34.5 | 40.6 | 285 | 185 | 2000 | 14.7 | 15 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.2 | 27.3 | 37.55 | 6.1 | 1012.4661 | 4082.7337 | 11472.8883 | 3020 | 3.799 | 3.9836 | 0.6 | 2 | 9.6 |  |  | 2.2003 | 6.4583 | 37.9897
46023.3226 | 6 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 59 | 59 | 59 | 2422.2 | 588.4 | 40.7 | -5.1 | 46 | 51.7 | 0.6 | 3174 | 6.6 | 16 | 181 | 44 | -3.6 | -4.3 | 37.4 | 35 | 41 | 285 | 185 | 2000 | 13.9 | 14.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.1 | 27.3 | 38 | 6 | 1012.25 | 4083.15 | 11283.5502 | 3174 | 3.555 | 4.1166 | 0.8 | 3.3 | 9.1 |  |  | 2.2268 | 6.5524 | 35.5499 | 36.7459
46023.323 | 6.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 59 | 59 | 59 | 2432 | 588.4 | 40.9 | -5.5 | 46 | 51.5 | 0.6 | 3174 | 6.5 | 16 | 181 | 43 | -3.7 | -4.4 | 36.2 | 35 | 41.1 | 285 | 175 | 2000 | 13.3 | 13.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.1 | 27.3 | 38.05 | 6.1 | 1012.2259 | 4083.1962 | 11471.4665 | 3174 | 3.6142 | 4.1332 | 1.1 | 4.7 | 9 |  |  | 2.2532 | 6.648 | 36.142 | 36.6957
46023.3233 | 7 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2461.5 | 578.6 | 41.4 | -5.5 | 46 | 51.5 | 0.6 | 3300 | 6.7 | 16 | 183 | 43 | -3.7 | -4.1 | 34.7 | 35.2 | 41.5 | 285 | 166 | 2000 | 12.7 | 13 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.2 | 27.7 | 38.35 | 6.3 | 1012.0812 | 4083.4738 | 12020.2688 | 3300 | 3.6425 | 4.2542 | 1.4 | 6.7 | 8.7 |  |  | 2.2807 | 6.7481 | 36.4251 | 36.5705
46023.3237 | 7.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2530.1 | 568.8 | 42.5 | -5.9 | 46.4 | 52 | 0.6 | 3300 | 6.8 | 16 | 183 | 42 | -4 | -3.5 | 34.1 | 35.4 | 41.6 | 285 | 157 | 2000 | 12.1 | 12.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.2 | 27.5 | 38.5 | 6.2 | 1012.0086 | 4083.6125 | 11743.6165 | 3300 | 3.5587 | 4.4481 | 2.4 | 8.4 | 8.6 |  |  | 2.3082 | 6.846 | 35.5867 | 36.3387
46023.324 | 8 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2588.9 | 549.2 | 43.4 | -6.8 | 47.1 | 53 | 0.6 | 3389 | 7 | 17 | 183 | 42 | -4.2 | -3.3 | 34 | 35.8 | 41.8 | 301 | 157 | 2000 | 11.7 | 12 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.2 | 27.5 | 38.8 | 6 | 1011.8631 | 4083.89 | 11363.9283 | 3389 | 3.3532 | 4.7139 | 3.5 | 9.4 | 8.4 |  |  | 2.3365 | 6.9407 | 33.5318 | 35.4471
46023.3243 | 8.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2647.8 | 549.2 | 44.3 | -6.8 | 47.8 | 54 | 0.6 | 3389 | 7.1 | 17 | 183 | 42 | -4.2 | -3.1 | 34.1 | 36.1 | 42 | 301 | 149 | 2000 | 11.6 | 11.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.2 | 27.5 | 39.05 | 5.9 | 1011.7414 | 4084.1213 | 11173.8187 | 3389 | 3.2971 | 4.8212 | 3.7 | 10.2 | 8.2 |  |  | 2.3647 | 7.0338 | 32.9708 | 34.9313
46023.3247 | 9 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2687 | 559 | 44.9 | -6.4 | 49.3 | 56.4 | 0.7 | 3511 | 7.2 | 17 | 184 | 42 | -4 | -3.3 | 34.2 | 36.4 | 42.4 | 325 | 141 | 2000 | 11.6 | 11.9 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.2 | 27.7 | 39.4 | 6 | 1011.5706 | 4084.445 | 11444.8209 | 3511 | 3.2597 | 4.8068 | 3.1 | 10.7 | 7.8 |  |  | 2.394 | 7.1292 | 32.597 | 34.2223
46023.325 | 9.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2677.2 | 568.8 | 44.7 | -5.9 | 50.8 | 58.8 | 0.8 | 3619 | 7.1 | 17 | 184 | 42 | -3.9 | -4 | 34.7 | 37 | 43 | 331 | 133 | 2000 | 11.6 | 11.9 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.1 | 27.7 | 40 | 6 | 1011.276 | 4085 | 11443.043 | 3619 | 3.1619 | 4.7068 | 1.9 | 10 | 7.1 |  |  | 2.4241 | 7.2245 | 31.6194 | 33.2612
46023.3254 | 10 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2657.6 | 578.6 | 44.5 | -5.5 | 53 | 61 | 0.8 | 3619 | 7.1 | 17 | 184 | 42 | -3.6 | -4.7 | 35.1 | 37.1 | 43.5 | 327 | 133 | 2000 | 11.7 | 12 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.1 | 27.7 | 40.3 | 6.4 | 1011.128 | 4085.2775 | 12204.9549 | 3619 | 3.3725 | 4.5932 | 0.8 | 9.4 | 6.6 |  |  | 2.4543 | 7.3263 | 33.7247 | 32.8887
46023.3257 | 10.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2657.6 | 578.6 | 44.5 | -5.5 | 54.5 | 62.5 | 0.7 | 3600 | 7.1 | 17 | 184 | 42 | -3.5 | -4.6 | 35.5 | 37.5 | 44 | 324 | 126 | 2000 | 11.9 | 12.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.1 | 27.5 | 40.75 | 6.5 | 1010.905 | 4085.6937 | 12304.6976 | 3600 | 3.418 | 4.5932 | 0.9 | 9 | 6.1 |  |  | 2.4843 | 7.4288 | 34.1797 | 33.0183
46023.3261 | 11 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2657.6 | 578.6 | 44.5 | -5.5 | 55.3 | 63.2 | 0.7 | 3600 | 7.1 | 17 | 184 | 42 | -3.6 | -4.7 | 36.1 | 37.8 | 44.2 | 324 | 119 | 2000 | 11.9 | 12.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.1 | 27.5 | 41 | 6.4 | 1010.7806 | 4085.925 | 12114.5896 | 3600 | 3.3652 | 4.5932 | 0.8 | 8.4 | 5.9 |  |  | 2.5143 | 7.5298 | 33.6516 | 33.1545
46023.3264 | 11.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2657.6 | 578.6 | 44.5 | -5.5 | 56 | 64.1 | 0.6 | 3595 | 7.1 | 17 | 180 | 42 | -3.6 | -4.7 | 37.4 | 38.1 | 44.6 | 324 | 113 | 2000 | 11.9 | 12.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.2 | 27.7 | 41.35 | 6.5 | 1010.6059 | 4086.2488 | 12392.2025 | 3595 | 3.4471 | 4.5932 | 0.8 | 7.1 | 5.6 |  |  | 2.5442 | 7.633 | 34.4707 | 33.5292
46023.3268 | 12 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2677.2 | 578.6 | 44.7 | -5.5 | 56.8 | 65.1 | 0.6 | 3595 | 7.2 | 18 | 180 | 42 | -3.5 | -4.6 | 39.7 | 38.5 | 45.1 | 324 | 113 | 2000 | 12.5 | 12.9 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.2 | 27.7 | 41.8 | 6.6 | 1010.3802 | 4086.665 | 12581.3238 | 3595 | 3.4997 | 4.627 | 0.9 | 5 | 5.1 |  |  | 2.5742 | 7.7379 | 34.9967 | 34.2047
46023.3271 | 12.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2687 | 578.6 | 44.9 | -5.5 | 58.1 | 66.2 | 0.6 | 3647 | 7.2 | 18 | 180 | 43 | -3.6 | -4.7 | 41.6 | 38.8 | 45.3 | 324 | 107 | 2000 | 12.9 | 13.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.2 | 27.5 | 42.05 | 6.5 | 1010.2544 | 4086.8962 | 12300.398 | 3647 | 3.3727 | 4.644 | 0.8 | 3.3 | 4.9 |  |  | 2.6046 | 7.8404 | 33.7274 | 34.2052
46023.3275 | 13 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2716.4 | 588.4 | 45.3 | -5.1 | 59.8 | 67.8 | 0.6 | 3647 | 7.3 | 18 | 180 | 43 | -3.4 | -4.6 | 42.4 | 39.2 | 45.6 | 324 | 101 | 2000 | 13 | 13.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.2 | 27.7 | 42.4 | 6.4 | 1010.0776 | 4087.22 | 12198.0739 | 3647 | 3.3447 | 4.6166 | 0.5 | 2.9 | 4.6 |  |  | 2.635 | 7.942 | 33.4469 | 34.0587
46023.3278 | 13.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 60 | 60 | 60 | 2726.2 | 588.4 | 45.5 | -5.1 | 61.4 | 69.2 | 0.8 | 3694 | 7.3 | 18 | 184 | 43 | -3.2 | -4.4 | 42.8 | 39.4 | 45.8 | 324 | 101 | 2000 | 13.1 | 13.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.1 | 27.3 | 42.6 | 6.4 | 1009.9763 | 4087.405 | 12021.2666 | 3694 | 3.2543 | 4.6332 | 0.7 | 2.7 | 4.3 |  |  | 2.6658 | 8.0422 | 32.5427 | 33.8369
46023.3282 | 14 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 59 | 58 | 59 | 2745.8 | 588.4 | 45.8 | -5.1 | 63.2 | 71.4 | 0.9 | 3694 | 7.3 | 18 | 184 | 44 | -3.3 | -4.4 | 43.3 | 39.8 | 46.1 | 324 | 101 | 2000 | 13.1 | 13.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50.1 | 27.3 | 42.95 | 6.3 | 1009.7985 | 4087.7288 | 11832.2877 | 3694 | 3.2031 | 4.6666 | 0.7 | 2.5 | 4 |  |  | 2.6965 | 8.1408 | 32.0311 | 33.349
46023.3285 | 14.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 58 | 58 | 58 | 2736 | 598.2 | 45.6 | -4.6 | 65.1 | 73.4 | 0.9 | 3711 | 7.2 | 18 | 184 | 44 | -3.2 | -4.3 | 43.6 | 40 | 46.1 | 324 | 101 | 2000 | 13.3 | 14.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50 | 27.7 | 43.05 | 6.1 | 1009.7475 | 4087.8212 | 11624.1993 | 3711 | 3.1324 | 4.5737 | 0.3 | 2 | 3.9 |  |  | 2.7275 | 8.2377 | 31.3236 | 32.6143
46023.3289 | 15 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 57 | 57 | 57 | 2755.7 | 608 | 45.9 | -4.2 | 66.8 | 75 | 1 | 3711 | 7.2 | 18 | 184 | 45 | -2.9 | -4 | 44 | 40.5 | 46.5 | 324 | 105 | 2000 | 13.9 | 22.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.5 | 43.5 | 6 | 1009.5176 | 4088.2375 | 11349.6562 | 3711 | 3.0584 | 4.5324 | 0.2 | 1.9 | 3.4 |  |  | 2.7584 | 8.3322 | 30.5838 | 31.9856
46023.3292 | 15.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 57 | 57 | 57 | 2745.8 | 608 | 45.8 | -4.2 | 67.8 | 76.1 | 1.1 | 3659 | 7.2 | 18 | 184 | 45 | -2.7 | -4 | 44.2 | 40.6 | 46.5 | 322 | 121 | 2000 | 14.2 | 28.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 43.55 | 5.9 | 1009.492 | 4088.2838 | 11241.5044 | 3659 | 3.0723 | 4.5161 | 0.2 | 1.6 | 3.4 |  |  | 2.7889 | 8.4259 | 30.7229 | 31.4408
46023.3296 | 16 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 56 | 55 | 56 | 2755.7 | 608 | 45.9 | -4.2 | 69.1 | 77.5 | 1.1 | 3659 | 7.2 | 19 | 185 | 46 | -2.7 | -3.9 | 44.2 | 41 | 46.5 | 322 | 121 | 2000 | 14.9 | 34.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 43.75 | 5.5 | 1009.3894 | 4088.4688 | 10478.7775 | 3659 | 2.8638 | 4.5324 | 0.3 | 1.7 | 3.4 |  |  | 2.8194 | 8.5132 | 28.6384 | 30.66
46023.3299 | 16.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 55 | 55 | 55 | 2745.8 | 608 | 45.8 | -4.2 | 70.1 | 78.8 | 1 | 3639 | 7 | 19 | 185 | 48 | -2.6 | -3.8 | 44.4 | 41.3 | 46.6 | 321 | 135 | 2000 | 15.5 | 37.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.1 | 43.95 | 5.3 | 1009.2865 | 4088.6537 | 9878.4482 | 3639 | 2.7146 | 4.5161 | 0.4 | 1.4 | 3.3 |  |  | 2.8497 | 8.5956 | 27.1461 | 29.683
46023.3303 | 17 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 56 | 57 | 56 | 2755.7 | 617.8 | 45.9 | -3.8 | 70.8 | 79.7 | 0.9 | 3639 | 7.2 | 19 | 185 | 50 | -2.3 | -3.6 | 44.4 | 41.6 | 46.8 | 321 | 148 | 2000 | 15.8 | 39.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50 | 27.7 | 44.2 | 5.2 | 1009.1577 | 4088.885 | 9905.9422 | 3639 | 2.7222 | 4.4605 | 0.2 | 1.5 | 3.2 |  |  | 2.88 | 8.6781 | 27.2216 | 28.8625
46023.3306 | 17.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 57 | 57 | 57 | 2785.1 | 608 | 46.4 | -4.2 | 71.4 | 80.4 | 0.9 | 3639 | 7.4 | 19 | 185 | 52 | -2.4 | -3.6 | 44.8 | 42 | 47.2 | 320 | 160 | 2000 | 16.1 | 40.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50 | 27.7 | 44.6 | 5.2 | 1008.9508 | 4089.255 | 9904.8075 | 3639 | 2.7218 | 4.5808 | 0.6 | 1.6 | 2.8 |  |  | 2.9103 | 8.7607 | 27.2185 | 28.1895
46023.3309 | 18 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 56 | 54 | 56 | 2804.7 | 608 | 46.7 | -4.2 | 72 | 81 | 0.9 | 3621 | 7.5 | 19 | 181 | 53 | -2.5 | -3.6 | 45 | 42.1 | 47.2 | 320 | 160 | 2000 | 16.8 | 40.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50 | 27.7 | 44.65 | 5.1 | 1008.9249 | 4089.3012 | 9714.1907 | 3621 | 2.6827 | 4.613 | 0.6 | 1.7 | 2.8 |  |  | 2.9405 | 8.8416 | 26.8274 | 27.4104
46023.3313 | 18.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 54 | 54 | 54 | 2794.9 | 617.8 | 46.5 | -3.8 | 72.5 | 81.5 | 0.9 | 3621 | 7.1 | 19 | 181 | 54 | -2.4 | -3.5 | 45.1 | 42.2 | 47.3 | 318 | 168 | 2000 | 17.8 | 39.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50 | 27.5 | 44.75 | 5.1 | 1008.873 | 4089.3938 | 9643.7743 | 3621 | 2.6633 | 4.524 | 0.3 | 1.4 | 2.7 |  |  | 2.9707 | 8.922 | 26.6329 | 27.0093
46023.3316 | 19 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 55 | 58 | 55 | 2804.7 | 617.8 | 46.7 | -3.8 | 73 | 82 | 1 | 3734 | 7.2 | 19 | 181 | 55 | -2 | -3.1 | 45.1 | 42.4 | 47.3 | 318 | 176 | 2000 | 18.4 | 40 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50 | 27.9 | 44.85 | 4.9 | 1008.821 | 4089.4862 | 9400.0878 | 3734 | 2.5174 | 4.5398 | 0.7 | 1.6 | 2.7 |  |  | 3.0018 | 9.0003 | 25.1743 | 26.6149
46023.332 | 19.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 57 | 58 | 57 | 2843.9 | 617.8 | 47.2 | -3.8 | 73.1 | 82.1 | 1 | 3734 | 7.6 | 20 | 181 | 56 | -2 | -3.2 | 45.3 | 42.7 | 47.6 | 318 | 186 | 2000 | 18.4 | 40.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 45.15 | 4.9 | 1008.6648 | 4089.7638 | 9331.892 | 3734 | 2.4992 | 4.6033 | 0.6 | 1.9 | 2.3 |  |  | 3.0329 | 9.0781 | 24.9917 | 26.1689
46023.3323 | 20 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 55 | 53 | 55 | 2843.9 | 617.8 | 47.2 | -3.8 | 73.5 | 82.5 | 1.1 | 3657 | 7.5 | 20 | 181 | 57 | -2.1 | -3.2 | 45.6 | 42.8 | 47.8 | 318 | 186 | 2000 | 18.8 | 40.3 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 45.3 | 5 | 1008.5866 | 4089.9025 | 9521.9228 | 3657 | 2.6038 | 4.6033 | 0.6 | 1.6 | 2.1 |  |  | 3.0634 | 9.1574 | 26.0375 | 25.9328
46023.3327 | 20.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 53 | 53 | 53 | 2834.1 | 617.8 | 47.1 | -3.8 | 74.2 | 83 | 1.1 | 3657 | 7.2 | 20 | 184 | 57 | -2.2 | -3.3 | 45.8 | 43 | 47.8 | 317 | 193 | 2000 | 19.6 | 39.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.5 | 45.4 | 4.8 | 1008.5343 | 4089.995 | 9074.7806 | 3657 | 2.4815 | 4.5874 | 0.5 | 1.3 | 2.1 |  |  | 3.0939 | 9.233 | 24.8148 | 25.5302
46023.333 | 21 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 54 | 56 | 54 | 2834.1 | 627.6 | 47.1 | -3.4 | 74.3 | 83.1 | 1.1 | 3780 | 7.2 | 20 | 184 | 58 | -1.9 | -3 | 45.8 | 43.3 | 47.8 | 317 | 201 | 2000 | 19.8 | 40.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 45.55 | 4.5 | 1008.4558 | 4090.1337 | 8569.1041 | 3780 | 2.267 | 4.5158 | 0.4 | 1.3 | 2.1 |  |  | 3.1254 | 9.3045 | 22.6696 | 24.7376
46023.3334 | 21.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 56 | 56 | 56 | 2863.5 | 627.6 | 47.5 | -3.4 | 74.3 | 83.1 | 1.1 | 3780 | 7.6 | 20 | 184 | 60 | -1.9 | -2.9 | 45.8 | 43.3 | 48 | 316 | 211 | 2000 | 19.7 | 41 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 45.65 | 4.7 | 1008.4034 | 4090.2263 | 8949.6906 | 3780 | 2.3676 | 4.5626 | 0.5 | 1.7 | 1.9 |  |  | 3.1569 | 9.379 | 23.6764 | 24.438
46023.3337 | 22 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 55 | 50 | 55 | 2873.3 | 617.8 | 47.6 | -3.8 | 74.5 | 83.1 | 1.1 | 3671 | 7.6 | 20 | 184 | 60 | -2.1 | -3.1 | 46.1 | 43.5 | 48.6 | 316 | 211 | 2000 | 20.1 | 40.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.5 | 46.05 | 5.1 | 1008.1933 | 4090.5963 | 9640.111 | 3671 | 2.626 | 4.6509 | 0.7 | 1.5 | 1.3 |  |  | 3.1875 | 9.4594 | 26.2602 | 24.6917
46023.3341 | 22.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 53 | 50 | 53 | 2883.1 | 617.8 | 47.9 | -3.4 | 74.6 | 83.1 | 1.1 | 3671 | 7.5 | 20 | 179 | 60 | -2.1 | -3.1 | 46.1 | 43.8 | 48.6 | 311 | 218 | 2000 | 20.6 | 39.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.9 | 46.2 | 4.8 | 1008.1142 | 4090.735 | 9204.6078 | 3671 | 2.5074 | 4.6667 | 0.3 | 1.8 | 1.2 |  |  | 3.2181 | 9.5361 | 25.0738 | 24.499
46023.3344 | 23 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 51 | 49 | 51 | 2883.1 | 627.6 | 47.8 | -3.4 | 74.8 | 83.1 | 1.1 | 3827 | 7.2 | 20 | 179 | 60 | -2 | -2.9 | 46.3 | 44 | 48.6 | 311 | 225 | 2000 | 21 | 39.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 28.1 | 46.3 | 4.6 | 1008.0615 | 4090.8275 | 8884.052 | 3827 | 2.3214 | 4.5938 | 0.5 | 1.5 | 1.3 |  |  | 3.25 | 9.6101 | 23.2141 | 24.1788
46023.3348 | 23.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 49 | 49 | 49 | 2863.5 | 637.4 | 47.5 | -3 | 75 | 83.2 | 1.1 | 3827 | 6.8 | 20 | 179 | 61 | -1.8 | -2.6 | 46.3 | 44 | 48.6 | 309 | 234 | 2000 | 21.3 | 40.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 28.1 | 46.3 | 4.6 | 1008.0615 | 4090.8275 | 8884.052 | 3827 | 2.3214 | 4.4925 | 0.4 | 1.2 | 1.3 |  |  | 3.2818 | 9.6841 | 23.2141 | 24.2877
46023.3351 | 24 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 50 | 55 | 50 | 2863.5 | 647.2 | 47.5 | -2.6 | 74.5 | 82.8 | 1.1 | 3621 | 7 | 20 | 179 | 62 | -1.6 | -2.3 | 46.1 | 44.2 | 48.3 | 309 | 234 | 2000 | 21.5 | 41.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 46.25 | 4.1 | 1008.0879 | 4090.7812 | 7805.7929 | 3621 | 2.1557 | 4.4244 | 0.3 | 1.4 | 1.6 |  |  | 3.312 | 9.7492 | 21.557 | 23.8639
46023.3355 | 24.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 52 | 55 | 52 | 2892.9 | 637.4 | 47.9 | -3 | 74.2 | 82.1 | 1.1 | 3621 | 7.3 | 20 | 179 | 63 | -1.7 | -2.4 | 46.1 | 44.2 | 48.6 | 311 | 243 | 2000 | 21.8 | 41.1 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 46.4 | 4.4 | 1008.0087 | 4090.92 | 8376.5744 | 3621 | 2.3133 | 4.5386 | 0.6 | 1.8 | 1.3 |  |  | 3.3422 | 9.819 | 23.1333 | 23.2385
46023.3358 | 25 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 52 | 46 | 52 | 2912.6 | 627.6 | 48.2 | -3.4 | 74.2 | 82 | 1.1 | 3477 | 7.5 | 20 | 184 | 63 | -1.9 | -2.6 | 46.3 | 44.4 | 49.2 | 311 | 251 | 2000 | 21.8 | 41 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.5 | 46.8 | 4.8 | 1007.7968 | 4091.29 | 9071.0162 | 3477 | 2.6089 | 4.6409 | 0.8 | 1.9 | 0.7 |  |  | 3.3712 | 9.8946 | 26.0886 | 23.4414
46023.3362 | 25.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 50 | 46 | 50 | 2892.9 | 627.6 | 47.9 | -3.4 | 74.3 | 82 | 1.1 | 3477 | 7.2 | 20 | 184 | 63 | -2 | -2.7 | 46.5 | 44.6 | 49.2 | 308 | 257 | 2000 | 22.4 | 40.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.5 | 46.9 | 4.6 | 1007.7438 | 4091.3825 | 8692.7957 | 3477 | 2.5001 | 4.6095 | 0.7 | 1.4 | 0.7 |  |  | 3.4001 | 9.967 | 25.0009 | 23.7988
46023.3365 | 26 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 48 | 45 | 48 | 2883.1 | 637.4 | 47.8 | -3 | 74.3 | 82 | 1.1 | 3681 | 6.8 | 20 | 184 | 63 | -1.7 | -2.5 | 46.5 | 44.8 | 49.2 | 308 | 257 | 2000 | 22.8 | 40.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.5 | 47 | 4.4 | 1007.6906 | 4091.475 | 8314.5975 | 3681 | 2.2588 | 4.5232 | 0.5 | 1.3 | 0.7 |  |  | 3.4308 | 10.0363 | 22.5879 | 23.6735
46023.3369 | 26.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 46 | 45 | 46 | 2892.9 | 637.4 | 47.9 | -3 | 74.1 | 81.8 | 1.1 | 3681 | 6.5 | 20 | 184 | 64 | -1.7 | -2.3 | 46.5 | 45 | 49.2 | 304 | 264 | 2000 | 23.2 | 40.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.9 | 47.1 | 4.2 | 1007.6374 | 4091.5675 | 8051.8604 | 3681 | 2.1874 | 4.5386 | 0.7 | 1.4 | 0.7 |  |  | 3.4615 | 10.1034 | 21.8741 | 23.737
46023.3372 | 27 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 46 | 46 | 46 | 2892.9 | 647.2 | 47.9 | -2.6 | 73.8 | 81.5 | 1 | 3472 | 6.5 | 20 | 181 | 64 | -1.7 | -2.2 | 46.5 | 45 | 49 | 304 | 258 | 2000 | 23.5 | 40.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.5 | 47 | 4 | 1007.6906 | 4091.475 | 7558.725 | 3472 | 2.1771 | 4.4699 | 0.4 | 1.4 | 0.9 |  |  | 3.4904 | 10.1664 | 21.7705 | 23.4644
46023.3375 | 27.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 46 | 46 | 46 | 2912.6 | 637.4 | 48.2 | -3 | 73.7 | 81.4 | 1 | 3472 | 6.6 | 20 | 181 | 64 | -1.7 | -2.2 | 46.5 | 45.1 | 49.2 | 288 | 258 | 2000 | 23.4 | 40.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.5 | 47.15 | 4.1 | 1007.6108 | 4091.6137 | 7747.342 | 3472 | 2.2314 | 4.5695 | 0.8 | 1.7 | 0.7 |  |  | 3.5194 | 10.231 | 22.3138 | 22.7094
46023.3379 | 28 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 45 | 44 | 45 | 2912.6 | 637.4 | 48.2 | -3 | 73.7 | 81.2 | 1 | 3297 | 6.6 | 20 | 181 | 64 | -1.8 | -2.3 | 46.6 | 45.3 | 49.4 | 287 | 258 | 2000 | 23.5 | 40.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.5 | 47.35 | 4.1 | 1007.5041 | 4091.7987 | 7746.8723 | 3297 | 2.3497 | 4.5695 | 0.7 | 1.6 | 0.5 |  |  | 3.5468 | 10.2955 | 23.4967 | 22.4086
46023.3382 | 28.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 44 | 44 | 44 | 2902.8 | 647.2 | 48.1 | -2.6 | 73.7 | 81.2 | 0.9 | 3297 | 6.3 | 20 | 181 | 64 | -1.7 | -2.2 | 46.6 | 45.3 | 49.2 | 287 | 254 | 2000 | 23.6 | 41 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.9 | 47.25 | 3.9 | 1007.5575 | 4091.7063 | 7476.3881 | 3297 | 2.2676 | 4.4852 | 0.4 | 1.5 | 0.7 |  |  | 3.5743 | 10.3578 | 22.6763 | 22.4263
46023.3386 | 29 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 45 | 48 | 45 | 2912.6 | 647.2 | 48.2 | -2.6 | 73.7 | 81.2 | 0.9 | 3271 | 6.5 | 21 | 181 | 64 | -1.6 | -2.1 | 46.6 | 45.5 | 49.4 | 286 | 250 | 2000 | 23.7 | 41.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50 | 27.9 | 47.45 | 3.9 | 1007.4507 | 4091.8913 | 7475.934 | 3271 | 2.2855 | 4.5003 | 0.5 | 1.6 | 0.6 |  |  | 3.6016 | 10.4201 | 22.8552 | 22.6225
46023.3389 | 29.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 47 | 48 | 47 | 2932.2 | 637.4 | 48.3 | -2.6 | 73.8 | 81.2 | 0.9 | 3271 | 6.8 | 21 | 180 | 65 | -1.6 | -2.1 | 46.6 | 45.5 | 49.4 | 286 | 258 | 2000 | 23.4 | 41.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50 | 27.7 | 47.45 | 3.9 | 1007.4507 | 4091.8913 | 7422.343 | 3271 | 2.2691 | 4.6003 | 0.5 | 1.7 | 0.6 |  |  | 3.6288 | 10.482 | 22.6914 | 22.8067
46023.3393 | 30 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 45 | 37 | 45 | 2942 | 637.4 | 48.6 | -3 | 74.1 | 81.5 | 0.9 | 3225 | 6.7 | 21 | 180 | 65 | -1.7 | -2.2 | 47 | 45.8 | 50 | 287 | 258 | 2000 | 23.6 | 41.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 50 | 27.7 | 47.9 | 4.2 | 1007.2097 | 4092.3075 | 7992.1932 | 3225 | 2.4782 | 4.6156 | 0.8 | 1.6 | 0 |  |  | 3.6557 | 10.5486 | 24.782 | 23.3003
46023.3396 | 30.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 43 | 37 | 43 | 2922.4 | 647.2 | 48.3 | -2.6 | 74.2 | 81.8 | 1 | 3225 | 6.3 | 21 | 180 | 65 | -1.5 | -2 | 47 | 45.6 | 49.6 | 287 | 254 | 2000 | 24 | 41.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.9 | 47.6 | 4 | 1007.3705 | 4092.03 | 7667.2741 | 3225 | 2.3774 | 4.5155 | 0.6 | 1.3 | 0.3 |  |  | 3.6826 | 10.6125 | 23.7745 | 23.3559
46023.34 | 31 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 41 | 39 | 41 | 2922.4 | 657 | 48.3 | -2.2 | 74.2 | 81.8 | 1 | 3314 | 6 | 20 | 180 | 65 | -1.4 | -1.9 | 47 | 45.8 | 49.6 | 282 | 242 | 2000 | 24 | 41.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.9 | 47.7 | 3.8 | 1007.317 | 4092.1225 | 7283.6878 | 3314 | 2.1979 | 4.4481 | 0.3 | 1.3 | 0.3 |  |  | 3.7102 | 10.6732 | 21.9785 | 23.2163
46023.3403 | 31.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 39 | 39 | 39 | 2912.6 | 657 | 48.2 | -2.2 | 73.8 | 81.7 | 1.1 | 3314 | 5.7 | 20 | 180 | 65 | -1.3 | -1.7 | 46.8 | 45.8 | 49.6 | 282 | 235 | 2000 | 24.1 | 41.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 47.7 | 3.8 | 1007.317 | 4092.1225 | 7231.475 | 3314 | 2.1821 | 4.4332 | 0.5 | 1.4 | 0.3 |  |  | 3.7378 | 10.7334 | 21.821 | 23.0095
46023.3407 | 32 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 40 | 40 | 40 | 2922.4 | 657 | 48.3 | -2.2 | 73.4 | 81.4 | 1.1 | 3047 | 5.8 | 20 | 179 | 65 | -1.3 | -1.7 | 46.8 | 46 | 49.6 | 280 | 235 | 2000 | 24.2 | 41.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.9 | 47.8 | 3.6 | 1007.2634 | 4092.215 | 6900.1247 | 3047 | 2.2646 | 4.4481 | 0.5 | 1.5 | 0.3 |  |  | 3.7632 | 10.7909 | 22.6456 | 23.0003
46023.341 | 32.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 40 | 40 | 40 | 2922.4 | 657 | 48.3 | -2.2 | 73.2 | 81.1 | 1.1 | 3047 | 5.9 | 20 | 179 | 65 | -1.3 | -1.7 | 46.8 | 46 | 49.6 | 280 | 235 | 2000 | 24.1 | 42 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 47.8 | 3.6 | 1007.2634 | 4092.215 | 6850.6614 | 3047 | 2.2483 | 4.4481 | 0.5 | 1.5 | 0.3 |  |  | 3.7886 | 10.848 | 22.4833 | 22.5406
46023.3414 | 33 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 41 | 41 | 41 | 2922.4 | 657 | 48.3 | -2.2 | 73.2 | 81 | 1.1 | 2906 | 5.9 | 20 | 179 | 65 | -1.1 | -1.6 | 47 | 46.1 | 49.6 | 282 | 235 | 2000 | 24.1 | 42.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 47.85 | 3.5 | 1007.2365 | 4092.2613 | 6660.2632 | 2906 | 2.2919 | 4.4481 | 0.6 | 1.3 | 0.3 |  |  | 3.8128 | 10.9035 | 22.919 | 22.3695
46023.3417 | 33.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 41 | 41 | 41 | 2942 | 657 | 48.6 | -2.2 | 73.2 | 80.8 | 1.1 | 2975 | 6 | 21 | 179 | 65 | -1.1 | -1.6 | 47 | 46.1 | 49.8 | 282 | 238 | 2000 | 24 | 42.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.5 | 47.95 | 3.7 | 1007.1829 | 4092.3538 | 6989.7986 | 2975 | 2.3495 | 4.4779 | 0.6 | 1.6 | 0.1 |  |  | 3.8376 | 10.9618 | 23.4951 | 22.6728
46023.3421 | 34 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 40 | 39 | 40 | 2942 | 657 | 48.6 | -2.2 | 73.2 | 81 | 1.1 | 2975 | 5.9 | 20 | 184 | 65 | -1.2 | -1.7 | 47 | 46.1 | 49.8 | 279 | 238 | 2000 | 24 | 42.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 47.95 | 3.7 | 1007.1829 | 4092.3538 | 7040.6335 | 2975 | 2.3666 | 4.4779 | 0.5 | 1.6 | 0.1 |  |  | 3.8624 | 11.0204 | 23.666 | 23.0418
46023.3424 | 34.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 39 | 39 | 39 | 2932.2 | 657 | 48.5 | -2.2 | 73.2 | 81 | 1.1 | 2978 | 5.7 | 21 | 184 | 65 | -1.2 | -1.7 | 47 | 46.3 | 49.8 | 279 | 235 | 2000 | 24.1 | 42.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.5 | 48.05 | 3.5 | 1007.1291 | 4092.4462 | 6611.7683 | 2978 | 2.2202 | 4.463 | 0.5 | 1.5 | 0.1 |  |  | 3.8872 | 11.0755 | 22.202 | 22.9531
46023.3428 | 35 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 40 | 40 | 40 | 2942 | 657 | 48.6 | -2.2 | 73.2 | 81 | 1.1 | 2978 | 5.7 | 21 | 184 | 65 | -1.1 | -1.6 | 47 | 46.3 | 49.8 | 277 | 231 | 2000 | 24.3 | 42.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.5 | 48.05 | 3.5 | 1007.1291 | 4092.4462 | 6611.7683 | 2978 | 2.2202 | 4.4779 | 0.6 | 1.6 | 0.1 |  |  | 3.912 | 11.1306 | 22.202 | 22.8968
46023.3431 | 35.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 40 | 40 | 40 | 2961.6 | 666.8 | 48.8 | -2.2 | 73.2 | 81 | 1.1 | 2921 | 5.9 | 21 | 184 | 65 | -1 | -1.5 | 47.1 | 46.3 | 49.8 | 277 | 235 | 2000 | 24.2 | 42.2 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 48.05 | 3.5 | 1007.1291 | 4092.4462 | 6659.8539 | 2921 | 2.28 | 4.4415 | 0.7 | 1.7 | 0.1 |  |  | 3.9364 | 11.1861 | 22.7999 | 22.873
46023.3434 | 36 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 39 | 38 | 39 | 2942 | 666.8 | 48.8 | -1.8 | 73.4 | 81.1 | 1.2 | 2921 | 5.8 | 20 | 184 | 65 | -1 | -1.5 | 47.1 | 46.3 | 50 | 276 | 235 | 2000 | 24.2 | 42.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 48.15 | 3.7 | 1007.0753 | 4092.5388 | 7040.2 | 2921 | 2.4102 | 4.4121 | 0.3 | 1.7 | -0.1 |  |  | 3.9607 | 11.2448 | 24.102 | 22.9944
46023.3438 | 36.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 38 | 38 | 38 | 2942 | 666.8 | 48.6 | -1.8 | 73.4 | 81.1 | 1.2 | 2923 | 5.6 | 21 | 179 | 65 | -1 | -1.5 | 47.1 | 46.3 | 49.8 | 276 | 231 | 2000 | 24.4 | 42.4 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.7 | 48.05 | 3.5 | 1007.1291 | 4092.4462 | 6659.8539 | 2923 | 2.2784 | 4.4121 | 0.3 | 1.5 | 0 |  |  | 3.9851 | 11.3003 | 22.7843 | 22.8181
46023.3441 | 37 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 39 | 40 | 39 | 2942 | 666.8 | 48.6 | -1.8 | 73.4 | 81.1 | 1.2 | 2923 | 5.6 | 20 | 179 | 65 | -1 | -1.5 | 47.1 | 46.5 | 49.8 | 274 | 227 | 2000 | 24.5 | 42.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.7 | 48.15 | 3.3 | 1007.0753 | 4092.5388 | 6279.0973 | 2923 | 2.1482 | 4.4121 | 0.3 | 1.5 | 0 |  |  | 4.0094 | 11.3526 | 21.4817 | 22.674
46023.3445 | 37.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 40 | 40 | 40 | 2961.6 | 657 | 48.9 | -2.2 | 73.4 | 81.2 | 1.2 | 2879 | 5.9 | 20 | 179 | 65 | -1 | -1.5 | 47.1 | 46.5 | 50 | 274 | 235 | 2000 | 24.2 | 42.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.9 | 48.25 | 3.5 | 1007.0215 | 4092.6312 | 6707.5257 | 2879 | 2.3298 | 4.5078 | 0.7 | 1.8 | -0.2 |  |  | 4.0334 | 11.4085 | 23.2981 | 22.8932
46023.3448 | 38 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 39 | 38 | 39 | 2961.6 | 657 | 48.9 | -2.2 | 73.8 | 81.5 | 1.2 | 2879 | 5.8 | 20 | 179 | 65 | -1 | -1.5 | 47.2 | 46.5 | 50 | 275 | 235 | 2000 | 24.2 | 42.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 28.1 | 48.25 | 3.5 | 1007.0215 | 4092.6312 | 6755.6083 | 2879 | 2.3465 | 4.5078 | 0.7 | 1.7 | -0.2 |  |  | 4.0574 | 11.4648 | 23.4651 | 23.0262
46023.3452 | 38.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 38 | 38 | 38 | 2951.8 | 666.8 | 48.8 | -1.8 | 73.8 | 81.7 | 1.2 | 2933 | 5.7 | 21 | 181 | 65 | -1 | -1.5 | 47.2 | 46.5 | 50 | 275 | 231 | 2000 | 24.5 | 42.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.7 | 48.25 | 3.5 | 1007.0215 | 4092.6312 | 6659.4431 | 2933 | 2.2705 | 4.4268 | 0.3 | 1.6 | -0.2 |  |  | 4.0819 | 11.5203 | 22.7052 | 22.7469
46023.3455 | 39 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 38 | 38 | 38 | 2961.6 | 666.8 | 48.9 | -1.8 | 73.7 | 81.7 | 1.2 | 2933 | 5.7 | 21 | 181 | 66 | -1 | -1.5 | 47.2 | 46.6 | 50 | 274 | 227 | 2000 | 24.6 | 42.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.7 | 48.3 | 3.4 | 1006.9945 | 4092.6775 | 6469.0733 | 2933 | 2.2056 | 4.4415 | 0.3 | 1.7 | -0.2 |  |  | 4.1063 | 11.5742 | 22.0562 | 22.6013
46023.3459 | 39.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 38 | 38 | 38 | 2951.8 | 666.8 | 48.8 | -1.8 | 73.8 | 81.7 | 1.2 | 2933 | 5.7 | 20 | 181 | 66 | -1 | -1.4 | 47.2 | 46.6 | 50 | 274 | 227 | 2000 | 24.5 | 42.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.9 | 48.3 | 3.4 | 1006.9945 | 4092.6775 | 6515.7814 | 2933 | 2.2215 | 4.4268 | 0.4 | 1.6 | -0.2 |  |  | 4.1307 | 11.6285 | 22.2154 | 22.748
46023.3462 | 40 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 38 | 38 | 38 | 2961.6 | 666.8 | 48.9 | -1.8 | 73.8 | 81.8 | 1.2 | 2848 | 5.7 | 20 | 181 | 66 | -1.1 | -1.5 | 47.2 | 46.6 | 50 | 273 | 227 | 2000 | 24.5 | 42.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.7 | 48.3 | 3.4 | 1006.9945 | 4092.6775 | 6469.0733 | 2848 | 2.2714 | 4.4415 | 0.3 | 1.7 | -0.2 |  |  | 4.1545 | 11.6824 | 22.7144 | 22.6313
46023.3466 | 40.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 38 | 38 | 38 | 2961.6 | 666.8 | 48.9 | -1.8 | 74 | 81.8 | 1.2 | 2848 | 5.7 | 21 | 181 | 66 | -0.9 | -1.4 | 47.2 | 46.6 | 50 | 273 | 227 | 2000 | 24.5 | 42.7 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 28.1 | 48.3 | 3.4 | 1006.9945 | 4092.6775 | 6562.4895 | 2848 | 2.3042 | 4.4415 | 0.4 | 1.7 | -0.2 |  |  | 4.1782 | 11.7371 | 23.0424 | 22.5467
46023.3469 | 41 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 37 | 36 | 37 | 2961.6 | 666.8 | 48.9 | -1.8 | 74.1 | 82 | 1.2 | 2852 | 5.5 | 21 | 183 | 66 | -0.9 | -1.4 | 47.2 | 46.6 | 50.2 | 272 | 227 | 2000 | 24.5 | 42.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 28.1 | 48.4 | 3.6 | 1006.9406 | 4092.77 | 6948.3032 | 2852 | 2.4363 | 4.4415 | 0.4 | 1.7 | -0.4 |  |  | 4.202 | 11.795 | 24.3629 | 22.8783
46023.3473 | 41.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 36 | 36 | 36 | 2951.8 | 666.8 | 48.8 | -1.8 | 74 | 82 | 1.2 | 2852 | 5.4 | 21 | 183 | 66 | -0.9 | -1.3 | 47.2 | 46.6 | 50 | 272 | 219 | 2000 | 25.1 | 42.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.5 | 48.3 | 3.4 | 1006.9945 | 4092.6775 | 6422.3652 | 2852 | 2.2519 | 4.4268 | 0.5 | 1.6 | -0.2 |  |  | 4.2257 | 11.8485 | 22.5188 | 22.9708
46023.3476 | 42 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 37 | 38 | 37 | 2961.6 | 666.8 | 48.9 | -1.8 | 73.8 | 82 | 1.2 | 2812 | 5.4 | 21 | 183 | 66 | -0.9 | -1.3 | 47.2 | 46.8 | 50 | 271 | 219 | 2000 | 25.1 | 42.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 28.1 | 48.4 | 3.2 | 1006.9406 | 4092.77 | 6176.2695 | 2812 | 2.1964 | 4.4415 | 0.5 | 1.7 | -0.2 |  |  | 4.2492 | 11.9 | 21.964 | 22.9205
46023.348 | 42.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 38 | 38 | 38 | 2971.4 | 666.8 | 49 | -1.8 | 74 | 82 | 1.2 | 2812 | 5.7 | 21 | 183 | 66 | -0.9 | -1.3 | 47.2 | 46.8 | 50.2 | 271 | 223 | 2000 | 24.7 | 42.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 28.1 | 48.5 | 3.4 | 1006.8866 | 4092.8625 | 6562.0827 | 2812 | 2.3336 | 4.4562 | 0.5 | 1.8 | -0.4 |  |  | 4.2726 | 11.9547 | 23.336 | 23.0448
46023.3483 | 43 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 37 | 36 | 37 | 2971.4 | 657 | 49 | -2.2 | 74.5 | 82.3 | 1.2 | 2769 | 5.6 | 21 | 179 | 66 | -1.1 | -1.4 | 47.3 | 46.8 | 50.2 | 270 | 227 | 2000 | 24.5 | 42.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.7 | 48.5 | 3.4 | 1006.8866 | 4092.8625 | 6468.6723 | 2769 | 2.3361 | 4.5227 | 0.8 | 1.7 | -0.4 |  |  | 4.2957 | 12.0086 | 23.361 | 23.1085
46023.3487 | 43.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 36 | 36 | 36 | 2961.6 | 666.8 | 48.9 | -1.8 | 74.5 | 82.6 | 1.2 | 2769 | 5.4 | 21 | 179 | 66 | -0.9 | -1.4 | 47.3 | 46.8 | 50.2 | 270 | 219 | 2000 | 25 | 42.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.5 | 48.5 | 3.4 | 1006.8866 | 4092.8625 | 6421.9671 | 2769 | 2.3192 | 4.4415 | 0.4 | 1.6 | -0.4 |  |  | 4.3188 | 12.0621 | 23.1924 | 22.8744
46023.349 | 44 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 36 | 36 | 36 | 2961.6 | 666.8 | 48.9 | -1.8 | 74.3 | 82.6 | 1.2 | 2822 | 5.4 | 21 | 179 | 66 | -0.9 | -1.3 | 47.3 | 46.8 | 50.2 | 269 | 219 | 2000 | 25.1 | 42.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.7 | 48.5 | 3.4 | 1006.8866 | 4092.8625 | 6468.6723 | 2822 | 2.2922 | 4.4415 | 0.5 | 1.6 | -0.4 |  |  | 4.3423 | 12.116 | 22.9223 | 22.9551
46023.3494 | 44.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 36 | 36 | 36 | 2961.6 | 666.8 | 48.9 | -1.8 | 74.2 | 82.6 | 1.2 | 2822 | 5.4 | 21 | 179 | 66 | -0.9 | -1.3 | 47.3 | 46.8 | 50.2 | 269 | 219 | 2000 | 25.1 | 42.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.7 | 48.5 | 3.4 | 1006.8866 | 4092.8625 | 6468.6723 | 2822 | 2.2922 | 4.4415 | 0.5 | 1.6 | -0.4 |  |  | 4.3658 | 12.1699 | 22.9223 | 23.1468
46023.3497 | 45 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 36 | 36 | 36 | 2971.4 | 666.8 | 49 | -1.8 | 74.3 | 82.6 | 1.2 | 2730 | 5.4 | 21 | 179 | 66 | -0.8 | -1.2 | 47.3 | 46.8 | 50.2 | 268 | 219 | 2000 | 25.1 | 42.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.5 | 48.5 | 3.4 | 1006.8866 | 4092.8625 | 6421.9671 | 2730 | 2.3524 | 4.4562 | 0.6 | 1.7 | -0.4 |  |  | 4.3885 | 12.2235 | 23.5237 | 23.1843
46023.35 | 45.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 36 | 36 | 36 | 2971.4 | 666.8 | 49 | -1.8 | 74.5 | 82.6 | 1.2 | 2730 | 5.4 | 21 | 179 | 66 | -0.9 | -1.2 | 47.3 | 46.8 | 50.2 | 268 | 219 | 2000 | 25.1 | 42.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.7 | 48.5 | 3.4 | 1006.8866 | 4092.8625 | 6468.6723 | 2730 | 2.3695 | 4.4562 | 0.6 | 1.7 | -0.4 |  |  | 4.4113 | 12.2774 | 23.6948 | 23.2511
46023.3504 | 46 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 36 | 36 | 36 | 2971.4 | 666.8 | 49 | -1.8 | 74.6 | 82.8 | 1.2 | 2738 | 5.4 | 21 | 179 | 66 | -0.9 | -1.2 | 47.3 | 47 | 50.2 | 267 | 219 | 2000 | 25.1 | 42.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.9 | 48.6 | 3.2 | 1006.8326 | 4092.955 | 6131.9294 | 2738 | 2.2396 | 4.4562 | 0.6 | 1.7 | -0.4 |  |  | 4.4341 | 12.3285 | 22.3957 | 23.0917
46023.3507 | 46.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 36 | 36 | 36 | 2971.4 | 666.8 | 49 | -1.8 | 74.6 | 83 | 1.2 | 2738 | 5.4 | 21 | 179 | 66 | -0.9 | -1.2 | 47.3 | 47 | 50.2 | 267 | 219 | 2000 | 25.1 | 42.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.9 | 48.6 | 3.2 | 1006.8326 | 4092.955 | 6131.9294 | 2738 | 2.2396 | 4.4562 | 0.6 | 1.7 | -0.4 |  |  | 4.4569 | 12.3796 | 22.3957 | 22.9864
46023.3511 | 47 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 36 | 36 | 36 | 2971.4 | 666.8 | 49 | -1.8 | 74.7 | 83 | 1.2 | 2740 | 5.4 | 21 | 179 | 66 | -0.9 | -1.2 | 47.3 | 47 | 50.2 | 266 | 219 | 2000 | 25.1 | 42.8 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.5 | 48.6 | 3.2 | 1006.8326 | 4092.955 | 6044.0165 | 2740 | 2.2058 | 4.4562 | 0.6 | 1.7 | -0.4 |  |  | 4.4798 | 12.4299 | 22.0585 | 22.8136
46023.3514 | 47.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 36 | 36 | 36 | 2971.4 | 666.8 | 49 | -1.8 | 74.8 | 83.1 | 1.2 | 2740 | 5.4 | 21 | 182 | 66 | -0.9 | -1.3 | 47.3 | 47 | 50.2 | 266 | 219 | 2000 | 25.1 | 42.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.7 | 48.6 | 3.2 | 1006.8326 | 4092.955 | 6087.973 | 2740 | 2.2219 | 4.4562 | 0.5 | 1.7 | -0.4 |  |  | 4.5026 | 12.4807 | 22.2189 | 22.5527
46023.3518 | 48 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 36 | 36 | 36 | 2981.2 | 666.8 | 49.2 | -1.8 | 74.8 | 83.1 | 1.1 | 2741 | 5.4 | 21 | 182 | 66 | -0.9 | -1.2 | 47.3 | 47 | 50.4 | 265 | 219 | 2000 | 25.1 | 42.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.9 | 48.7 | 3.4 | 1006.7784 | 4093.0475 | 6514.9722 | 2741 | 2.3769 | 4.4709 | 0.6 | 1.9 | -0.5 |  |  | 4.5254 | 12.5349 | 23.7686 | 22.5674
46023.3521 | 48.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 36 | 36 | 36 | 2981.2 | 666.8 | 49.2 | -1.8 | 74.8 | 83.2 | 1.2 | 2741 | 5.4 | 21 | 182 | 66 | -0.8 | -1.2 | 47.3 | 47 | 50.4 | 265 | 219 | 2000 | 25.2 | 43 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.9 | 48.7 | 3.4 | 1006.7784 | 4093.0475 | 6514.9722 | 2741 | 2.3769 | 4.4709 | 0.6 | 1.9 | -0.5 |  |  | 4.5483 | 12.5892 | 23.7686 | 22.842
46023.3525 | 49 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 35 | 32 | 35 | 2981.2 | 666.8 | 49.2 | -1.8 | 75 | 83.2 | 1.2 | 2745 | 5.3 | 21 | 182 | 66 | -0.9 | -1.2 | 47.3 | 47.1 | 50.4 | 266 | 219 | 2000 | 25.2 | 43 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.5 | 48.75 | 3.3 | 1006.7514 | 4093.0938 | 6232.6007 | 2745 | 2.2705 | 4.4709 | 0.6 | 1.9 | -0.6 |  |  | 4.5711 | 12.6412 | 22.7053 | 22.904
46023.3528 | 49.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 33 | 32 | 33 | 2971.4 | 666.8 | 49 | -1.8 | 75 | 83.3 | 1.1 | 2745 | 5.2 | 21 | 182 | 66 | -0.9 | -1.2 | 47.3 | 47.1 | 50.4 | 266 | 211 | 2000 | 25.5 | 43 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.9 | 48.75 | 3.3 | 1006.7514 | 4093.0938 | 6323.2567 | 2745 | 2.3036 | 4.4562 | 0.6 | 1.7 | -0.5 |  |  | 4.594 | 12.6939 | 23.0355 | 23.0994
46023.3532 | 50 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 33 | 33 | 33 | 2961.6 | 676.7 | 48.9 | -1.4 | 75.1 | 83.2 | 1.1 | 2709 | 4.9 | 21 | 181 | 66 | -0.8 | -1 | 47.3 | 47.1 | 50.2 | 264 | 211 | 2000 | 26.1 | 43.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.9 | 48.65 | 3.1 | 1006.8055 | 4093.0012 | 5940.2142 | 2709 | 2.1928 | 4.3765 | 0.4 | 1.6 | -0.3 |  |  | 4.6166 | 12.7434 | 21.9277 | 23.0411
46023.3535 | 50.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 33 | 33 | 33 | 2961.6 | 676.7 | 48.9 | -1.4 | 75.2 | 83.2 | 1.1 | 2709 | 5.1 | 21 | 181 | 66 | -0.7 | -1 | 47.3 | 47.1 | 50.2 | 263 | 207 | 2000 | 26.1 | 43.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.9 | 48.65 | 3.1 | 1006.8055 | 4093.0012 | 5940.2142 | 2709 | 2.1928 | 4.3765 | 0.4 | 1.6 | -0.3 |  |  | 4.6392 | 12.7929 | 21.9277 | 22.673
46023.3539 | 51 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 34 | 35 | 34 | 2971.4 | 676.7 | 49 | -1.4 | 75.2 | 83.2 | 1.1 | 2548 | 5.2 | 21 | 181 | 66 | -0.7 | -0.9 | 47.3 | 47.1 | 50.2 | 262 | 207 | 2000 | 26.1 | 43.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 48.65 | 3.1 | 1006.8055 | 4093.0012 | 5897.632 | 2548 | 2.3146 | 4.391 | 0.5 | 1.7 | -0.3 |  |  | 4.6604 | 12.842 | 23.1461 | 22.5485
46023.3542 | 51.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 35 | 35 | 35 | 2981.2 | 666.8 | 49.2 | -1.8 | 75.4 | 83.3 | 1.1 | 2548 | 5.3 | 21 | 181 | 66 | -0.8 | -1.1 | 47.3 | 47.1 | 50.4 | 261 | 215 | 2000 | 25.5 | 43.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.9 | 48.75 | 3.3 | 1006.7514 | 4093.0938 | 6323.2567 | 2548 | 2.4817 | 4.4709 | 0.7 | 1.9 | -0.5 |  |  | 4.6816 | 12.8947 | 24.8165 | 22.9707
46023.3546 | 52 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 34 | 31 | 34 | 2991 | 666.8 | 49.2 | -1.8 | 75.5 | 83.4 | 1.1 | 2602 | 5.3 | 21 | 181 | 66 | -0.9 | -1.2 | 47.5 | 47.1 | 50.4 | 262 | 215 | 2000 | 25.5 | 43.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.9 | 48.75 | 3.3 | 1006.7514 | 4093.0938 | 6323.2567 | 2602 | 2.4302 | 4.4856 | 0.6 | 1.7 | -0.5 |  |  | 4.7033 | 12.9474 | 24.3015 | 23.2239
46023.3549 | 52.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 32 | 31 | 32 | 2971.4 | 676.7 | 49 | -1.4 | 75.7 | 83.5 | 1.1 | 2602 | 5.1 | 21 | 181 | 66 | -0.7 | -1.1 | 47.5 | 47.2 | 50.6 | 262 | 211 | 2000 | 26 | 43.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.3 | 48.9 | 3.4 | 1006.6701 | 4093.2325 | 6374.4671 | 2602 | 2.4498 | 4.391 | 0.3 | 1.5 | -0.7 |  |  | 4.725 | 13.0005 | 24.4983 | 23.738
46023.3553 | 53 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 30 | 30 | 2971.4 | 676.7 | 49 | -1.4 | 75.7 | 83.6 | 1.1 | 2658 | 4.8 | 20 | 181 | 66 | -0.6 | -0.9 | 47.5 | 47.2 | 50.4 | 259 | 200 | 2000 | 26.7 | 43.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 48.8 | 3.2 | 1006.7243 | 4093.14 | 6087.5935 | 2658 | 2.2903 | 4.391 | 0.5 | 1.5 | -0.5 |  |  | 4.7472 | 13.0513 | 22.9029 | 23.9331
46023.3556 | 53.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 30 | 30 | 2961.6 | 676.7 | 48.9 | -1.4 | 75.5 | 83.5 | 1.1 | 2658 | 4.7 | 21 | 181 | 66 | -0.6 | -0.8 | 47.3 | 47.2 | 50.2 | 258 | 196 | 2000 | 27.1 | 43.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 28.1 | 48.7 | 3 | 1006.7784 | 4093.0475 | 5789.7128 | 2658 | 2.1782 | 4.3765 | 0.6 | 1.6 | -0.4 |  |  | 4.7693 | 13.0995 | 21.7822 | 23.6603
46023.3559 | 54 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 31 | 32 | 31 | 2961.6 | 676.7 | 48.9 | -1.4 | 75.5 | 83.5 | 1.1 | 2433 | 4.7 | 20 | 181 | 66 | -0.7 | -0.8 | 47.3 | 47.2 | 50.2 | 257 | 196 | 2000 | 26.5 | 44.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 28.1 | 48.7 | 3 | 1006.7784 | 4093.0475 | 5789.7128 | 2433 | 2.3797 | 4.3765 | 0.6 | 1.6 | -0.4 |  |  | 4.7896 | 13.1478 | 23.7966 | 23.4563
46023.3563 | 54.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 32 | 32 | 32 | 2971.4 | 676.7 | 49 | -1.4 | 75.7 | 83.5 | 1.1 | 2433 | 5 | 21 | 179 | 66 | -0.6 | -0.8 | 47.3 | 47.2 | 50.2 | 256 | 200 | 2000 | 26.4 | 44.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.9 | 48.7 | 3 | 1006.7784 | 4093.0475 | 5748.5049 | 2433 | 2.3627 | 4.391 | 0.6 | 1.7 | -0.3 |  |  | 4.8099 | 13.1957 | 23.6272 | 23.3215
46023.3566 | 55 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 31 | 28 | 31 | 2981.2 | 676.7 | 49.2 | -1.4 | 76 | 83.6 | 1.1 | 2405 | 5 | 21 | 179 | 66 | -0.6 | -0.8 | 47.3 | 47.2 | 50.4 | 257 | 204 | 2000 | 26.5 | 43.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 28.1 | 48.8 | 3.2 | 1006.7243 | 4093.14 | 6175.501 | 2405 | 2.5678 | 4.4055 | 0.6 | 1.9 | -0.5 |  |  | 4.8299 | 13.2471 | 25.6778 | 23.5573
46023.357 | 55.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 28 | 29 | 2971.4 | 676.7 | 49 | -1.4 | 76.1 | 83.7 | 1.1 | 2405 | 4.7 | 21 | 179 | 66 | -0.5 | -0.8 | 47.3 | 47.3 | 50.4 | 257 | 196 | 2000 | 27.2 | 43.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 48.85 | 3.1 | 1006.6972 | 4093.1863 | 5897.2641 | 2405 | 2.4521 | 4.391 | 0.6 | 1.7 | -0.5 |  |  | 4.8499 | 13.2963 | 24.5208 | 23.8809
46023.3573 | 56 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 30 | 29 | 2951.8 | 686.5 | 48.8 | -1 | 76 | 83.7 | 1.1 | 2472 | 4.5 | 20 | 179 | 66 | -0.5 | -0.7 | 47.3 | 47.2 | 50 | 255 | 196 | 2000 | 27.6 | 44 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 48.6 | 2.8 | 1006.8326 | 4092.955 | 5326.9763 | 2472 | 2.1549 | 4.2998 | 0.3 | 1.5 | -0.1 |  |  | 4.8705 | 13.3407 | 21.5493 | 23.8343
46023.3577 | 56.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 30 | 30 | 2961.6 | 676.7 | 48.9 | -1.4 | 76 | 83.7 | 1.1 | 2472 | 4.7 | 21 | 180 | 66 | -0.6 | -0.7 | 47.2 | 47.2 | 50 | 254 | 192 | 2000 | 26.6 | 44.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 48.6 | 2.8 | 1006.8326 | 4092.955 | 5326.9763 | 2472 | 2.1549 | 4.3765 | 0.7 | 1.7 | -0.1 |  |  | 4.8911 | 13.385 | 21.5493 | 23.3849
46023.358 | 57 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 30 | 30 | 2971.4 | 676.7 | 49 | -1.4 | 76.1 | 83.7 | 1.1 | 2293 | 4.7 | 21 | 180 | 66 | -0.6 | -0.8 | 47.3 | 47.3 | 50.2 | 253 | 196 | 2000 | 26.4 | 44.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.9 | 48.75 | 2.9 | 1006.7514 | 4093.0938 | 5556.8014 | 2293 | 2.4234 | 4.391 | 0.6 | 1.7 | -0.3 |  |  | 4.9102 | 13.4314 | 24.2338 | 23.5062
46023.3584 | 57.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 30 | 30 | 2961.6 | 676.7 | 48.9 | -1.4 | 76.2 | 83.8 | 1.1 | 2293 | 4.7 | 21 | 180 | 66 | -0.6 | -0.8 | 47.3 | 47.3 | 50.2 | 252 | 196 | 2000 | 26.7 | 44.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 48.75 | 2.9 | 1006.7514 | 4093.0938 | 5516.9677 | 2293 | 2.406 | 4.3765 | 0.6 | 1.6 | -0.3 |  |  | 4.9294 | 13.4773 | 24.06 | 23.1826
46023.3587 | 58 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 30 | 30 | 2961.6 | 676.7 | 48.9 | -1.4 | 76.4 | 84 | 1.1 | 2362 | 4.7 | 21 | 180 | 66 | -0.7 | -0.8 | 47.3 | 47.3 | 50.2 | 251 | 196 | 2000 | 27 | 44 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 48.75 | 2.9 | 1006.7514 | 4093.0938 | 5516.9677 | 2362 | 2.3357 | 4.3765 | 0.6 | 1.6 | -0.3 |  |  | 4.949 | 13.5233 | 23.3572 | 22.9499
46023.3591 | 58.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 30 | 30 | 2971.4 | 676.7 | 49 | -1.4 | 76.4 | 84.1 | 1.1 | 2362 | 4.8 | 21 | 180 | 66 | -0.7 | -0.8 | 47.3 | 47.3 | 50.2 | 250 | 196 | 2000 | 27.2 | 44 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 48.75 | 2.9 | 1006.7514 | 4093.0938 | 5516.9677 | 2362 | 2.3357 | 4.391 | 0.6 | 1.7 | -0.3 |  |  | 4.9687 | 13.5693 | 23.3572 | 23.3115
46023.3594 | 59 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 26 | 29 | 2971.4 | 676.7 | 49 | -1.4 | 76.5 | 84.1 | 1.2 | 2379 | 4.8 | 21 | 183 | 66 | -0.7 | -0.8 | 47.3 | 47.3 | 50.4 | 251 | 196 | 2000 | 27.2 | 44 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.5 | 48.85 | 3.1 | 1006.6972 | 4093.1863 | 5854.6845 | 2379 | 2.461 | 4.391 | 0.6 | 1.7 | -0.5 |  |  | 4.9885 | 13.6181 | 24.6099 | 23.9236
46023.3598 | 59.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 26 | 27 | 2961.6 | 676.7 | 48.9 | -1.4 | 76.5 | 84.1 | 1.2 | 2379 | 4.4 | 21 | 183 | 66 | -0.7 | -0.8 | 47.3 | 47.3 | 50.2 | 250 | 188 | 2000 | 27.8 | 43.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.5 | 48.75 | 2.9 | 1006.7514 | 4093.0938 | 5477.134 | 2379 | 2.3023 | 4.3765 | 0.6 | 1.6 | -0.4 |  |  | 5.0084 | 13.6637 | 23.0228 | 23.6814
46023.3601 | 60 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 28 | 27 | 2942 | 686.5 | 48.6 | -1 | 76.4 | 84.1 | 1.1 | 2344 | 4.2 | 20 | 183 | 66 | -0.5 | -0.7 | 47.2 | 47.3 | 50 | 249 | 188 | 2000 | 28.3 | 44.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.5 | 48.65 | 2.7 | 1006.8055 | 4093.0012 | 5099.5595 | 2344 | 2.1756 | 4.2855 | 0.3 | 1.4 | -0.2 |  |  | 5.0279 | 13.7062 | 21.7558 | 23.2206
46023.3605 | 60.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2961.6 | 676.7 | 48.9 | -1.4 | 76.2 | 84 | 1.1 | 2170 | 4.4 | 20 | 183 | 66 | -0.5 | -0.6 | 47.2 | 47.3 | 50 | 248 | 184 | 2000 | 28.1 | 44.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.5 | 48.65 | 2.7 | 1006.8055 | 4093.0012 | 5099.5595 | 2170 | 2.35 | 4.3765 | 0.8 | 1.7 | -0.1 |  |  | 5.046 | 13.7487 | 23.5003 | 23.2492
46023.3608 | 61 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 30 | 29 | 2961.6 | 676.7 | 48.9 | -1.4 | 76.2 | 83.8 | 1.1 | 2170 | 4.5 | 20 | 183 | 66 | -0.6 | -0.7 | 47.2 | 47.3 | 50 | 247 | 188 | 2000 | 27.3 | 45 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 48.65 | 2.7 | 1006.8055 | 4093.0012 | 5136.6473 | 2170 | 2.3671 | 4.3765 | 0.7 | 1.7 | -0.1 |  |  | 5.0641 | 13.7915 | 23.6712 | 23.312
46023.3612 | 61.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 30 | 30 | 2971.4 | 676.7 | 49 | -1.4 | 76.2 | 83.8 | 1.1 | 2266 | 4.7 | 20 | 182 | 66 | -0.7 | -0.7 | 47.3 | 47.3 | 50.2 | 246 | 196 | 2000 | 26.8 | 45 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 48.75 | 2.9 | 1006.7514 | 4093.0938 | 5516.9677 | 2266 | 2.4347 | 4.391 | 0.7 | 1.7 | -0.3 |  |  | 5.083 | 13.8375 | 24.3467 | 23.2594
46023.3615 | 62 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 28 | 29 | 2971.4 | 676.7 | 49 | -1.4 | 76.5 | 84 | 1 | 2266 | 4.8 | 21 | 182 | 66 | -0.7 | -0.8 | 47.3 | 47.3 | 50.2 | 245 | 196 | 2000 | 27.3 | 44 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 48.75 | 2.9 | 1006.7514 | 4093.0938 | 5516.9677 | 2266 | 2.4347 | 4.391 | 0.6 | 1.7 | -0.3 |  |  | 5.1018 | 13.8835 | 24.3467 | 23.5241
46023.3619 | 62.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2961.6 | 676.7 | 48.9 | -1.4 | 76.7 | 84.1 | 1 | 2348 | 4.5 | 21 | 182 | 66 | -0.7 | -0.8 | 47.3 | 47.3 | 50.2 | 244 | 192 | 2000 | 28 | 43.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.3 | 48.75 | 2.9 | 1006.7514 | 4093.0938 | 5437.3003 | 2348 | 2.3157 | 4.3765 | 0.6 | 1.6 | -0.3 |  |  | 5.1214 | 13.9288 | 23.1572 | 23.8044
46023.3622 | 63 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2961.6 | 676.7 | 48.9 | -1.4 | 76.5 | 84.1 | 1 | 2348 | 4.5 | 21 | 182 | 66 | -0.6 | -0.7 | 47.3 | 47.3 | 50.2 | 243 | 188 | 2000 | 28 | 44.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 28.1 | 48.75 | 2.9 | 1006.7514 | 4093.0938 | 5596.6351 | 2348 | 2.3836 | 4.3765 | 0.7 | 1.6 | -0.3 |  |  | 5.141 | 13.9754 | 23.8358 | 23.8715
46023.3625 | 63.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2971.4 | 686.5 | 49 | -1 | 76.5 | 84.1 | 1.1 | 2251 | 4.5 | 21 | 183 | 66 | -0.5 | -0.6 | 47.3 | 47.3 | 50.2 | 242 | 188 | 2000 | 28 | 44.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 28.1 | 48.75 | 2.9 | 1006.7514 | 4093.0938 | 5596.6351 | 2251 | 2.4863 | 4.3283 | 0.4 | 1.7 | -0.3 |  |  | 5.1597 | 14.022 | 24.8629 | 24.1098
46023.3629 | 64 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2961.6 | 686.5 | 48.9 | -1 | 76.5 | 84.1 | 1.1 | 2251 | 4.5 | 21 | 183 | 66 | -0.5 | -0.6 | 47.3 | 47.3 | 50.2 | 241 | 188 | 2000 | 28.2 | 44.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 48.75 | 2.9 | 1006.7514 | 4093.0938 | 5516.9677 | 2251 | 2.4509 | 4.3141 | 0.4 | 1.6 | -0.3 |  |  | 5.1785 | 14.068 | 24.509 | 24.1423
46023.3632 | 64.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2961.6 | 686.5 | 48.9 | -1 | 76.5 | 84 | 1.1 | 2251 | 4.5 | 21 | 183 | 66 | -0.5 | -0.6 | 47.3 | 47.3 | 50.2 | 240 | 188 | 2000 | 28.1 | 44.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 48.75 | 2.9 | 1006.7514 | 4093.0938 | 5516.9677 | 2251 | 2.4509 | 4.3141 | 0.4 | 1.6 | -0.3 |  |  | 5.1972 | 14.114 | 24.509 | 24.1747
46023.3636 | 65 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2961.6 | 676.7 | 48.9 | -1.4 | 76.5 | 84 | 1.1 | 2251 | 4.5 | 21 | 183 | 66 | -0.6 | -0.7 | 47.3 | 47.3 | 50.2 | 239 | 188 | 2000 | 28.2 | 44.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 48.75 | 2.9 | 1006.7514 | 4093.0938 | 5516.9677 | 2251 | 2.4509 | 4.3765 | 0.7 | 1.6 | -0.3 |  |  | 5.216 | 14.16 | 24.509 | 24.4451
46023.3639 | 65.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2971.4 | 686.5 | 49 | -1 | 76.5 | 84 | 1.2 | 2251 | 4.5 | 21 | 183 | 66 | -0.5 | -0.6 | 47.3 | 47.3 | 50.2 | 238 | 188 | 2000 | 28.5 | 44.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 48.75 | 2.9 | 1006.7514 | 4093.0938 | 5516.9677 | 2251 | 2.4509 | 4.3283 | 0.4 | 1.7 | -0.3 |  |  | 5.2348 | 14.2059 | 24.509 | 24.5797
46023.3643 | 66 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2971.4 | 676.7 | 49 | -1.4 | 76.5 | 84 | 1.2 | 2255 | 4.5 | 21 | 183 | 66 | -0.5 | -0.6 | 47.3 | 47.3 | 50.2 | 237 | 188 | 2000 | 28.6 | 44.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.5 | 48.75 | 2.9 | 1006.7514 | 4093.0938 | 5477.134 | 2255 | 2.4289 | 4.391 | 0.8 | 1.7 | -0.4 |  |  | 5.2536 | 14.2516 | 24.2888 | 24.4649
46023.3646 | 66.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2971.4 | 676.7 | 49 | -1.4 | 76.5 | 84 | 1.2 | 2255 | 4.5 | 21 | 183 | 66 | -0.6 | -0.6 | 47.3 | 47.5 | 50.2 | 236 | 188 | 2000 | 28.6 | 44.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.7 | 48.85 | 2.7 | 1006.6972 | 4093.1863 | 5136.3268 | 2255 | 2.2778 | 4.391 | 0.8 | 1.7 | -0.4 |  |  | 5.2723 | 14.2944 | 22.7775 | 24.1186
46023.365 | 67 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2961.6 | 676.7 | 48.9 | -1.4 | 76.7 | 84 | 1.1 | 2263 | 4.5 | 21 | 183 | 66 | -0.6 | -0.7 | 47.3 | 47.5 | 50.2 | 235 | 188 | 2000 | 28.7 | 44 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 48.85 | 2.7 | 1006.6972 | 4093.1863 | 5136.3268 | 2263 | 2.2697 | 4.3765 | 0.7 | 1.6 | -0.3 |  |  | 5.2912 | 14.3372 | 22.697 | 23.7563
46023.3653 | 67.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2961.6 | 676.7 | 48.9 | -1.4 | 76.7 | 84 | 1.1 | 2263 | 4.5 | 21 | 183 | 66 | -0.6 | -0.7 | 47.3 | 47.3 | 50.2 | 234 | 188 | 2000 | 28.8 | 43.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 48.75 | 2.9 | 1006.7514 | 4093.0938 | 5516.9677 | 2263 | 2.4379 | 4.3765 | 0.7 | 1.6 | -0.3 |  |  | 5.3101 | 14.3832 | 24.379 | 23.7303
46023.3657 | 68 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 30 | 29 | 2971.4 | 676.7 | 49 | -1.4 | 76.7 | 84 | 1.2 | 2269 | 4.5 | 21 | 181 | 66 | -0.6 | -0.6 | 47.3 | 47.3 | 50.2 | 233 | 188 | 2000 | 28.8 | 43.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 48.75 | 2.9 | 1006.7514 | 4093.0938 | 5516.9677 | 2269 | 2.4315 | 4.391 | 0.8 | 1.7 | -0.3 |  |  | 5.329 | 14.4291 | 24.3145 | 23.6914
46023.366 | 68.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 30 | 30 | 2981.2 | 676.7 | 49.2 | -1.4 | 76.8 | 84 | 1.2 | 2269 | 4.8 | 21 | 181 | 66 | -0.6 | -0.7 | 47.3 | 47.5 | 50.4 | 234 | 192 | 2000 | 28.3 | 43.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.5 | 48.95 | 2.9 | 1006.6429 | 4093.2787 | 5476.7916 | 2269 | 2.4137 | 4.4055 | 0.7 | 1.9 | -0.6 |  |  | 5.3479 | 14.4748 | 24.1375 | 23.6611
46023.3664 | 69 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 26 | 29 | 2981.2 | 676.7 | 49.2 | -1.4 | 77 | 84.1 | 1.1 | 2315 | 4.8 | 21 | 181 | 66 | -0.7 | -0.8 | 47.3 | 47.5 | 50.4 | 235 | 196 | 2000 | 28 | 43.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 48.95 | 2.9 | 1006.6429 | 4093.2787 | 5516.6228 | 2315 | 2.383 | 4.4055 | 0.6 | 1.9 | -0.5 |  |  | 5.3672 | 14.5208 | 23.8299 | 23.8716
46023.3667 | 69.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 26 | 27 | 2961.6 | 676.7 | 48.9 | -1.4 | 77 | 84.2 | 1.2 | 2315 | 4.5 | 21 | 181 | 67 | -0.6 | -0.7 | 47.5 | 47.5 | 50.4 | 234 | 188 | 2000 | 28.6 | 43.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 48.95 | 2.9 | 1006.6429 | 4093.2787 | 5516.6228 | 2315 | 2.383 | 4.3765 | 0.7 | 1.4 | -0.5 |  |  | 5.3865 | 14.5667 | 23.8299 | 24.0982
46023.3671 | 70 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 28 | 27 | 2971.4 | 686.5 | 49 | -1 | 77 | 84.2 | 1.2 | 2369 | 4.2 | 21 | 181 | 66 | -0.5 | -0.6 | 47.3 | 47.5 | 50.2 | 233 | 188 | 2000 | 29.3 | 43.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.5 | 48.85 | 2.7 | 1006.6972 | 4093.1863 | 5099.2414 | 2369 | 2.1525 | 4.3283 | 0.4 | 1.7 | -0.4 |  |  | 5.4062 | 14.6092 | 21.5249 | 23.5273
46023.3674 | 70.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2971.4 | 686.5 | 49 | -1 | 76.8 | 84.1 | 1.2 | 2369 | 4.5 | 21 | 182 | 66 | -0.5 | -0.6 | 47.3 | 47.5 | 50.2 | 232 | 184 | 2000 | 29 | 44.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.7 | 48.85 | 2.7 | 1006.6972 | 4093.1863 | 5136.3268 | 2369 | 2.1681 | 4.3283 | 0.4 | 1.7 | -0.4 |  |  | 5.4259 | 14.652 | 21.6814 | 23.0007
46023.3678 | 71 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 25 | 27 | 2971.4 | 686.5 | 49 | -1 | 76.8 | 84 | 1.2 | 2204 | 4.5 | 21 | 182 | 67 | -0.5 | -0.6 | 47.3 | 47.5 | 50.4 | 233 | 188 | 2000 | 29 | 44.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 28.3 | 48.95 | 2.9 | 1006.6429 | 4093.2787 | 5636.1164 | 2204 | 2.5572 | 4.3283 | 0.4 | 1.7 | -0.6 |  |  | 5.4443 | 14.699 | 25.5722 | 23.2877
46023.3681 | 71.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2961.6 | 686.5 | 48.9 | -1 | 76.7 | 84 | 1.1 | 2204 | 4.2 | 21 | 182 | 66 | -0.5 | -0.6 | 47.3 | 47.5 | 50.2 | 232 | 180 | 2000 | 29.3 | 43.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 28.3 | 48.85 | 2.7 | 1006.6972 | 4093.1863 | 5247.5829 | 2204 | 2.3809 | 4.3141 | 0.4 | 1.6 | -0.4 |  |  | 5.4627 | 14.7427 | 23.8094 | 23.2836
46023.3684 | 72 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 26 | 31 | 26 | 2942 | 686.5 | 48.6 | -1 | 76.7 | 83.8 | 1.1 | 2234 | 4 | 21 | 182 | 66 | -0.4 | -0.5 | 47.2 | 47.3 | 50 | 230 | 180 | 2000 | 30 | 44.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 48.65 | 2.7 | 1006.8055 | 4093.0012 | 5136.6473 | 2234 | 2.2993 | 4.2855 | 0.5 | 1.4 | -0.1 |  |  | 5.4813 | 14.7855 | 22.993 | 23.1162
46023.3688 | 72.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 31 | 28 | 2951.8 | 686.5 | 48.8 | -1 | 76.5 | 83.6 | 1.1 | 2234 | 4.3 | 21 | 180 | 66 | -0.4 | -0.5 | 47.2 | 47.3 | 50 | 229 | 180 | 2000 | 29.5 | 44.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.7 | 48.65 | 2.7 | 1006.8055 | 4093.0012 | 5136.6473 | 2234 | 2.2993 | 4.2998 | 0.5 | 1.6 | -0.1 |  |  | 5.4999 | 14.8283 | 22.993 | 23.4098
46023.3691 | 73 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 31 | 30 | 2961.6 | 686.5 | 48.9 | -1 | 76.4 | 83.5 | 1.1 | 2103 | 4.6 | 21 | 180 | 66 | -0.4 | -0.5 | 47.2 | 47.3 | 50.2 | 228 | 186 | 2000 | 28.7 | 44 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.5 | 48.75 | 2.9 | 1006.7514 | 4093.0938 | 5477.134 | 2103 | 2.6044 | 4.3141 | 0.5 | 1.7 | -0.3 |  |  | 5.5174 | 14.874 | 26.0444 | 24.2824
46023.3695 | 73.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 31 | 31 | 31 | 2981.2 | 676.7 | 49.2 | -1.4 | 76.4 | 83.5 | 1.2 | 2103 | 4.9 | 21 | 180 | 66 | -0.5 | -0.6 | 47.3 | 47.3 | 50.4 | 229 | 186 | 2000 | 28 | 43.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.9 | 27.5 | 48.85 | 3.1 | 1006.6972 | 4093.1863 | 5854.6845 | 2103 | 2.784 | 4.4055 | 0.8 | 1.9 | -0.5 |  |  | 5.535 | 14.9228 | 27.8397 | 24.7359
46023.3698 | 74 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 25 | 30 | 2971.4 | 676.7 | 49 | -1.4 | 76.7 | 83.7 | 1.2 | 2349 | 4.9 | 21 | 180 | 66 | -0.6 | -0.8 | 47.5 | 47.3 | 50.4 | 230 | 193 | 2000 | 27.3 | 43.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.5 | 48.85 | 3.1 | 1006.6972 | 4093.1863 | 5854.6845 | 2349 | 2.4924 | 4.391 | 0.6 | 1.5 | -0.6 |  |  | 5.5545 | 14.9716 | 24.9242 | 24.9589
46023.3702 | 74.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 25 | 28 | 2961.6 | 686.5 | 48.9 | -1 | 77 | 84 | 1.2 | 2349 | 4.6 | 21 | 180 | 66 | -0.5 | -0.7 | 47.5 | 47.2 | 50.2 | 229 | 196 | 2000 | 27.8 | 43.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 28.1 | 48.7 | 3 | 1006.7784 | 4093.0475 | 5789.7128 | 2349 | 2.4648 | 4.3141 | 0.3 | 1.4 | -0.4 |  |  | 5.5741 | 15.0198 | 24.6476 | 25.2898
46023.3705 | 75 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2942 | 686.5 | 48.6 | -1 | 76.8 | 84.1 | 1.2 | 2420 | 4.3 | 21 | 182 | 66 | -0.4 | -0.5 | 47.2 | 47.1 | 50 | 227 | 184 | 2000 | 29.2 | 43 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 28.1 | 48.55 | 2.9 | 1006.8596 | 4092.9088 | 5596.9836 | 2420 | 2.3128 | 4.2855 | 0.5 | 1.4 | -0.2 |  |  | 5.5943 | 15.0664 | 23.128 | 25.3168
46023.3709 | 75.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2942 | 686.5 | 48.6 | -1 | 76.4 | 83.8 | 1.3 | 2420 | 4.3 | 21 | 182 | 66 | -0.4 | -0.5 | 47.2 | 47.2 | 50 | 226 | 184 | 2000 | 29.5 | 43.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.9 | 48.6 | 2.8 | 1006.8326 | 4092.955 | 5365.4383 | 2420 | 2.2171 | 4.2855 | 0.5 | 1.4 | -0.2 |  |  | 5.6144 | 15.1112 | 22.1712 | 24.5421
46023.3712 | 76 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2942 | 686.5 | 48.6 | -1 | 76.2 | 83.6 | 1.3 | 2220 | 4.3 | 21 | 182 | 66 | -0.5 | -0.5 | 47.1 | 47.2 | 50 | 225 | 184 | 2000 | 29.6 | 43.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.7 | 28.1 | 48.6 | 2.8 | 1006.8326 | 4092.955 | 5403.9002 | 2220 | 2.4342 | 4.2855 | 0.5 | 1.5 | -0.3 |  |  | 5.6329 | 15.1562 | 24.3419 | 23.8426
46023.3716 | 76.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2932.2 | 686.5 | 48.5 | -1 | 76.1 | 83.4 | 1.2 | 2220 | 4.3 | 21 | 182 | 66 | -0.5 | -0.5 | 47.1 | 47.1 | 49.8 | 224 | 184 | 2000 | 29.6 | 43.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.7 | 28.5 | 48.45 | 2.7 | 1006.9136 | 4092.8162 | 5285.3266 | 2220 | 2.3808 | 4.2712 | 0.5 | 1.4 | -0.1 |  |  | 5.6514 | 15.2002 | 23.8078 | 23.6193
46023.3719 | 77 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 29 | 28 | 2922.4 | 686.5 | 48.3 | -1 | 76 | 83.2 | 1.2 | 2194 | 4.3 | 20 | 179 | 66 | -0.4 | -0.5 | 47.1 | 47 | 49.8 | 221 | 184 | 2000 | 29.6 | 43.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.7 | 28.5 | 48.4 | 2.8 | 1006.9406 | 4092.77 | 5481.1644 | 2194 | 2.4983 | 4.257 | 0.5 | 1.2 | -0.1 |  |  | 5.6697 | 15.2459 | 24.9825 | 23.6863
46023.3723 | 77.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 29 | 29 | 2942 | 676.7 | 48.6 | -1.4 | 75.8 | 83.1 | 1.3 | 2194 | 4.6 | 21 | 179 | 66 | -0.5 | -0.6 | 47 | 47 | 49.6 | 220 | 190 | 2000 | 28.8 | 42.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.8 | 27.7 | 48.3 | 2.6 | 1006.9945 | 4092.6775 | 4946.9384 | 2194 | 2.2548 | 4.3476 | 0.8 | 1.6 | 0.2 |  |  | 5.688 | 15.2871 | 22.5476 | 23.5702
46023.3726 | 78 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 31 | 29 | 2922.4 | 686.5 | 48.3 | -1 | 76 | 83 | 1.3 | 2228 | 4.6 | 21 | 179 | 66 | -0.5 | -0.6 | 47 | 46.8 | 49.6 | 219 | 190 | 2000 | 28.5 | 42.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.7 | 27.5 | 48.2 | 2.8 | 1007.0484 | 4092.585 | 5289.1701 | 2228 | 2.374 | 4.257 | 0.4 | 1.3 | 0.1 |  |  | 5.7066 | 15.3312 | 23.7395 | 23.8839
46023.373 | 78.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 31 | 31 | 31 | 2942 | 676.7 | 48.6 | -1.4 | 76 | 83.1 | 1.3 | 2228 | 4.8 | 21 | 179 | 66 | -0.5 | -0.6 | 47 | 46.8 | 49.8 | 218 | 196 | 2000 | 28 | 42.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.7 | 27.7 | 48.3 | 3 | 1006.9945 | 4092.6775 | 5708.0058 | 2228 | 2.5619 | 4.3476 | 0.8 | 1.6 | -0.1 |  |  | 5.7251 | 15.3788 | 25.6194 | 24.1394
46023.3733 | 79 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 29 | 30 | 2942 | 676.7 | 48.6 | -1.4 | 76.1 | 83.2 | 1.3 | 2355 | 4.8 | 21 | 179 | 66 | -0.6 | -0.8 | 47 | 46.8 | 49.8 | 217 | 200 | 2000 | 27.3 | 42.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.7 | 27.7 | 48.3 | 3 | 1006.9945 | 4092.6775 | 5708.0058 | 2355 | 2.4238 | 4.3476 | 0.6 | 1.6 | -0.1 |  |  | 5.7448 | 15.4263 | 24.2378 | 24.2254
46023.3737 | 79.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 29 | 29 | 2922.4 | 676.7 | 48.3 | -1.4 | 76.2 | 83.3 | 1.3 | 2355 | 4.6 | 21 | 183 | 66 | -0.6 | -0.7 | 47 | 46.8 | 49.8 | 215 | 200 | 2000 | 28.1 | 42 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.7 | 27.7 | 48.3 | 3 | 1006.9945 | 4092.6775 | 5708.0058 | 2355 | 2.4238 | 4.3186 | 0.7 | 1.3 | -0.1 |  |  | 5.7644 | 15.4739 | 24.2378 | 24.0764
46023.374 | 80 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 31 | 29 | 2912.6 | 686.5 | 48.2 | -1 | 76 | 83.3 | 1.3 | 2404 | 4.5 | 20 | 183 | 66 | -0.5 | -0.7 | 47 | 46.6 | 49.4 | 214 | 192 | 2000 | 28.5 | 42.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.7 | 28.1 | 48 | 2.8 | 1007.156 | 4092.4 | 5404.9032 | 2404 | 2.2483 | 4.2427 | 0.3 | 1.2 | 0.3 |  |  | 5.7844 | 15.5189 | 22.483 | 24.0635
46023.3744 | 80.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 31 | 31 | 31 | 2932.2 | 686.5 | 48.5 | -1 | 76 | 83.2 | 1.3 | 2404 | 4.8 | 20 | 183 | 66 | -0.4 | -0.5 | 46.8 | 46.6 | 49.6 | 215 | 196 | 2000 | 27.7 | 42.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.7 | 27.7 | 48.1 | 3 | 1007.1022 | 4092.4925 | 5708.3583 | 2404 | 2.3745 | 4.2712 | 0.5 | 1.7 | 0.1 |  |  | 5.8045 | 15.5665 | 23.7453 | 24.0647
46023.3747 | 81 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 29 | 31 | 2942 | 676.7 | 48.6 | -1.4 | 76 | 83.1 | 1.4 | 2354 | 4.8 | 21 | 183 | 66 | -0.5 | -0.6 | 47 | 46.8 | 49.8 | 214 | 200 | 2000 | 27.5 | 41.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.7 | 27.7 | 48.3 | 3 | 1006.9945 | 4092.6775 | 5708.0058 | 2354 | 2.4248 | 4.3476 | 0.8 | 1.6 | -0.1 |  |  | 5.8241 | 15.6141 | 24.2481 | 23.7904
46023.375 | 81.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 29 | 29 | 2922.4 | 686.5 | 48.3 | -1 | 76 | 83.1 | 1.4 | 2354 | 4.6 | 21 | 180 | 66 | -0.5 | -0.6 | 47.1 | 46.8 | 49.8 | 214 | 200 | 2000 | 28.3 | 40.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.6 | 27.7 | 48.3 | 3 | 1006.9945 | 4092.6775 | 5708.0058 | 2354 | 2.4248 | 4.257 | 0.4 | 1.2 | -0.2 |  |  | 5.8437 | 15.6617 | 24.2481 | 23.7925
46023.3754 | 82 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 31 | 30 | 2922.4 | 686.5 | 48.3 | -1 | 75.7 | 83.1 | 1.4 | 2415 | 4.6 | 20 | 180 | 65 | -0.4 | -0.6 | 47 | 46.8 | 49.6 | 212 | 192 | 2000 | 28.7 | 41.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.6 | 27.9 | 48.2 | 2.8 | 1007.0484 | 4092.585 | 5366.1034 | 2415 | 2.222 | 4.257 | 0.4 | 1.3 | 0 |  |  | 5.8638 | 15.7064 | 22.2199 | 23.3889
46023.3757 | 82.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 31 | 31 | 31 | 2942 | 676.7 | 48.6 | -1.4 | 75.7 | 82.8 | 1.4 | 2415 | 4.8 | 21 | 180 | 66 | -0.4 | -0.6 | 47 | 46.8 | 49.6 | 211 | 196 | 2000 | 27.8 | 42.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.6 | 27.7 | 48.2 | 2.8 | 1007.0484 | 4092.585 | 5327.6367 | 2415 | 2.2061 | 4.3476 | 0.8 | 1.6 | 0 |  |  | 5.8839 | 15.7508 | 22.0606 | 23.3044
46023.3761 | 83 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 29 | 31 | 2961.6 | 676.7 | 48.9 | -1.4 | 76 | 83 | 1.4 | 2362 | 4.8 | 21 | 180 | 66 | -0.6 | -0.7 | 47.1 | 46.8 | 50 | 212 | 200 | 2000 | 27.5 | 41 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.6 | 27.7 | 48.4 | 3.2 | 1006.9406 | 4092.77 | 6088.351 | 2362 | 2.5776 | 4.3765 | 0.7 | 1.8 | -0.4 |  |  | 5.9036 | 15.8015 | 25.7763 | 23.7106
46023.3764 | 83.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 29 | 29 | 2932.2 | 676.7 | 48.5 | -1.4 | 76 | 83.1 | 1.4 | 2362 | 4.6 | 21 | 180 | 66 | -0.6 | -0.7 | 47.1 | 46.8 | 49.8 | 211 | 200 | 2000 | 28.2 | 40 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.6 | 27.7 | 48.3 | 3 | 1006.9945 | 4092.6775 | 5708.0058 | 2362 | 2.4166 | 4.3331 | 0.7 | 1.4 | -0.2 |  |  | 5.9233 | 15.8491 | 24.166 | 23.6942
46023.3768 | 84 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 29 | 29 | 2942 | 686.5 | 48.6 | -1 | 75.8 | 83 | 1.4 | 2427 | 4.6 | 21 | 181 | 65 | -0.5 | -0.6 | 47.1 | 47 | 49.8 | 210 | 192 | 2000 | 28.8 | 40.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.6 | 27.5 | 48.4 | 2.8 | 1006.9406 | 4092.77 | 5288.8428 | 2427 | 2.1792 | 4.2855 | 0.4 | 1.5 | -0.2 |  |  | 5.9435 | 15.8931 | 21.7917 | 23.2029
46023.3771 | 84.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 29 | 29 | 2932.2 | 686.5 | 48.5 | -1 | 75.7 | 82.8 | 1.4 | 2427 | 4.6 | 21 | 181 | 65 | -0.4 | -0.6 | 47.1 | 46.8 | 49.8 | 208 | 192 | 2000 | 28.7 | 41.5 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.6 | 27.5 | 48.3 | 3 | 1006.9945 | 4092.6775 | 5666.7928 | 2427 | 2.3349 | 4.2712 | 0.4 | 1.4 | -0.2 |  |  | 5.9638 | 15.9404 | 23.349 | 23.4287
46023.3775 | 85 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 29 | 29 | 2942 | 686.5 | 48.6 | -1 | 75.7 | 82.8 | 1.4 | 2336 | 4.6 | 21 | 181 | 65 | -0.3 | -0.5 | 47 | 46.8 | 49.8 | 207 | 192 | 2000 | 28.7 | 41.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.6 | 27.5 | 48.3 | 3 | 1006.9945 | 4092.6775 | 5666.7928 | 2336 | 2.4259 | 4.2855 | 0.5 | 1.6 | -0.2 |  |  | 5.9832 | 15.9876 | 24.2585 | 23.8683
46023.3778 | 85.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 29 | 29 | 2942 | 686.5 | 48.3 | -1 | 75.8 | 82.8 | 1.4 | 2333 | 4.6 | 21 | 181 | 66 | -0.4 | -0.5 | 47 | 46.8 | 49.8 | 206 | 192 | 2000 | 28.7 | 41.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.6 | 28.1 | 48.3 | 3 | 1006.9945 | 4092.6775 | 5790.4319 | 2333 | 2.482 | 4.2855 | 0.5 | 1.3 | -0.2 |  |  | 6.0027 | 16.0358 | 24.8197 | 23.677
46023.3782 | 86 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 29 | 29 | 2942 | 686.5 | 48.6 | -1 | 75.8 | 82.8 | 1.4 | 2333 | 4.6 | 21 | 181 | 66 | -0.5 | -0.5 | 47.1 | 46.8 | 49.8 | 205 | 192 | 2000 | 28.8 | 41.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.6 | 27.7 | 48.3 | 3 | 1006.9945 | 4092.6775 | 5708.0058 | 2333 | 2.4466 | 4.2855 | 0.5 | 1.5 | -0.2 |  |  | 6.0221 | 16.0834 | 24.4664 | 23.737
46023.3785 | 86.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 29 | 29 | 2942 | 676.7 | 48.6 | -1.4 | 75.8 | 82.8 | 1.4 | 2344 | 4.6 | 21 | 180 | 65 | -0.5 | -0.6 | 47.1 | 46.8 | 49.8 | 204 | 192 | 2000 | 28.8 | 40.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.6 | 27.7 | 48.3 | 3 | 1006.9945 | 4092.6775 | 5708.0058 | 2344 | 2.4352 | 4.3476 | 0.8 | 1.5 | -0.2 |  |  | 6.0416 | 16.131 | 24.3516 | 24.249
46023.3789 | 87 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 29 | 29 | 2942 | 686.5 | 48.6 | -1 | 75.8 | 82.8 | 1.4 | 2344 | 4.6 | 21 | 180 | 65 | -0.5 | -0.6 | 47.1 | 46.8 | 49.8 | 203 | 192 | 2000 | 28.8 | 40 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.6 | 27.7 | 48.3 | 3 | 1006.9945 | 4092.6775 | 5708.0058 | 2344 | 2.4352 | 4.2855 | 0.4 | 1.5 | -0.2 |  |  | 6.0612 | 16.1785 | 24.3516 | 24.4495
46023.3792 | 87.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 29 | 29 | 2942 | 686.5 | 48.6 | -1 | 75.8 | 82.8 | 1.4 | 2349 | 4.6 | 21 | 180 | 65 | -0.5 | -0.6 | 47.1 | 47 | 50 | 204 | 192 | 2000 | 29 | 39.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.6 | 27.5 | 48.5 | 3 | 1006.8866 | 4092.8625 | 5666.4416 | 2349 | 2.4123 | 4.2855 | 0.4 | 1.5 | -0.4 |  |  | 6.0808 | 16.2258 | 24.1228 | 24.4224
46023.3796 | 88 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 27 | 29 | 2951.8 | 686.5 | 48.6 | -1 | 75.7 | 82.6 | 1.4 | 2349 | 4.6 | 21 | 180 | 65 | -0.5 | -0.6 | 47.1 | 47 | 50 | 203 | 192 | 2000 | 29 | 39 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.6 | 27.7 | 48.5 | 3 | 1006.8866 | 4092.8625 | 5707.652 | 2349 | 2.4298 | 4.2998 | 0.4 | 1.5 | -0.4 |  |  | 6.1003 | 16.2733 | 24.2982 | 24.3181
46023.3799 | 88.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2942 | 686.5 | 48.6 | -1 | 75.7 | 82.5 | 1.4 | 2349 | 4.4 | 21 | 183 | 65 | -0.4 | -0.5 | 47.1 | 47 | 50 | 202 | 188 | 2000 | 29.5 | 38.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.6 | 27.7 | 48.5 | 3 | 1006.8866 | 4092.8625 | 5707.652 | 2349 | 2.4298 | 4.2855 | 0.5 | 1.5 | -0.4 |  |  | 6.1199 | 16.3209 | 24.2982 | 24.2845
46023.3803 | 89 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 29 | 27 | 2932.2 | 686.5 | 48.5 | -1 | 75.4 | 82.3 | 1.4 | 2314 | 4.4 | 21 | 183 | 65 | -0.3 | -0.4 | 47.1 | 47 | 49.8 | 201 | 184 | 2000 | 30.2 | 39.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.6 | 27.7 | 48.4 | 2.8 | 1006.9406 | 4092.77 | 5327.3072 | 2314 | 2.3022 | 4.2712 | 0.6 | 1.4 | -0.2 |  |  | 6.1392 | 16.3653 | 23.0221 | 24.0186
46023.3806 | 89.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 29 | 29 | 2951.8 | 686.5 | 48.8 | -1 | 75.4 | 82 | 1.4 | 2314 | 4.6 | 21 | 183 | 65 | -0.4 | -0.5 | 47.1 | 47 | 49.8 | 200 | 184 | 2000 | 29.3 | 41.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.6 | 27.3 | 48.4 | 2.8 | 1006.9406 | 4092.77 | 5250.3785 | 2314 | 2.269 | 4.2998 | 0.5 | 1.7 | -0.2 |  |  | 6.1585 | 16.409 | 22.6896 | 23.6862
46023.381 | 90 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 27 | 29 | 2951.8 | 686.5 | 48.8 | -1 | 75.7 | 82.1 | 1.4 | 2261 | 4.6 | 21 | 183 | 65 | -0.4 | -0.5 | 47.2 | 47 | 50 | 201 | 192 | 2000 | 28.8 | 40.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.6 | 27.5 | 48.5 | 3 | 1006.8866 | 4092.8625 | 5666.4416 | 2261 | 2.5062 | 4.2998 | 0.5 | 1.6 | -0.4 |  |  | 6.1773 | 16.4563 | 25.0617 | 23.874
46023.3813 | 90.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2932.2 | 686.5 | 48.6 | -1 | 75.8 | 82.5 | 1.4 | 2261 | 4.4 | 21 | 183 | 65 | -0.4 | -0.4 | 47.2 | 47 | 50 | 200 | 188 | 2000 | 29.8 | 38.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.6 | 27.5 | 48.5 | 3 | 1006.8866 | 4092.8625 | 5666.4416 | 2261 | 2.5062 | 4.2712 | 0.6 | 1.4 | -0.4 |  |  | 6.1962 | 16.5035 | 25.0617 | 24.0266
46023.3816 | 91 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 29 | 27 | 2942 | 686.5 | 48.6 | -1 | 75.5 | 82.3 | 1.5 | 2317 | 4.4 | 21 | 181 | 65 | -0.3 | -0.4 | 47.1 | 47 | 49.8 | 199 | 184 | 2000 | 30.2 | 38.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.6 | 27.5 | 48.4 | 2.8 | 1006.9406 | 4092.77 | 5288.8428 | 2317 | 2.2826 | 4.2855 | 0.6 | 1.5 | -0.2 |  |  | 6.2155 | 16.5476 | 22.8263 | 23.7323
46023.382 | 91.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 29 | 29 | 2951.8 | 686.5 | 48.8 | -1 | 75.4 | 82 | 1.5 | 2317 | 4.6 | 21 | 181 | 65 | -0.4 | -0.4 | 47.1 | 47 | 49.8 | 200 | 184 | 2000 | 29.7 | 40.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.6 | 27.5 | 48.4 | 2.8 | 1006.9406 | 4092.77 | 5288.8428 | 2317 | 2.2826 | 4.2998 | 0.6 | 1.7 | -0.2 |  |  | 6.2348 | 16.5916 | 22.8263 | 23.6931
46023.3823 | 92 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 27 | 29 | 2961.6 | 686.5 | 48.9 | -1 | 75.7 | 82.1 | 1.5 | 2268 | 4.6 | 21 | 181 | 65 | -0.4 | -0.5 | 47.2 | 47 | 50 | 201 | 191 | 2000 | 29 | 39.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.6 | 27.5 | 48.5 | 3 | 1006.8866 | 4092.8625 | 5666.4416 | 2268 | 2.4984 | 4.3141 | 0.5 | 1.7 | -0.4 |  |  | 6.2537 | 16.6388 | 24.9843 | 24.152
46023.3827 | 92.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2942 | 686.5 | 48.6 | -1 | 75.7 | 82.3 | 1.5 | 2268 | 4.4 | 21 | 181 | 65 | -0.4 | -0.5 | 47.2 | 47 | 50 | 200 | 188 | 2000 | 29.7 | 37.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.6 | 27.5 | 48.5 | 3 | 1006.8866 | 4092.8625 | 5666.4416 | 2268 | 2.4984 | 4.2855 | 0.5 | 1.4 | -0.4 |  |  | 6.2726 | 16.6861 | 24.9843 | 24.1366
46023.383 | 93 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2942 | 686.5 | 48.5 | -1 | 75.4 | 82.1 | 1.5 | 2323 | 4.4 | 21 | 181 | 65 | -0.4 | -0.4 | 47.2 | 47 | 49.8 | 198 | 184 | 2000 | 30.2 | 37.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.6 | 27.7 | 48.4 | 2.8 | 1006.9406 | 4092.77 | 5327.3072 | 2323 | 2.2933 | 4.2855 | 0.6 | 1.3 | -0.2 |  |  | 6.2919 | 16.7305 | 22.9329 | 23.7108
46023.3834 | 93.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2932.2 | 686.5 | 48.5 | -1 | 75.1 | 81.7 | 1.5 | 2323 | 4.4 | 21 | 181 | 65 | -0.3 | -0.3 | 47.1 | 47 | 49.8 | 197 | 184 | 2000 | 30.2 | 38.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.6 | 27.9 | 48.4 | 2.8 | 1006.9406 | 4092.77 | 5365.7715 | 2323 | 2.3098 | 4.2712 | 0.7 | 1.4 | -0.2 |  |  | 6.3113 | 16.7752 | 23.0985 | 23.7652
46023.3837 | 94 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 29 | 27 | 2942 | 686.5 | 48.6 | -1 | 75.1 | 81.5 | 1.5 | 2231 | 4.4 | 21 | 181 | 65 | -0.2 | -0.3 | 47.1 | 47 | 49.8 | 196 | 184 | 2000 | 30.2 | 39.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.6 | 27.5 | 48.4 | 2.8 | 1006.9406 | 4092.77 | 5288.8428 | 2231 | 2.3706 | 4.2855 | 0.7 | 1.5 | -0.2 |  |  | 6.3299 | 16.8192 | 23.7062 | 23.9412
46023.3841 | 94.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 29 | 29 | 2961.6 | 686.5 | 48.9 | -1 | 75.2 | 81.5 | 1.5 | 2231 | 4.6 | 21 | 181 | 65 | -0.3 | -0.3 | 47.1 | 47 | 50 | 195 | 188 | 2000 | 29.6 | 39.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.6 | 27.5 | 48.5 | 3 | 1006.8866 | 4092.8625 | 5666.4416 | 2231 | 2.5399 | 4.3141 | 0.7 | 1.8 | -0.4 |  |  | 6.3485 | 16.8665 | 25.3987 | 24.0241
46023.3844 | 95 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 25 | 29 | 2971.4 | 686.5 | 49 | -1 | 75.4 | 81.7 | 1.6 | 2266 | 4.7 | 21 | 181 | 65 | -0.3 | -0.4 | 47.2 | 47 | 50.2 | 196 | 190 | 2000 | 29 | 36.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.5 | 28.1 | 48.6 | 3.2 | 1006.8326 | 4092.955 | 6175.8859 | 2266 | 2.7255 | 4.3283 | 0.6 | 1.8 | -0.7 |  |  | 6.3674 | 16.9179 | 27.2546 | 24.4781
46023.3848 | 95.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 25 | 27 | 2961.6 | 686.5 | 48.9 | -1 | 75.4 | 81.8 | 1.6 | 2266 | 4.4 | 21 | 183 | 65 | -0.3 | -0.3 | 47.3 | 47 | 50.2 | 195 | 190 | 2000 | 29 | 31.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.5 | 27.7 | 48.6 | 3.2 | 1006.8326 | 4092.955 | 6087.973 | 2266 | 2.6867 | 4.3141 | 0.7 | 1.6 | -0.7 |  |  | 6.3862 | 16.9687 | 26.8666 | 25.2649
46023.3851 | 96 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2932.2 | 696.3 | 48.5 | -0.6 | 74.3 | 81 | 1.7 | 2324 | 4.1 | 21 | 183 | 64 | -0.3 | -0.2 | 47.3 | 47 | 49.8 | 194 | 184 | 2000 | 30.1 | 31.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.5 | 27.7 | 48.4 | 2.8 | 1006.9406 | 4092.77 | 5327.3072 | 2324 | 2.2923 | 4.2111 | 0.4 | 1.2 | -0.3 |  |  | 6.4056 | 17.0131 | 22.923 | 25.2298
46023.3855 | 96.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2922.4 | 696.3 | 48.3 | -0.6 | 73.5 | 79.7 | 1.7 | 2324 | 4.1 | 21 | 183 | 64 | -0.1 | -0.1 | 47.1 | 47 | 49.6 | 193 | 176 | 2000 | 31.2 | 33.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.9 | 48.3 | 2.6 | 1006.9945 | 4092.6775 | 4982.6564 | 2324 | 2.144 | 4.197 | 0.5 | 1.2 | -0.2 |  |  | 6.425 | 17.0546 | 21.44 | 24.7766
46023.3858 | 97 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 27 | 25 | 2912.6 | 696.3 | 48.2 | -0.6 | 73.4 | 79 | 1.7 | 2136 | 4.1 | 21 | 183 | 65 | -0.1 | -0.1 | 47 | 47 | 49.6 | 192 | 176 | 2000 | 31.4 | 38.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.7 | 48.3 | 2.6 | 1006.9945 | 4092.6775 | 4946.9384 | 2136 | 2.316 | 4.183 | 0.5 | 1.2 | -0.2 |  |  | 6.4428 | 17.0958 | 23.1598 | 24.3288
46023.3862 | 97.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2922.4 | 696.3 | 48.3 | -0.6 | 73.7 | 78.8 | 1.7 | 2136 | 4.4 | 20 | 181 | 65 | -0.1 | -0.1 | 47 | 46.8 | 49.4 | 191 | 176 | 2000 | 30.6 | 40.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.9 | 48.1 | 2.6 | 1007.1022 | 4092.4925 | 4982.964 | 2136 | 2.3328 | 4.197 | 0.5 | 1.3 | 0 |  |  | 6.4606 | 17.1373 | 23.3285 | 23.5436
46023.3865 | 98 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2932.2 | 696.3 | 48.5 | -0.6 | 74 | 79.2 | 1.7 | 2133 | 4.4 | 21 | 181 | 65 | -0.1 | -0.2 | 47 | 46.8 | 49.6 | 192 | 183 | 2000 | 30.2 | 39.7 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.9 | 48.2 | 2.8 | 1007.0484 | 4092.585 | 5366.1034 | 2133 | 2.5158 | 4.2111 | 0.4 | 1.5 | -0.2 |  |  | 6.4783 | 17.1821 | 25.1575 | 23.2018
46023.3869 | 98.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2942 | 696.3 | 48.6 | -0.6 | 74.1 | 79.7 | 1.7 | 2133 | 4.4 | 21 | 181 | 65 | -0.2 | -0.2 | 47 | 46.8 | 49.6 | 191 | 183 | 2000 | 30.1 | 35.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.9 | 48.2 | 2.8 | 1007.0484 | 4092.585 | 5366.1034 | 2133 | 2.5158 | 4.2252 | 0.4 | 1.6 | -0.2 |  |  | 6.4961 | 17.2268 | 25.1575 | 23.6487
46023.3872 | 99 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 25 | 27 | 2942 | 686.5 | 48.6 | -1 | 74 | 79.8 | 1.7 | 2221 | 4.4 | 21 | 181 | 64 | -0.2 | -0.2 | 47.1 | 46.8 | 49.8 | 190 | 183 | 2000 | 29.7 | 31.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.7 | 48.3 | 3 | 1006.9945 | 4092.6775 | 5708.0058 | 2221 | 2.57 | 4.2855 | 0.8 | 1.5 | -0.4 |  |  | 6.5146 | 17.2743 | 25.7002 | 24.5007
46023.3875 | 99.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2922.4 | 696.3 | 48.3 | -0.6 | 73.2 | 79.5 | 1.7 | 2221 | 4.1 | 21 | 181 | 64 | -0.2 | -0.2 | 47.1 | 46.8 | 49.8 | 189 | 183 | 2000 | 30 | 30.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.9 | 48.3 | 3 | 1006.9945 | 4092.6775 | 5749.2189 | 2221 | 2.5886 | 4.197 | 0.4 | 1.2 | -0.4 |  |  | 6.5331 | 17.3222 | 25.8857 | 25.0459
46023.3879 | 100 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 27 | 25 | 2922.4 | 696.3 | 48.3 | -0.6 | 72.2 | 78.2 | 1.7 | 2183 | 4.1 | 20 | 183 | 64 | -0.1 | -0.1 | 47.1 | 46.8 | 49.6 | 188 | 176 | 2000 | 30.7 | 31.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.9 | 48.2 | 2.8 | 1007.0484 | 4092.585 | 5366.1034 | 2183 | 2.4581 | 4.197 | 0.5 | 1.2 | -0.2 |  |  | 6.5513 | 17.367 | 24.5813 | 25.2965
46023.3882 | 100.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2942 | 696.3 | 48.6 | -0.6 | 72 | 77.5 | 1.7 | 2183 | 4.4 | 21 | 183 | 64 | -0.1 | -0.1 | 47.1 | 46.8 | 49.6 | 187 | 176 | 2000 | 30.4 | 31.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 28.1 | 48.2 | 2.8 | 1007.0484 | 4092.585 | 5404.5701 | 2183 | 2.4758 | 4.2252 | 0.5 | 1.5 | -0.2 |  |  | 6.5695 | 17.412 | 24.7575 | 25.2165
46023.3886 | 101 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2942 | 696.3 | 48.6 | -0.6 | 72 | 77.1 | 1.7 | 2136 | 4.4 | 21 | 183 | 64 | -0.2 | -0.2 | 47.1 | 46.6 | 49.6 | 188 | 176 | 2000 | 29 | 29.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 28.1 | 48.1 | 3 | 1007.1022 | 4092.4925 | 5790.7895 | 2136 | 2.711 | 4.2252 | 0.4 | 1.5 | -0.2 |  |  | 6.5873 | 17.4603 | 27.1104 | 25.607
46023.3889 | 101.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2951.8 | 686.5 | 48.8 | -1 | 71.1 | 76.5 | 1.7 | 2136 | 4.3 | 20 | 183 | 63 | -0.3 | -0.2 | 47.1 | 46.6 | 49.8 | 188 | 176 | 2000 | 28.1 | 28.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.5 | 48.2 | 3.2 | 1007.0484 | 4092.585 | 6044.7658 | 2136 | 2.8299 | 4.2998 | 0.8 | 1.7 | -0.4 |  |  | 6.6051 | 17.5106 | 28.2995 | 26.1269
46023.3893 | 102 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 25 | 27 | 2971.4 | 686.5 | 49 | -1 | 69.5 | 75 | 1.8 | 2206 | 4.4 | 21 | 183 | 63 | -0.3 | -0.2 | 47.2 | 46.6 | 50 | 188 | 176 | 2000 | 27.6 | 28.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.5 | 48.3 | 3.4 | 1006.9945 | 4092.6775 | 6422.3652 | 2206 | 2.9113 | 4.3283 | 0.8 | 1.8 | -0.6 |  |  | 6.6235 | 17.5642 | 29.1132 | 26.7724
46023.3896 | 102.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2942 | 686.5 | 48.6 | -1 | 68.2 | 73.7 | 1.8 | 2206 | 4.1 | 21 | 183 | 62 | -0.3 | -0.2 | 47.3 | 46.6 | 49.8 | 188 | 176 | 2000 | 27.5 | 28.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.7 | 48.2 | 3.2 | 1007.0484 | 4092.585 | 6088.7277 | 2206 | 2.7601 | 4.2855 | 0.8 | 1.3 | -0.4 |  |  | 6.6419 | 17.6149 | 27.6008 | 27.3763
46023.39 | 103 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2951.8 | 696.3 | 48.8 | -0.6 | 66.2 | 71.2 | 1.7 | 2169 | 4.1 | 21 | 183 | 62 | -0.2 | -0.2 | 47.2 | 46.8 | 49.8 | 188 | 176 | 2000 | 29 | 29.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.9 | 48.3 | 3 | 1006.9945 | 4092.6775 | 5749.2189 | 2169 | 2.6506 | 4.2393 | 0.4 | 1.6 | -0.4 |  |  | 6.66 | 17.6628 | 26.5063 | 27.726
46023.3903 | 103.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2932.2 | 696.3 | 48.5 | -0.6 | 65.2 | 69.4 | 1.7 | 2169 | 4.1 | 20 | 183 | 62 | -0.2 | -0.2 | 47.2 | 46.6 | 49.6 | 188 | 176 | 2000 | 29.2 | 29.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.7 | 48.1 | 3 | 1007.1022 | 4092.4925 | 5708.3583 | 2169 | 2.6318 | 4.2111 | 0.4 | 1.3 | -0.2 |  |  | 6.678 | 17.7104 | 26.3179 | 27.5675
46023.3907 | 104 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 27 | 25 | 2932.2 | 696.3 | 48.5 | -0.6 | 65 | 68.5 | 1.7 | 2100 | 4.1 | 21 | 183 | 62 | -0.2 | -0.2 | 47.1 | 46.6 | 49.6 | 187 | 176 | 2000 | 29.5 | 30.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.7 | 48.1 | 3 | 1007.1022 | 4092.4925 | 5708.3583 | 2100 | 2.7183 | 4.2111 | 0.4 | 1.4 | -0.2 |  |  | 6.6955 | 17.7579 | 27.1827 | 27.3442
46023.391 | 104.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2942 | 686.5 | 48.6 | -1 | 65 | 68.2 | 1.7 | 2100 | 4.3 | 20 | 183 | 62 | -0.3 | -0.3 | 47.1 | 46.5 | 49.4 | 187 | 176 | 2000 | 28.7 | 29.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 28.1 | 47.95 | 2.9 | 1007.1829 | 4092.3538 | 5598.0215 | 2100 | 2.6657 | 4.2855 | 0.7 | 1.5 | 0 |  |  | 6.713 | 17.8046 | 26.6572 | 26.853
46023.3914 | 105 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2942 | 686.5 | 48.6 | -1 | 65.4 | 68.7 | 1.7 | 2129 | 4.3 | 21 | 183 | 62 | -0.3 | -0.3 | 47.1 | 46.5 | 49.6 | 186 | 176 | 2000 | 27.8 | 28.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.9 | 48.05 | 3.1 | 1007.1291 | 4092.4462 | 5941.3178 | 2129 | 2.7907 | 4.2855 | 0.7 | 1.5 | -0.2 |  |  | 6.7308 | 17.8541 | 27.9066 | 26.9142
46023.3917 | 105.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2951.8 | 686.5 | 48.8 | -1 | 65.4 | 69.1 | 1.7 | 2129 | 4.3 | 21 | 183 | 61 | -0.3 | -0.3 | 47.1 | 46.5 | 49.6 | 186 | 176 | 2000 | 27.2 | 27.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 28.1 | 48.05 | 3.1 | 1007.1291 | 4092.4462 | 5983.9079 | 2129 | 2.8107 | 4.2998 | 0.7 | 1.7 | -0.2 |  |  | 6.7485 | 17.904 | 28.1067 | 27.2342
46023.3921 | 106 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2961.6 | 686.5 | 48.9 | -1 | 64.7 | 68.7 | 1.7 | 2198 | 4.3 | 20 | 183 | 61 | -0.4 | -0.4 | 47.2 | 46.5 | 49.8 | 187 | 176 | 2000 | 27 | 27.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 28.1 | 48.15 | 3.3 | 1007.0753 | 4092.5388 | 6369.7702 | 2198 | 2.898 | 4.3141 | 0.6 | 1.7 | -0.4 |  |  | 6.7668 | 17.957 | 28.9798 | 27.7666
46023.3924 | 106.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2961.6 | 686.5 | 48.9 | -1 | 63.8 | 67.7 | 1.7 | 2198 | 4.3 | 20 | 182 | 61 | -0.4 | -0.4 | 47.2 | 46.5 | 49.8 | 187 | 176 | 2000 | 26.7 | 27.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.7 | 48.15 | 3.3 | 1007.0753 | 4092.5388 | 6279.0973 | 2198 | 2.8567 | 4.3141 | 0.6 | 1.7 | -0.4 |  |  | 6.7852 | 18.0094 | 28.5673 | 28.0435
46023.3928 | 107 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 25 | 27 | 2951.8 | 686.5 | 48.8 | -1 | 62.8 | 66.7 | 1.7 | 2205 | 4.3 | 20 | 182 | 60 | -0.5 | -0.4 | 47.2 | 46.5 | 49.8 | 187 | 167 | 2000 | 26.7 | 27.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.7 | 48.15 | 3.3 | 1007.0753 | 4092.5388 | 6279.0973 | 2205 | 2.8477 | 4.2998 | 0.6 | 1.6 | -0.4 |  |  | 6.8035 | 18.0617 | 28.4766 | 28.4074
46023.3931 | 107.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2932.2 | 686.5 | 48.5 | -1 | 62.4 | 66 | 1.7 | 2205 | 4 | 20 | 182 | 60 | -0.4 | -0.4 | 47.2 | 46.5 | 49.6 | 187 | 167 | 2000 | 26.5 | 27.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.7 | 48.05 | 3.1 | 1007.1291 | 4092.4462 | 5898.7277 | 2205 | 2.6752 | 4.2712 | 0.6 | 1.3 | -0.2 |  |  | 6.8219 | 18.1109 | 26.7516 | 28.1764
46023.3935 | 108 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 27 | 25 | 2942 | 696.3 | 48.6 | -0.6 | 61.7 | 65.1 | 1.7 | 2162 | 4.1 | 21 | 182 | 60 | -0.2 | -0.3 | 47.2 | 46.5 | 49.6 | 186 | 158 | 2000 | 28 | 28.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.7 | 48.05 | 3.1 | 1007.1291 | 4092.4462 | 5898.7277 | 2162 | 2.7284 | 4.2252 | 0.3 | 1.4 | -0.2 |  |  | 6.8399 | 18.16 | 27.2837 | 28.0118
46023.3938 | 108.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2942 | 686.5 | 48.6 | -1 | 61.8 | 64.8 | 1.7 | 2162 | 4.3 | 20 | 182 | 60 | -0.3 | -0.3 | 47.1 | 46.5 | 49.6 | 186 | 150 | 2000 | 27.6 | 28.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.5 | 48.05 | 3.1 | 1007.1291 | 4092.4462 | 5856.1376 | 2162 | 2.7087 | 4.2855 | 0.7 | 1.5 | -0.2 |  |  | 6.8579 | 18.2088 | 27.0867 | 27.6332
46023.3941 | 109 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2942 | 686.5 | 48.6 | -1 | 62.7 | 65.8 | 1.7 | 2116 | 4.2 | 20 | 183 | 60 | -0.5 | -0.4 | 47.1 | 46.3 | 49.6 | 185 | 142 | 2000 | 26.1 | 26.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.7 | 47.95 | 3.3 | 1007.1829 | 4092.3538 | 6279.4839 | 2116 | 2.9676 | 4.2855 | 0.6 | 1.5 | -0.2 |  |  | 6.8756 | 18.2611 | 29.6762 | 27.855
46023.3945 | 109.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2961.6 | 686.5 | 48.9 | -1 | 63 | 66.5 | 1.7 | 2116 | 4.2 | 20 | 183 | 60 | -0.4 | -0.4 | 47.1 | 46.5 | 49.6 | 185 | 142 | 2000 | 25.4 | 25.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.7 | 48.05 | 3.1 | 1007.1291 | 4092.4462 | 5898.7277 | 2116 | 2.7877 | 4.3141 | 0.6 | 1.8 | -0.2 |  |  | 6.8932 | 18.3103 | 27.8768 | 27.735
46023.3948 | 110 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 25 | 27 | 2961.6 | 686.5 | 48.9 | -1 | 62.8 | 67.1 | 1.7 | 2166 | 4.2 | 20 | 183 | 59 | -0.5 | -0.4 | 47.2 | 46.5 | 49.8 | 185 | 134 | 2000 | 25 | 25.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.7 | 48.15 | 3.3 | 1007.0753 | 4092.5388 | 6279.0973 | 2166 | 2.8989 | 4.3141 | 0.6 | 1.7 | -0.4 |  |  | 6.9113 | 18.3626 | 28.9894 | 28.1825
46023.3952 | 110.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2951.8 | 696.3 | 48.8 | -0.6 | 62.5 | 67.1 | 1.7 | 2166 | 4 | 20 | 183 | 59 | -0.4 | -0.4 | 47.2 | 46.5 | 49.8 | 185 | 127 | 2000 | 25 | 25.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.9 | 48.15 | 3.3 | 1007.0753 | 4092.5388 | 6324.4338 | 2166 | 2.9199 | 4.2393 | 0.2 | 1.6 | -0.4 |  |  | 6.9293 | 18.4153 | 29.1987 | 28.5655
46023.3955 | 111 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 27 | 25 | 2932.2 | 696.3 | 48.5 | -0.6 | 62 | 66.5 | 1.7 | 2123 | 4 | 20 | 178 | 58 | -0.2 | -0.3 | 47.2 | 46.5 | 49.6 | 184 | 120 | 2000 | 26.2 | 26.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.9 | 48.05 | 3.1 | 1007.1291 | 4092.4462 | 5941.3178 | 2123 | 2.7985 | 4.2111 | 0.3 | 1.3 | -0.2 |  |  | 6.947 | 18.4648 | 27.9855 | 28.7453
46023.3959 | 111.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2961.6 | 686.5 | 48.9 | -1 | 62 | 66.2 | 1.8 | 2123 | 4.2 | 20 | 178 | 58 | -0.3 | -0.3 | 47.1 | 46.6 | 49.6 | 184 | 120 | 2000 | 25.6 | 26.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.9 | 48.1 | 3 | 1007.1022 | 4092.4925 | 5749.5739 | 2123 | 2.7082 | 4.3141 | 0.7 | 1.8 | -0.2 |  |  | 6.9647 | 18.5128 | 27.0823 | 28.2265
46023.3962 | 112 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 25 | 27 | 2971.4 | 686.5 | 49 | -1 | 62.4 | 66.7 | 1.8 | 2082 | 4.2 | 20 | 178 | 58 | -0.4 | -0.4 | 47.2 | 46.6 | 49.8 | 184 | 114 | 2000 | 24.4 | 24.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.5 | 48.2 | 3.2 | 1007.0484 | 4092.585 | 6044.7658 | 2082 | 2.9033 | 4.3283 | 0.6 | 1.8 | -0.4 |  |  | 6.982 | 18.5631 | 29.0335 | 28.4579
46023.3966 | 112.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2951.8 | 696.3 | 48.8 | -0.6 | 62.7 | 67.5 | 1.8 | 2082 | 3.9 | 20 | 178 | 58 | -0.4 | -0.4 | 47.2 | 46.5 | 49.6 | 184 | 108 | 2000 | 23.8 | 24.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.5 | 48.05 | 3.1 | 1007.1291 | 4092.4462 | 5856.1376 | 2082 | 2.8127 | 4.2393 | 0.2 | 1.6 | -0.2 |  |  | 6.9994 | 18.6119 | 28.1275 | 28.2855
46023.3969 | 113 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 27 | 25 | 2942 | 696.3 | 48.6 | -0.6 | 62.2 | 67.5 | 1.8 | 2089 | 4 | 20 | 178 | 57 | -0.3 | -0.2 | 47.2 | 46.5 | 49.6 | 183 | 102 | 2000 | 25.3 | 25.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.5 | 48.05 | 3.1 | 1007.1291 | 4092.4462 | 5856.1376 | 2089 | 2.8033 | 4.2252 | 0.4 | 1.4 | -0.2 |  |  | 7.0168 | 18.6607 | 28.0332 | 28.0524
46023.3973 | 113.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2961.6 | 686.5 | 48.9 | -1 | 62.1 | 67.4 | 1.8 | 2089 | 4.1 | 19 | 181 | 57 | -0.3 | -0.3 | 47.2 | 46.6 | 49.6 | 183 | 102 | 2000 | 24.6 | 25 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.5 | 48.1 | 3 | 1007.1022 | 4092.4925 | 5667.1427 | 2089 | 2.7128 | 4.3141 | 0.7 | 1.7 | -0.2 |  |  | 7.0342 | 18.708 | 27.1285 | 27.881
46023.3976 | 114 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 25 | 27 | 2981.2 | 686.5 | 49.2 | -1 | 62.7 | 68 | 1.9 | 2056 | 4.1 | 19 | 181 | 57 | -0.4 | -0.4 | 47.2 | 46.6 | 49.8 | 183 | 96 | 2000 | 22.8 | 23.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.4 | 27.7 | 48.2 | 3.2 | 1007.0484 | 4092.585 | 6088.7277 | 2056 | 2.9614 | 4.3426 | 0.6 | 2 | -0.4 |  |  | 7.0513 | 18.7587 | 29.6144 | 28.3874
46023.398 | 114.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2951.8 | 686.5 | 48.8 | -1 | 63 | 68.4 | 1.9 | 2056 | 3.8 | 19 | 181 | 57 | -0.3 | -0.4 | 47.2 | 46.6 | 49.8 | 183 | 91 | 2000 | 22.6 | 23 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.3 | 27.7 | 48.2 | 3.2 | 1007.0484 | 4092.585 | 6088.7277 | 2056 | 2.9614 | 4.2998 | 0.6 | 1.6 | -0.5 |  |  | 7.0685 | 18.8094 | 29.6144 | 28.5036
46023.3983 | 115 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 27 | 25 | 2951.8 | 696.3 | 48.8 | -0.6 | 62.4 | 68.5 | 1.9 | 2053 | 3.9 | 19 | 181 | 56 | -0.3 | -0.3 | 47.2 | 46.5 | 49.6 | 182 | 86 | 2000 | 23.4 | 24 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.3 | 27.7 | 48.05 | 3.1 | 1007.1291 | 4092.4462 | 5898.7277 | 2053 | 2.8732 | 4.2393 | 0.3 | 1.6 | -0.3 |  |  | 7.0856 | 18.8586 | 28.7322 | 28.6246
46023.3987 | 115.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2971.4 | 686.5 | 49 | -1 | 62.1 | 68.1 | 1.9 | 2053 | 4.1 | 19 | 181 | 56 | -0.3 | -0.3 | 47.1 | 46.6 | 49.8 | 182 | 86 | 2000 | 23.3 | 23.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.3 | 27.7 | 48.2 | 3.2 | 1007.0484 | 4092.585 | 6088.7277 | 2053 | 2.9658 | 4.3283 | 0.7 | 1.9 | -0.5 |  |  | 7.1027 | 18.9093 | 29.6577 | 28.9495
46023.399 | 116 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 25 | 27 | 2971.4 | 686.5 | 49 | -1 | 62.5 | 68.4 | 1.9 | 2016 | 4 | 19 | 183 | 56 | -0.4 | -0.4 | 47.2 | 46.6 | 49.8 | 182 | 81 | 2000 | 21.7 | 22.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.3 | 27.9 | 48.2 | 3.2 | 1007.0484 | 4092.585 | 6132.6896 | 2016 | 3.042 | 4.3283 | 0.6 | 1.8 | -0.5 |  |  | 7.1195 | 18.9604 | 30.4201 | 29.6078
46023.3994 | 116.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2961.6 | 696.3 | 48.9 | -0.6 | 62.8 | 68.8 | 2 | 2016 | 3.8 | 19 | 183 | 55 | -0.4 | -0.3 | 47.2 | 46.6 | 49.8 | 182 | 80 | 2000 | 21.5 | 22 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.3 | 27.9 | 48.2 | 3.2 | 1007.0484 | 4092.585 | 6132.6896 | 2016 | 3.042 | 4.2533 | 0.3 | 1.7 | -0.5 |  |  | 7.1363 | 19.0115 | 30.4201 | 29.7689
46023.3997 | 117 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2961.6 | 696.3 | 48.9 | -0.6 | 62.5 | 68.8 | 2 | 2030 | 3.8 | 19 | 183 | 55 | -0.3 | -0.2 | 47.2 | 46.6 | 49.8 | 182 | 80 | 2000 | 22.2 | 22.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.2 | 27.9 | 48.2 | 3.2 | 1007.0484 | 4092.585 | 6132.6896 | 2030 | 3.021 | 4.2533 | 0.4 | 1.7 | -0.6 |  |  | 7.1532 | 19.0626 | 30.2103 | 29.8881
46023.4 | 117.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2961.6 | 696.3 | 48.9 | -0.6 | 62 | 68.2 | 2 | 2030 | 3.8 | 19 | 183 | 55 | -0.3 | -0.2 | 47.2 | 46.6 | 49.8 | 182 | 80 | 2000 | 22.8 | 23.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.2 | 27.9 | 48.2 | 3.2 | 1007.0484 | 4092.585 | 6132.6896 | 2030 | 3.021 | 4.2533 | 0.4 | 1.7 | -0.6 |  |  | 7.1701 | 19.1137 | 30.2103 | 30.1837
46023.4004 | 118 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2961.6 | 696.3 | 48.9 | -0.6 | 62 | 68.1 | 2 | 1969 | 3.9 | 19 | 181 | 55 | -0.2 | -0.2 | 47.2 | 46.8 | 49.8 | 182 | 80 | 2000 | 23.3 | 23.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.2 | 27.5 | 48.3 | 3 | 1006.9945 | 4092.6775 | 5666.7928 | 1969 | 2.878 | 4.2533 | 0.4 | 1.7 | -0.6 |  |  | 7.1865 | 19.161 | 28.7801 | 30.0082
46023.4007 | 118.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2961.6 | 696.3 | 48.9 | -0.6 | 62.4 | 68.4 | 2 | 1969 | 3.8 | 19 | 181 | 55 | -0.2 | -0.2 | 47.2 | 46.8 | 49.8 | 182 | 80 | 2000 | 23.5 | 24 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.2 | 27.7 | 48.3 | 3 | 1006.9945 | 4092.6775 | 5708.0058 | 1969 | 2.8989 | 4.2533 | 0.4 | 1.7 | -0.6 |  |  | 7.2029 | 19.2085 | 28.9894 | 29.722
46023.4011 | 119 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 24 | 25 | 2951.8 | 696.3 | 48.8 | -0.6 | 62.8 | 69 | 2 | 1974 | 3.4 | 17 | 181 | 55 | -0.2 | -0.2 | 47.2 | 46.8 | 49.8 | 182 | 0 | 0 | 22.8 | 23.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.2 | 27.7 | 48.3 | 3 | 1006.9945 | 4092.6775 | 5708.0058 | 1974 | 2.8916 | 4.2393 | 0.4 | 1.6 | -0.6 |  |  | 7.2194 | 19.2561 | 28.9159 | 29.4212
46023.4014 | 119.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 24 | 24 | 2912.6 | 696.3 | 48.2 | -0.6 | 63.2 | 69.7 | 2 | 1974 | 3.2 | 16 | 181 | 54 | -0.2 | -0.1 | 46.8 | 46.8 | 49.2 | 182 | 0 | 0 | 19.9 | 26.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.2 | 27.7 | 48 | 2.4 | 1007.156 | 4092.4 | 4566.8272 | 1974 | 2.3135 | 4.183 | 0.5 | 1.4 | 0 |  |  | 7.2358 | 19.2942 | 23.1349 | 28.0061
46023.4018 | 120 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 30 | 24 | 2912.6 | 696.3 | 48.2 | -0.6 | 64.5 | 71.8 | 2 | 1794 | 3.2 | 16 | 181 | 53 | -0.1 | -0.1 | 46 | 46.6 | 49 | 178 | 0 | 0 | 17.6 | 31 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.2 | 28.1 | 47.8 | 2.4 | 1007.2634 | 4092.215 | 4633.0586 | 1794 | 2.5825 | 4.183 | 0.5 | 2.2 | 0.2 |  |  | 7.2508 | 19.3328 | 25.8253 | 27.1291
46023.4021 | 120.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 30 | 26 | 2942 | 696.3 | 48.6 | -0.6 | 65.5 | 74.2 | 2 | 1794 | 3.4 | 16 | 183 | 55 | 0 | -0.1 | 45.3 | 46.6 | 49.2 | 179 | 0 | 0 | 14.4 | 31.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.2 | 27.5 | 47.9 | 2.6 | 1007.2097 | 4092.3075 | 4911.8258 | 1794 | 2.7379 | 4.2252 | 0.5 | 3.3 | 0 |  |  | 7.2657 | 19.3737 | 27.3792 | 26.8489
46023.4025 | 121 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 28 | 30 | 28 | 2961.6 | 696.3 | 48.9 | -0.6 | 66.8 | 76.5 | 2 | 1671 | 3.6 | 16 | 183 | 57 | -0.1 | -0.1 | 44.8 | 46.6 | 49.2 | 180 | 80 | 700 | 12.5 | 31.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.2 | 27.5 | 47.9 | 2.6 | 1007.2097 | 4092.3075 | 4911.8258 | 1671 | 2.9395 | 4.2533 | 0.5 | 4.1 | 0 |  |  | 7.2797 | 19.4146 | 29.3945 | 26.93
46023.4028 | 121.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 30 | 30 | 30 | 3020.4 | 696.3 | 49.7 | -0.6 | 67.8 | 78.1 | 2 | 1671 | 4.3 | 19 | 183 | 58 | -0.2 | -0.1 | 44.6 | 46.6 | 49.8 | 180 | 80 | 2000 | 15.4 | 34 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.2 | 27.9 | 48.2 | 3.2 | 1007.0484 | 4092.585 | 6132.6896 | 1671 | 3.6701 | 4.3378 | 0.5 | 5.1 | -0.6 |  |  | 7.2936 | 19.4657 | 36.7007 | 28.4869
46023.4032 | 122 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 30 | 25 | 30 | 3049.9 | 686.5 | 50.1 | -1 | 69.7 | 80.1 | 2.1 | 1962 | 4.4 | 19 | 183 | 59 | -0.5 | 0.4 | 44.6 | 46.6 | 50.2 | 189 | 88 | 2000 | 17.8 | 22.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.2 | 27.7 | 48.4 | 3.6 | 1006.9406 | 4092.77 | 6849.3949 | 1962 | 3.491 | 4.4427 | 1.4 | 5.5 | -1 |  |  | 7.3099 | 19.5228 | 34.9103 | 30.842
46023.4035 | 122.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 28 | 25 | 28 | 3049.9 | 686.5 | 50.1 | -1 | 69.7 | 80.5 | 2.1 | 1962 | 4.2 | 19 | 183 | 57 | -0.7 | 2 | 44.6 | 46.6 | 50.4 | 189 | 88 | 2000 | 17.8 | 19.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.2 | 28.3 | 48.5 | 3.8 | 1006.8866 | 4092.8625 | 7386.2924 | 1962 | 3.7647 | 4.4427 | 3 | 5.5 | -1.2 |  |  | 7.3263 | 19.5844 | 37.6468 | 33.2063
46023.4039 | 123 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 25 | 26 | 3020.4 | 686.5 | 49.7 | -1 | 67.1 | 78.1 | 2 | 2207 | 3.9 | 19 | 183 | 56 | -0.5 | 3 | 44.6 | 46.6 | 50.2 | 190 | 88 | 2000 | 18.8 | 19.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.2 | 28.3 | 48.4 | 3.6 | 1006.9406 | 4092.77 | 6997.7573 | 2207 | 3.1707 | 4.3997 | 4 | 5.1 | -1 |  |  | 7.3447 | 19.6427 | 31.7071 | 34.0719
46023.4042 | 123.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 3010.6 | 696.3 | 49.6 | -0.6 | 64.1 | 74.5 | 2.1 | 2207 | 3.8 | 19 | 183 | 55 | -0.3 | 3.5 | 44.6 | 46.8 | 50.2 | 190 | 87 | 2000 | 19.8 | 20.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.2 | 28.1 | 48.5 | 3.4 | 1006.8866 | 4092.8625 | 6562.0827 | 2207 | 2.9733 | 4.3237 | 4.1 | 5 | -1 |  |  | 7.3631 | 19.6974 | 29.733 | 34.1396
46023.4046 | 124 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 3000.8 | 696.3 | 49.5 | -0.6 | 62.5 | 72 | 2.1 | 2009 | 3.8 | 19 | 183 | 55 | -0.2 | 3.8 | 44.8 | 47 | 50.2 | 190 | 82 | 2000 | 20.2 | 20.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.2 | 27.7 | 48.6 | 3.2 | 1006.8326 | 4092.955 | 6087.973 | 2009 | 3.0303 | 4.3096 | 4.4 | 4.7 | -1 |  |  | 7.3798 | 19.7481 | 30.3035 | 32.8601
46023.4049 | 124.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2991 | 696.3 | 49.3 | -0.6 | 60.8 | 69 | 2.1 | 2009 | 3.7 | 19 | 183 | 54 | -0.1 | 2 | 45.1 | 47 | 50.2 | 190 | 77 | 2000 | 20.2 | 20.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.2 | 27.7 | 48.6 | 3.2 | 1006.8326 | 4092.955 | 6087.973 | 2009 | 3.0303 | 4.2956 | 2.6 | 4.2 | -1 |  |  | 7.3966 | 19.7988 | 30.3035 | 31.9388
46023.4053 | 125 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 23 | 25 | 2991 | 696.3 | 49.3 | -0.6 | 59.8 | 67 | 2.1 | 1941 | 3.6 | 18 | 180 | 54 | 0 | 0.2 | 46.3 | 47 | 50.2 | 190 | 0 | 0 | 20.2 | 20.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.2 | 27.7 | 48.6 | 3.2 | 1006.8326 | 4092.955 | 6087.973 | 1941 | 3.1365 | 4.2956 | 0.8 | 3 | -1 |  |  | 7.4127 | 19.8496 | 31.3651 | 30.6825
46023.4056 | 125.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 23 | 23 | 23 | 2922.4 | 696.3 | 48.3 | -0.6 | 60 | 67 | 2.2 | 1941 | 3.1 | 16 | 180 | 52 | 0 | 0 | 46 | 47 | 49.4 | 190 | 0 | 0 | 17.5 | 24.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.2 | 27.9 | 48.2 | 2.4 | 1007.0484 | 4092.585 | 4599.5172 | 1941 | 2.3697 | 4.197 | 0.6 | 2.3 | -0.2 |  |  | 7.4289 | 19.8879 | 23.6966 | 29.0804
46023.406 | 126 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 23 | 29 | 23 | 2922.4 | 696.3 | 48.3 | -0.6 | 61.2 | 68.4 | 2.2 | 1773 | 3.1 | 16 | 180 | 52 | 0 | 0 | 45.5 | 47 | 49.4 | 186 | 0 | 0 | 16.9 | 28.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.1 | 27.7 | 48.2 | 2.4 | 1007.0484 | 4092.585 | 4566.5458 | 1773 | 2.5756 | 4.197 | 0.6 | 2.8 | -0.3 |  |  | 7.4437 | 19.926 | 25.756 | 28.285
46023.4063 | 126.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 29 | 25 | 2961.6 | 696.3 | 48.9 | -0.6 | 63.1 | 71.1 | 2.2 | 1773 | 3.3 | 16 | 180 | 53 | 0 | 0 | 45.1 | 47 | 49.4 | 186 | 0 | 0 | 14.6 | 30.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.1 | 27.5 | 48.2 | 2.4 | 1007.0484 | 4092.585 | 4533.5743 | 1773 | 2.557 | 4.2533 | 0.6 | 3.8 | -0.3 |  |  | 7.4585 | 19.9637 | 25.5701 | 27.3383
46023.4066 | 127 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 27 | 29 | 27 | 2971.4 | 696.3 | 49 | -0.6 | 65.1 | 74.6 | 2.3 | 1630 | 3.5 | 16 | 183 | 55 | 0 | 0 | 45 | 47 | 49.4 | 186 | 0 | 0 | 12 | 30.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49.1 | 27.5 | 48.2 | 2.4 | 1007.0484 | 4092.585 | 4533.5743 | 1630 | 2.7813 | 4.2674 | 0.6 | 4 | -0.3 |  |  | 7.472 | 20.0015 | 27.8133 | 26.8402
46023.407 | 127.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 29 | 29 | 29 | 3059.7 | 696.3 | 50.3 | -0.6 | 67.1 | 77.1 | 2.3 | 1630 | 3.8 | 17 | 183 | 57 | 0 | 0 | 44.8 | 47 | 49.6 | 191 | 0 | 0 | 11 | 30.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49 | 27.7 | 48.3 | 2.6 | 1006.9945 | 4092.6775 | 4946.9384 | 1630 | 3.0349 | 4.3942 | 0.6 | 5.5 | -0.6 |  |  | 7.4856 | 20.0427 | 30.3493 | 26.6371
46023.4073 | 128 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 29 | 25 | 29 | 3216.6 | 696.3 | 51.5 | -0.6 | 69 | 79.1 | 2.3 | 1846 | 4 | 18 | 183 | 58 | -0.1 | 0.3 | 44.8 | 47 | 49.6 | 191 | 0 | 0 | 11 | 29.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49 | 27.5 | 48.3 | 2.6 | 1006.9945 | 4092.6775 | 4911.2204 | 1846 | 2.6605 | 4.6196 | 0.9 | 6.7 | -0.6 |  |  | 7.501 | 20.0837 | 26.6047 | 27.2187
46023.4077 | 128.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 27 | 25 | 28 | 3344.1 | 686.5 | 54 | -1 | 70.5 | 81.8 | 2.3 | 1846 | 4.1 | 19 | 183 | 60 | -0.3 | 1.3 | 44.8 | 47 | 49.4 | 216 | 0 | 0 | 11.4 | 29.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49 | 27.5 | 48.2 | 2.4 | 1007.0484 | 4092.585 | 4533.5743 | 1846 | 2.4559 | 4.8712 | 2.3 | 9.2 | -0.4 |  |  | 7.5164 | 20.1214 | 24.5589 | 26.9793
46023.408 | 129 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 25 | 26 | 3226.4 | 696.3 | 52.5 | -0.6 | 72.7 | 85 | 2.4 | 1846 | 3.7 | 18 | 183 | 62 | -0.1 | 2.7 | 44.8 | 47 | 49.4 | 217 | 0 | 0 | 12.4 | 28.2 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 49 | 27.7 | 48.2 | 2.4 | 1007.0484 | 4092.585 | 4566.5458 | 1846 | 2.4738 | 4.6336 | 3.3 | 7.7 | -0.4 |  |  | 7.5318 | 20.1595 | 24.7375 | 26.8127
46023.4084 | 129.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 3118.5 | 696.3 | 51.1 | -0.6 | 74.3 | 87.5 | 2.4 | 2044 | 3.5 | 18 | 179 | 62 | 0 | 3.4 | 44.8 | 47 | 49.4 | 214 | 0 | 0 | 13.8 | 27.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.9 | 27.7 | 48.2 | 2.4 | 1007.0484 | 4092.585 | 4566.5458 | 2044 | 2.2341 | 4.4787 | 4 | 6.3 | -0.5 |  |  | 7.5488 | 20.1976 | 22.3412 | 25.7183
46023.4087 | 130 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 24 | 25 | 3059.7 | 706.1 | 50.3 | -0.2 | 75.4 | 89.2 | 2.4 | 2044 | 3.4 | 17 | 179 | 63 | 0.1 | 0.7 | 44.8 | 47 | 49.4 | 212 | 0 | 0 | 15.1 | 26.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.9 | 27.7 | 48.2 | 2.4 | 1007.0484 | 4092.585 | 4566.5458 | 2044 | 2.2341 | 4.3332 | 0.9 | 5.5 | -0.5 |  |  | 7.5658 | 20.2356 | 22.3412 | 24.1167
46023.4091 | 130.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 24 | 24 | 3020.4 | 706.1 | 49.7 | -0.2 | 76 | 90 | 2.5 | 1896 | 3.3 | 17 | 179 | 63 | 0.1 | 0.3 | 44.8 | 47 | 49.4 | 210 | 0 | 0 | 16 | 26.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.9 | 27.7 | 48.2 | 2.4 | 1007.0484 | 4092.585 | 4566.5458 | 1896 | 2.4085 | 4.2776 | 0.5 | 4.9 | -0.5 |  |  | 7.5816 | 20.2737 | 24.0852 | 23.6128
46023.4094 | 131 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 26 | 24 | 2971.4 | 706.1 | 49 | -0.2 | 76.4 | 90.4 | 2.5 | 1740 | 3.2 | 17 | 179 | 63 | 0.1 | 0.2 | 44.8 | 46.8 | 49.2 | 210 | 0 | 0 | 17.2 | 26 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.9 | 27.9 | 48 | 2.4 | 1007.156 | 4092.4 | 4599.8007 | 1740 | 2.6436 | 4.2082 | 0.4 | 4.2 | -0.3 |  |  | 7.5961 | 20.312 | 26.4356 | 23.9882
46023.4098 | 131.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2971.4 | 706.1 | 49 | -0.2 | 76.4 | 90.4 | 2.5 | 1740 | 3.4 | 17 | 179 | 63 | 0.2 | 0.2 | 44.6 | 46.8 | 49.2 | 210 | 0 | 0 | 18.4 | 25.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.9 | 27.7 | 48 | 2.4 | 1007.156 | 4092.4 | 4566.8272 | 1740 | 2.6246 | 4.2082 | 0.4 | 4.4 | -0.3 |  |  | 7.6106 | 20.3501 | 26.2461 | 24.2899
46023.4101 | 132 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 22 | 26 | 2981.2 | 706.1 | 49.2 | -0.2 | 76.5 | 90.2 | 2.5 | 1701 | 3.4 | 17 | 182 | 63 | 0.2 | 0.1 | 44.6 | 46.8 | 49.4 | 210 | 0 | 0 | 19.2 | 25.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.9 | 28.1 | 48.1 | 2.6 | 1007.1022 | 4092.4925 | 5018.6842 | 1701 | 2.9504 | 4.2221 | 0.3 | 4.6 | -0.5 |  |  | 7.6248 | 20.3919 | 29.5043 | 25.7225
46023.4105 | 132.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 22 | 24 | 2942 | 706.1 | 48.6 | -0.2 | 76.2 | 90 | 2.5 | 1701 | 3.2 | 17 | 182 | 63 | 0.2 | 0.2 | 44.6 | 46.8 | 49.4 | 210 | 0 | 0 | 20 | 25 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.9 | 28.1 | 48.1 | 2.6 | 1007.1022 | 4092.4925 | 5018.6842 | 1701 | 2.9504 | 4.1665 | 0.4 | 4 | -0.5 |  |  | 7.639 | 20.4337 | 29.5043 | 27.1551
46023.4108 | 133 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 22 | 24 | 22 | 2922.4 | 706.1 | 48.3 | -0.2 | 75.8 | 89.5 | 2.5 | 1725 | 3 | 16 | 182 | 64 | 0.2 | 0.2 | 44.6 | 46.8 | 49.2 | 210 | 0 | 0 | 20.4 | 24.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.9 | 27.9 | 48 | 2.4 | 1007.156 | 4092.4 | 4599.8007 | 1725 | 2.6666 | 4.1388 | 0.4 | 3.7 | -0.3 |  |  | 7.6534 | 20.472 | 26.6655 | 27.6712
46023.4112 | 133.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 24 | 24 | 2922.4 | 706.1 | 48.2 | -0.2 | 75.1 | 88.8 | 2.6 | 1725 | 3.2 | 16 | 182 | 64 | 0.2 | 0.3 | 44.6 | 46.8 | 49.2 | 207 | 0 | 0 | 21.1 | 24.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.9 | 27.3 | 48 | 2.4 | 1007.156 | 4092.4 | 4500.8803 | 1725 | 2.6092 | 4.1388 | 0.5 | 3.6 | -0.3 |  |  | 7.6677 | 20.5095 | 26.0921 | 27.6025
46023.4115 | 134 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 24 | 24 | 2912.6 | 706.1 | 48.2 | -0.2 | 74.6 | 88 | 2.6 | 1588 | 3.2 | 16 | 181 | 64 | 0.3 | 0.3 | 44.6 | 46.6 | 49.2 | 206 | 0 | 0 | 21.5 | 24.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.8 | 27.9 | 47.9 | 2.6 | 1007.2097 | 4092.3075 | 4983.2705 | 1588 | 3.1381 | 4.1249 | 0.5 | 3.6 | -0.4 |  |  | 7.681 | 20.5511 | 31.3808 | 28.6294
46023.4119 | 134.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 24 | 24 | 2902.8 | 706.1 | 48.1 | -0.2 | 74.1 | 87.1 | 2.6 | 1588 | 3.1 | 16 | 181 | 64 | 0.3 | 0.3 | 44.6 | 46.6 | 49 | 205 | 0 | 0 | 22 | 24.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.8 | 27.9 | 47.8 | 2.4 | 1007.2634 | 4092.215 | 4600.0831 | 1588 | 2.8968 | 4.111 | 0.5 | 3.5 | -0.2 |  |  | 7.6942 | 20.5894 | 28.9678 | 28.5221
46023.4122 | 135 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 24 | 24 | 2912.6 | 706.1 | 48.2 | -0.2 | 73.4 | 86.1 | 2.6 | 1624 | 3.2 | 16 | 181 | 64 | 0.3 | 0.3 | 45 | 46.6 | 49.2 | 206 | 0 | 0 | 22.3 | 24.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.8 | 27.7 | 47.9 | 2.6 | 1007.2097 | 4092.3075 | 4947.5482 | 1624 | 3.0465 | 4.1249 | 0.5 | 3.2 | -0.4 |  |  | 7.7077 | 20.6306 | 30.4652 | 28.7143
46023.4126 | 135.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 24 | 24 | 2892.9 | 706.1 | 47.9 | -0.2 | 72.8 | 85.4 | 2.6 | 1624 | 3.2 | 16 | 181 | 64 | 0.3 | 0.3 | 45.8 | 46.6 | 49 | 205 | 0 | 0 | 22.4 | 24.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.8 | 27.7 | 47.8 | 2.4 | 1007.2634 | 4092.215 | 4567.1076 | 1624 | 2.8123 | 4.097 | 0.5 | 2.1 | -0.2 |  |  | 7.7213 | 20.6687 | 28.1226 | 29.0057
46023.4129 | 136 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 26 | 24 | 2902.8 | 706.1 | 48.1 | -0.2 | 72.1 | 84.4 | 2.6 | 1622 | 3.1 | 16 | 181 | 64 | 0.4 | 0.4 | 46.1 | 46.6 | 49 | 206 | 0 | 0 | 22.6 | 24.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.8 | 27.9 | 47.8 | 2.4 | 1007.2634 | 4092.215 | 4600.0831 | 1622 | 2.8361 | 4.111 | 0.6 | 2 | -0.2 |  |  | 7.7348 | 20.707 | 28.3606 | 29.4594
46023.4132 | 136.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2912.6 | 715.9 | 48.2 | 0.1 | 71.4 | 83.5 | 2.7 | 1622 | 3.4 | 16 | 182 | 64 | 0.5 | 0.4 | 46.1 | 46.6 | 49 | 207 | 0 | 0 | 23 | 24.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.8 | 27.9 | 47.8 | 2.4 | 1007.2634 | 4092.215 | 4600.0831 | 1622 | 2.8361 | 4.0684 | 0.3 | 2.1 | -0.2 |  |  | 7.7483 | 20.7454 | 28.3606 | 28.8553
46023.4136 | 137 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2912.6 | 715.9 | 48.2 | 0.1 | 70.5 | 82.6 | 2.7 | 1653 | 3.3 | 16 | 182 | 65 | 0.5 | 0.4 | 46.1 | 46.5 | 49 | 207 | 0 | 0 | 23.2 | 24.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.7 | 27.5 | 47.75 | 2.5 | 1007.2902 | 4092.1687 | 4723.1266 | 1653 | 2.8573 | 4.0684 | 0.3 | 2.1 | -0.3 |  |  | 7.7621 | 20.7847 | 28.5731 | 28.7764
46023.4139 | 137.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2912.6 | 715.9 | 48.2 | 0.1 | 70.2 | 82 | 2.8 | 1653 | 3.4 | 16 | 182 | 65 | 0.6 | 0.5 | 46.1 | 46.6 | 49 | 207 | 0 | 0 | 23.3 | 24.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.7 | 27.9 | 47.8 | 2.4 | 1007.2634 | 4092.215 | 4600.0831 | 1653 | 2.7829 | 4.0684 | 0.4 | 2.1 | -0.3 |  |  | 7.7759 | 20.823 | 27.8287 | 28.2491
46023.4143 | 138 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 22 | 26 | 2902.8 | 715.9 | 48.1 | 0.1 | 69.8 | 81.2 | 2.8 | 1720 | 3.3 | 16 | 182 | 65 | 0.6 | 0.5 | 46.1 | 46.5 | 49.2 | 207 | 0 | 0 | 23.5 | 24.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.7 | 27.5 | 47.85 | 2.7 | 1007.2365 | 4092.2613 | 5100.8204 | 1720 | 2.9656 | 4.0548 | 0.4 | 2 | -0.5 |  |  | 7.7902 | 20.8656 | 29.6559 | 28.5558
46023.4146 | 138.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 22 | 24 | 2883.1 | 715.9 | 47.8 | 0.1 | 69.4 | 80.7 | 2.9 | 1720 | 3.1 | 16 | 180 | 65 | 0.7 | 0.6 | 46.1 | 46.5 | 49 | 206 | 0 | 0 | 23.7 | 24.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.7 | 27.5 | 47.75 | 2.5 | 1007.2902 | 4092.1687 | 4723.1266 | 1720 | 2.746 | 4.0272 | 0.5 | 1.7 | -0.3 |  |  | 7.8045 | 20.9049 | 27.46 | 28.3757
46023.415 | 139 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 28 | 24 | 2873.3 | 725.7 | 47.6 | 0.5 | 68.8 | 80.1 | 2.9 | 1678 | 3.1 | 16 | 180 | 65 | 0.9 | 0.8 | 46 | 46.3 | 48.3 | 207 | 0 | 0 | 23.8 | 24.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.7 | 27.5 | 47.3 | 2 | 1007.5308 | 4091.7525 | 3779.0195 | 1678 | 2.2521 | 3.9593 | 0.3 | 1.6 | 0.4 |  |  | 7.8185 | 20.9364 | 22.521 | 27.2077
46023.4153 | 139.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 28 | 26 | 2892.9 | 725.7 | 47.9 | 0.5 | 68.5 | 79.5 | 2.9 | 1678 | 3.3 | 16 | 180 | 65 | 1 | 0.9 | 46 | 46.3 | 48.6 | 207 | 0 | 0 | 24 | 24.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.6 | 27.7 | 47.45 | 2.3 | 1007.4507 | 4091.8913 | 4377.2792 | 1678 | 2.6086 | 3.9864 | 0.4 | 1.9 | 0 |  |  | 7.8325 | 20.9729 | 26.0863 | 26.7104
46023.4157 | 140 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 22 | 26 | 2892.9 | 715.9 | 47.9 | 0.1 | 68.4 | 79.3 | 2.9 | 1621 | 3.4 | 16 | 180 | 65 | 0.9 | 0.8 | 46 | 46.3 | 48.6 | 206 | 0 | 0 | 24.1 | 24.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.6 | 27.7 | 47.45 | 2.3 | 1007.4507 | 4091.8913 | 4377.2792 | 1621 | 2.7004 | 4.0409 | 0.7 | 1.9 | 0 |  |  | 7.846 | 21.0094 | 27.0036 | 26.5454
46023.416 | 140.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 22 | 24 | 2873.3 | 725.7 | 47.6 | 0.5 | 68.2 | 79.1 | 3 | 1621 | 3.1 | 16 | 180 | 65 | 0.9 | 0.9 | 45.8 | 46.1 | 48.6 | 205 | 0 | 0 | 24.2 | 24.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.6 | 27.7 | 47.35 | 2.5 | 1007.5041 | 4091.7987 | 4758.0568 | 1621 | 2.9353 | 3.9593 | 0.4 | 1.8 | 0 |  |  | 7.8595 | 21.049 | 29.3526 | 26.4847
46023.4164 | 141 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 28 | 24 | 2863.5 | 725.7 | 47.5 | 0.5 | 68 | 79 | 3 | 1680 | 3.1 | 16 | 181 | 65 | 1.1 | 1.1 | 45.6 | 46.1 | 48 | 204 | 0 | 0 | 24.2 | 24.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.5 | 27.9 | 47.05 | 1.9 | 1007.664 | 4091.5212 | 3642.5633 | 1680 | 2.1682 | 3.9458 | 0.6 | 1.9 | 0.5 |  |  | 7.8735 | 21.0794 | 21.6819 | 25.3291
46023.4167 | 141.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 28 | 26 | 2873.3 | 725.7 | 47.6 | 0.5 | 67.8 | 78.5 | 3 | 1680 | 3.3 | 16 | 181 | 65 | 1.1 | 1.1 | 45.6 | 46.1 | 48 | 204 | 0 | 0 | 24.2 | 24.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.5 | 27.3 | 47.05 | 1.9 | 1007.664 | 4091.5212 | 3564.2286 | 1680 | 2.1216 | 3.9593 | 0.6 | 2 | 0.5 |  |  | 7.8875 | 21.1091 | 21.2156 | 25.068
46023.4171 | 142 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2892.9 | 715.9 | 47.9 | 0.1 | 67.7 | 78.4 | 3 | 1610 | 3.5 | 16 | 181 | 65 | 0.9 | 0.9 | 45.6 | 46 | 48.3 | 204 | 0 | 0 | 24.2 | 24.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.5 | 27.3 | 47.15 | 2.3 | 1007.6108 | 4091.6137 | 4314.4621 | 1610 | 2.6798 | 4.0409 | 0.8 | 2.3 | 0.2 |  |  | 7.9009 | 21.145 | 26.7979 | 25.2103
46023.4174 | 142.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2892.9 | 715.9 | 47.9 | 0.1 | 67.8 | 78.4 | 3 | 1610 | 3.5 | 16 | 181 | 65 | 0.8 | 0.8 | 45.3 | 46 | 48.3 | 204 | 0 | 0 | 24.2 | 24.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.5 | 27.5 | 47.15 | 2.3 | 1007.6108 | 4091.6137 | 4346.0699 | 1610 | 2.6994 | 4.0409 | 0.7 | 2.6 | 0.2 |  |  | 7.9143 | 21.1812 | 26.9942 | 25.2085
46023.4178 | 143 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 28 | 26 | 28 | 2902.8 | 715.9 | 47.9 | 0.1 | 68 | 78.7 | 3 | 1778 | 3.5 | 16 | 180 | 65 | 0.8 | 0.7 | 44.2 | 46 | 48.3 | 204 | 0 | 0 | 24.2 | 24.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.5 | 27.7 | 47.15 | 2.3 | 1007.6108 | 4091.6137 | 4377.6777 | 1778 | 2.4621 | 4.0548 | 0.6 | 3.7 | 0.2 |  |  | 7.9292 | 21.2177 | 24.6214 | 24.2622
46023.4181 | 143.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2883.1 | 715.9 | 47.8 | 0.1 | 68.2 | 79 | 3 | 1778 | 3.3 | 16 | 180 | 65 | 0.8 | 0.7 | 43.8 | 45.8 | 48 | 204 | 0 | 0 | 24.2 | 24.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.5 | 27.7 | 46.9 | 2.2 | 1007.7438 | 4091.3825 | 4187.6598 | 1778 | 2.3553 | 4.0272 | 0.6 | 4 | 0.5 |  |  | 7.944 | 21.2526 | 23.5526 | 24.6364
46023.4185 | 144 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 29 | 26 | 2883.1 | 725.7 | 47.8 | 0.5 | 68.5 | 79.2 | 3 | 1763 | 3.3 | 16 | 180 | 64 | 0.9 | 0.9 | 43.6 | 45.6 | 48 | 204 | 0 | 0 | 24.2 | 24.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.5 | 27.7 | 46.8 | 2.4 | 1007.7968 | 4091.29 | 4568.4936 | 1763 | 2.5913 | 3.9729 | 0.4 | 4.2 | 0.5 |  |  | 7.9587 | 21.2907 | 25.9132 | 25.5759
46023.4188 | 144.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 28 | 29 | 28 | 2892.9 | 715.9 | 47.9 | 0.1 | 69 | 79.7 | 3 | 1763 | 3.5 | 16 | 180 | 64 | 0.9 | 0.9 | 43.5 | 45.6 | 47.8 | 204 | 0 | 0 | 24.1 | 24.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.5 | 27.5 | 46.7 | 2.2 | 1007.8499 | 4091.1975 | 4157.6739 | 1763 | 2.3583 | 4.0409 | 0.8 | 4.4 | 0.7 |  |  | 7.9734 | 21.3253 | 23.5829 | 24.9329
46023.4191 | 145 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 29 | 30 | 29 | 2922.4 | 715.9 | 48.3 | 0.1 | 69.4 | 80.1 | 3.1 | 1723 | 3.6 | 16 | 180 | 64 | 0.8 | 0.8 | 43.5 | 45.6 | 48 | 204 | 0 | 0 | 24.1 | 24.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 27.9 | 46.8 | 2.4 | 1007.7968 | 4091.29 | 4601.4791 | 1723 | 2.6706 | 4.0821 | 0.7 | 4.8 | 0.4 |  |  | 7.9877 | 21.3637 | 26.7062 | 24.8753
46023.4195 | 145.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 30 | 30 | 30 | 2961.6 | 715.9 | 48.9 | 0.1 | 70.1 | 80.8 | 3.1 | 1723 | 3.7 | 16 | 183 | 64 | 0.7 | 0.7 | 43.3 | 45.6 | 48 | 204 | 0 | 0 | 24 | 24.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 27.7 | 46.8 | 2.4 | 1007.7968 | 4091.29 | 4568.4936 | 1723 | 2.6515 | 4.1369 | 0.6 | 5.6 | 0.4 |  |  | 8.0021 | 21.4018 | 26.5148 | 25.2539
46023.4198 | 146 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 30 | 30 | 30 | 3010.6 | 715.9 | 49.6 | 0.1 | 71.1 | 82.1 | 3.1 | 1887 | 3.7 | 16 | 183 | 64 | 0.6 | 0.7 | 43.3 | 45.5 | 47.8 | 215 | 0 | 700 | 23.8 | 24.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 27.7 | 46.65 | 2.3 | 1007.8764 | 4091.1512 | 4378.3367 | 1887 | 2.3203 | 4.2053 | 0.6 | 6.3 | 0.6 |  |  | 8.0178 | 21.4382 | 23.2026 | 25.1839
46023.4202 | 146.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 30 | 30 | 30 | 3000.8 | 715.9 | 49.5 | 0.1 | 72.2 | 83.4 | 3.1 | 1887 | 4.2 | 19 | 183 | 64 | 0.6 | 0.9 | 43.3 | 45.3 | 48 | 218 | 80 | 2000 | 20.1 | 30.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 27.7 | 46.65 | 2.7 | 1007.8764 | 4091.1512 | 5139.7866 | 1887 | 2.7238 | 4.1916 | 0.8 | 6.2 | 0.4 |  |  | 8.0335 | 21.4811 | 27.2379 | 25.4489
46023.4205 | 147 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 30 | 25 | 30 | 2981.2 | 706.1 | 49.3 | 0.1 | 73.2 | 84.1 | 3.1 | 2039 | 4.2 | 19 | 183 | 63 | 0.6 | 1 | 43.1 | 45.3 | 49 | 215 | 85 | 2000 | 19.9 | 24.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 27.7 | 47.15 | 3.7 | 1007.6108 | 4091.6137 | 7042.3511 | 2039 | 3.4538 | 4.2221 | 0.9 | 6.2 | -0.6 |  |  | 8.0505 | 21.5398 | 34.5383 | 27.6399
46023.4209 | 147.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 28 | 25 | 28 | 2951.8 | 715.9 | 48.8 | 0.1 | 73.2 | 83.8 | 3.2 | 2039 | 4.1 | 18 | 181 | 60 | 0.4 | 0.9 | 43.1 | 45.5 | 49 | 215 | 85 | 2000 | 19 | 19.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 28.1 | 47.25 | 3.5 | 1007.5575 | 4091.7063 | 6757.6764 | 2039 | 3.3142 | 4.1232 | 0.8 | 5.7 | -0.6 |  |  | 8.0675 | 21.5961 | 33.1421 | 28.9271
46023.4212 | 148 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 25 | 26 | 2912.6 | 715.9 | 48.2 | 0.1 | 70.4 | 81.7 | 3.1 | 2123 | 3.7 | 18 | 181 | 58 | 0.7 | 0.8 | 43.3 | 45.5 | 49 | 215 | 81 | 2000 | 19.6 | 20 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 28.1 | 47.25 | 3.5 | 1007.5575 | 4091.7063 | 6757.6764 | 2123 | 3.1831 | 4.0684 | 0.7 | 4.9 | -0.6 |  |  | 8.0852 | 21.6524 | 31.8308 | 29.9903
46023.4216 | 0 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Stop | Heat | 0 | 0 | 0 | 0 | 2696.8 | 784.5 | 45 | 2.7 | 67.2 | 77.8 | 3.2 | 2123 | 0 | 0 | 181 | 53 | 1.7 | 1.6 | 44.8 | 45.8 | 46.6 | 0 | 0 | 0 | 21 | 21.7 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 27.5 | 46.2 | 0.8 | 1008.1142 | 4090.735 | 1512.107 | 2123 | 0.71225 | 3.4376 | -1.1 | 0.2 | 1.8 |  |  | 8.1029 | 21.665
46023.4219 | 0.5 | EHS MONO LOWTEMP | On | Off | On | Off | On | Stop | Heat | 0 | 0 | 0 | 0 | 1500.4 | 833.6 | 24.6 | 4.4 | 64.4 | 74.7 | 3.2 | 1337 | 0 | 0 | 181 | 47 | 3.5 | 3.7 | 43.3 | 46.8 | 47 | 0 | 0 | 0 | 16.5 | 24.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 27.5 | 46.9 | 0.2 | 1007.7438 | 4091.3825 | 377.9476 | 1337 | 0.28268 | 1.7999 | -0.7 | -18.7 | 1.4 |  |  | 8.114 | 21.6681
46023.4223 | 1 | EHS MONO LOWTEMP | On | Off | On | Off | On | Stop | Heat | 0 | 0 | 0 | 0 | 912 | 823.8 | 7 | 4.1 | 61.7 | 72.8 | 3.2 | 1337 | 0 | 0 | 181 | 45 | 4 | 5.8 | 32 | 47 | 47.1 | 0 | 0 | 0 | 14.8 | 25.3 | 100 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 0 | 47.05 | 0.1 | 1007.664 | 4091.5212 | 0 | 1337 | 0 | 1.1071 | 1.7 | -25 | 1.3 |  |  | 8.1252 | 21.6681
46023.4226 | 1.5 | EHS MONO LOWTEMP | Off | Off | On | Off | On | Stop | Heat | 0 | 0 | 0 | 0 | 813.9 | 843.4 | 3.7 | 4.8 | 58.5 | 70.2 | 3.3 | 1337 | 0 | 0 | 168 | 44 | 4.5 | 7.2 | 13.7 | 46.1 | 47.1 | 0 | 0 | 0 | 13 | 24.3 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 0 | 46.6 | 1 | 1007.9029 | 4091.105 | 0 | 1337 | 0 | 0.96502 | 2.4 | -10 | 1.3 |  |  | 8.1363 | 21.6681
46023.423 | 2 | EHS MONO LOWTEMP | Off | Off | On | Off | On | Stop | Heat | 0 | 0 | 0 | 0 | 813.9 | 843.4 | 3.7 | 4.8 | 56.8 | 68.1 | 3.3 | 136 | 0 | 0 | 168 | 43 | 4.8 | 7.9 | 11.1 | 44 | 47.1 | 0 | 0 | 0 | 11.6 | 23.3 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.3 | 0 | 45.55 | 3.1 | 1008.4558 | 4090.1337 | 0 | 136 | 0 | 0.96502 | 3.1 | -7.4 | 1.2 |  |  | 8.1374 | 21.6681
46023.4233 | 2.5 | EHS MONO LOWTEMP | Off | Off | On | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 813.9 | 853.2 | 3.7 | 5.1 | 55.6 | 66.2 | 3.4 | 136 | 0 | 0 | 168 | 42 | 4.9 | 8.4 | 10.9 | 43 | 47.1 | 0 | 0 | 0 | 10.3 | 22.2 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.2 | 0 | 45.05 | 4.1 | 1008.717 | 4089.6712 | 0 | 136 | 0 | 0.95394 | 3.3 | -7.2 | 1.1 |  |  | 8.1386 | 21.6681
46023.4237 | 3 | EHS MONO LOWTEMP | Off | Off | On | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 804.1 | 843.4 | 3.4 | 4.8 | 54.5 | 64.8 | 3.5 | 139 | 0 | 0 | 168 | 42 | 4.9 | 8.8 | 11.4 | 42.5 | 47.1 | 0 | 0 | 0 | 9.3 | 21.2 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.2 | 0 | 44.8 | 4.6 | 1008.847 | 4089.44 | 0 | 139 | 0 | 0.9534 | 4 | -8 | 1.1 |  |  | 8.1397 | 21.6681
46023.424 | 3.5 | EHS MONO LOWTEMP | Off | Off | On | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 794.3 | 833.6 | 3 | 4.8 | 53.8 | 63.7 | 3.6 | 139 | 0 | 0 | 167 | 42 | 4.7 | 9.1 | 11.7 | 42.4 | 47.1 | 0 | 0 | 0 | 8.7 | 20.3 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.2 | 0 | 44.75 | 4.7 | 1008.873 | 4089.3938 | 0 | 139 | 0 | 0.95286 | 4.3 | -8.7 | 1.1 |  |  | 8.1409 | 21.6681
46023.4244 | 4 | EHS MONO LOWTEMP | Off | Off | On | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 794.3 | 833.6 | 3 | 4.4 | 53.1 | 62.7 | 3.6 | 139 | 0 | 0 | 167 | 42 | 4.4 | 9.4 | 12 | 42.2 | 47.1 | 0 | 0 | 0 | 8.1 | 19.6 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.1 | 0 | 44.65 | 4.9 | 1008.9249 | 4089.3012 | 0 | 139 | 0 | 0.95286 | 5 | -9 | 1 |  |  | 8.1421 | 21.6681
46023.4247 | 4.5 | EHS MONO LOWTEMP | Off | Off | On | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 794.3 | 823.8 | 3 | 4.1 | 52.3 | 61.8 | 3.6 | 139 | 0 | 0 | 167 | 41 | 4.3 | 9.8 | 12.4 | 42.4 | 47 | 0 | 0 | 0 | 7.5 | 18.8 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.1 | 0 | 44.7 | 4.6 | 1008.8989 | 4089.3475 | 0 | 139 | 0 | 0.96419 | 5.7 | -9.4 | 1.1 |  |  | 8.1432 | 21.6681
46023.4251 | 0 | EHS MONO LOWTEMP | Off | Off | On | Off | Off | Safety Start | Heat | 0 | 0 | 0 | 0 | 813.9 | 843.4 | 3.7 | 4.8 | 51 | 60.8 | 3.6 | 139 | 0 | 0 | 167 | 41 | 4.3 | 10.1 | 12.1 | 42.7 | 46.8 | 2000 | 0 | 0 | 7 | 18.1 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.1 | 0 | 44.75 | 4.1 | 1008.873 | 4089.3938 | 0 | 139 | 0 | 0.96502 | 5.3 | -8.4 | 1.3 |  |  | 8.1444 | 21.6681
46023.4254 | 0.5 | EHS MONO LOWTEMP | Off | Off | On | Off | On | Safety Start | Heat | 0 | 33 | 40 | 31 | 1471 | 774.7 | 22.3 | 2.3 | 51 | 59.8 | 3.6 | 200 | 1.9 | 8 | 167 | 38 | 3.9 | 8.5 | 11.1 | 45 | 45.3 | 125 | 0 | 0 | 7 | 17.2 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.1 | 29.7 | 45.15 | 0.3 | 1008.6648 | 4089.7638 | 612.5923 | 200 | 3.063 | 1.8988 | 6.2 | 11.2 | 2.8 |  |  | 8.146 | 21.6732
46023.4257 | 1 | EHS MONO LOWTEMP | On | Off | On | Off | On | Safety Start | Heat | 0 | 40 | 40 | 40 | 2500.7 | 745.3 | 42 | 1.3 | 55.1 | 59.4 | 3.6 | 200 | 4 | 14 | 181 | 39 | 2 | 3.2 | 26.3 | 44.2 | 44.8 | 125 | 0 | 0 | 7 | 17.3 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.1 | 27.7 | 44.5 | 0.6 | 1009.0026 | 4089.1625 | 1142.8952 | 200 | 5.7145 | 3.3553 | 1.9 | 15.7 | 3.3 |  |  | 8.1477 | 21.6828
46023.4261 | 1.5 | EHS MONO LOWTEMP | On | Off | On | Off | On | Safety Start | Heat | 0 | 40 | 40 | 40 | 2579.1 | 764.9 | 43.1 | 2 | 61.7 | 62.5 | 3.5 | 1261 | 4.2 | 14 | 181 | 47 | 2 | 2.2 | 38.4 | 43 | 44.4 | 330 | 0 | 0 | 6.6 | 19.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.2 | 27.7 | 43.7 | 1.4 | 1009.415 | 4088.4225 | 2667.3629 | 1261 | 2.1153 | 3.3718 | 0.2 | 4.7 | 3.8 |  |  | 8.1582 | 21.705
46023.4264 | 2 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Safety Start | Heat | 0 | 21 | 20 | 23 | 2667.4 | 715.9 | 44.6 | 0.1 | 64.2 | 66.8 | 3.4 | 1261 | 3 | 15 | 181 | 53 | 1.2 | 1.4 | 41.6 | 42.5 | 45.8 | 164 | 0 | 0 | 6.6 | 22.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.2 | 27.7 | 44.15 | 3.3 | 1009.1835 | 4088.8387 | 6286.553 | 1261 | 4.9854 | 3.7259 | 1.3 | 3 | 2.4 |  |  | 8.1687 | 21.7574
46023.4268 | 2.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Safety Start | Heat | 0 | 20 | 20 | 20 | 2608.6 | 725.7 | 43.7 | 0.5 | 64.2 | 69.2 | 3.3 | 1982 | 2.4 | 14 | 181 | 55 | 1.1 | 1.4 | 41.3 | 42.4 | 44.8 | 164 | 0 | 0 | 6.7 | 23.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.2 | 27.7 | 43.6 | 2.4 | 1009.4664 | 4088.33 | 4572.751 | 1982 | 2.3071 | 3.5946 | 0.9 | 2.4 | 3.4 |  |  | 8.1852 | 21.7955 | 23.0714
46023.4271 | 3 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Safety Start | Heat | 0 | 20 | 20 | 20 | 2608.6 | 725.7 | 43.7 | 0.1 | 63.1 | 69.7 | 3.3 | 1982 | 2.4 | 14 | 181 | 56 | 0.7 | 2.3 | 40.8 | 42.4 | 44.8 | 164 | 0 | 0 | 7 | 23.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.3 | 27.9 | 43.6 | 2.4 | 1009.4664 | 4088.33 | 4605.7672 | 1982 | 2.3238 | 3.5946 | 2.2 | 2.9 | 3.5 |  |  | 8.2018 | 21.8339 | 23.238
46023.4275 | 3.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Safety Start | Heat | 0 | 20 | 20 | 20 | 2608.6 | 725.7 | 43.7 | 0.5 | 62.1 | 69.4 | 3.3 | 1257 | 2.4 | 14 | 180 | 57 | 0.8 | 3.8 | 40.5 | 42.4 | 44.6 | 164 | 0 | 0 | 8 | 23.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.3 | 27.9 | 43.5 | 2.2 | 1009.5176 | 4088.2375 | 4222.0721 | 1257 | 3.3588 | 3.5946 | 3.3 | 3.2 | 3.7 |  |  | 8.2122 | 21.869 | 33.5885
46023.4278 | 4 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 20 | 20 | 20 | 2588.9 | 725.7 | 43.4 | 0.5 | 61.1 | 68.8 | 3.3 | 1257 | 2.4 | 14 | 180 | 57 | 0.9 | 4.9 | 40.3 | 42.1 | 44.4 | 164 | 0 | 0 | 9.3 | 23.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.3 | 27.9 | 43.25 | 2.3 | 1009.6455 | 4088.0062 | 4414.2939 | 1257 | 3.5118 | 3.5675 | 4.4 | 3.1 | 3.9 |  |  | 8.2227 | 21.9058 | 35.1177
46023.4282 | 4.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 20 | 20 | 20 | 2608.6 | 725.7 | 43.7 | 0.5 | 60.6 | 68.2 | 3.3 | 1242 | 2.4 | 15 | 180 | 57 | 1 | 5.3 | 40.1 | 42.2 | 44.4 | 163 | 0 | 0 | 10.8 | 23.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.3 | 27.9 | 43.3 | 2.2 | 1009.6199 | 4088.0525 | 4222.309 | 1242 | 3.3996 | 3.5946 | 4.8 | 3.6 | 3.9 |  |  | 8.2331 | 21.941 | 33.996
46023.4285 | 5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 21 | 26 | 21 | 2608.6 | 735.5 | 43.7 | 0.9 | 60.3 | 68 | 3.3 | 1242 | 2.4 | 14 | 180 | 57 | 1.1 | 5.6 | 40 | 42.1 | 44.2 | 162 | 0 | 0 | 12.2 | 23.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.3 | 27.5 | 43.15 | 2.1 | 1009.6965 | 4087.9138 | 3972.7691 | 1242 | 3.1987 | 3.5467 | 4.7 | 3.7 | 4.1 |  |  | 8.2434 | 21.9741 | 31.9869
46023.4289 | 5.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 23 | 26 | 22 | 2638 | 725.7 | 44.2 | 0.5 | 60.3 | 68 | 3.3 | 1244 | 2.6 | 15 | 182 | 58 | 1.1 | 5.7 | 40 | 42.1 | 44.4 | 162 | 0 | 0 | 13.2 | 23.2 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.3 | 27.5 | 43.25 | 2.3 | 1009.6455 | 4088.0062 | 4351.0065 | 1244 | 3.4976 | 3.6351 | 5.2 | 4.2 | 3.9 |  |  | 8.2538 | 22.0104 | 34.9759
46023.4292 | 6 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 26 | 24 | 2696.8 | 715.9 | 45 | 0.1 | 60.8 | 68.4 | 3.3 | 1244 | 2.8 | 15 | 182 | 58 | 0.9 | 5.7 | 40 | 42.1 | 44.6 | 162 | 0 | 0 | 14.4 | 23.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.3 | 27.5 | 43.35 | 2.5 | 1009.5944 | 4088.0988 | 4729.2225 | 1244 | 3.8016 | 3.767 | 5.6 | 5 | 3.7 |  |  | 8.2641 | 22.0498 | 38.0163
46023.4296 | 6.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2863.5 | 706.1 | 47.5 | -0.2 | 61.8 | 69.7 | 3.3 | 1402 | 3.2 | 16 | 182 | 59 | 0.5 | 5.4 | 40 | 42.1 | 44.6 | 162 | 0 | 0 | 15.5 | 22.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.3 | 27.9 | 43.35 | 2.5 | 1009.5944 | 4088.0988 | 4798.0112 | 1402 | 3.4223 | 4.0554 | 5.6 | 7.5 | 3.7 |  |  | 8.2758 | 22.0898 | 34.2226
46023.4299 | 7 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 26 | 26 | 3040 | 696.3 | 50 | -0.6 | 63.7 | 72.1 | 3.3 | 1402 | 3.4 | 17 | 182 | 60 | 0.1 | 5.2 | 40 | 42.1 | 44.2 | 189 | 0 | 0 | 16.4 | 22.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.3 | 27.5 | 43.15 | 2.1 | 1009.6965 | 4087.9138 | 3972.7691 | 1402 | 2.8336 | 4.3659 | 5.8 | 10 | 4.1 |  |  | 8.2875 | 22.1229 | 28.3364 | 33.5076
46023.4303 | 7.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 26 | 26 | 3069.5 | 706.1 | 50.4 | -0.2 | 65.1 | 74.1 | 3.3 | 1669 | 3.4 | 17 | 182 | 60 | 0.1 | 5.2 | 40 | 42.1 | 44.2 | 198 | 0 | 0 | 16.9 | 22.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.3 | 27.7 | 43.15 | 2.1 | 1009.6965 | 4087.9138 | 4001.662 | 1669 | 2.3976 | 4.3471 | 5.4 | 10.4 | 4.1 |  |  | 8.3014 | 22.1562 | 23.9764 | 31.9055
46023.4306 | 8 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 26 | 26 | 3010.6 | 706.1 | 49.6 | -0.2 | 67.2 | 77.2 | 3.3 | 1669 | 3.4 | 17 | 180 | 61 | 0.4 | 5.2 | 40 | 42.1 | 44.4 | 207 | 0 | 0 | 17.6 | 22.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.3 | 27.7 | 43.25 | 2.3 | 1009.6455 | 4088.0062 | 4382.6502 | 1669 | 2.6259 | 4.2637 | 5.4 | 9.6 | 3.9 |  |  | 8.3153 | 22.1928 | 26.2591 | 30.1622
46023.431 | 8.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2912.6 | 715.9 | 48.2 | 0.1 | 69.1 | 80.1 | 3.3 | 1746 | 3.3 | 16 | 180 | 61 | 0.6 | 5.4 | 40 | 42.1 | 44.6 | 213 | 0 | 0 | 18.3 | 22.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.3 | 27.7 | 43.35 | 2.5 | 1009.5944 | 4088.0988 | 4763.6169 | 1746 | 2.7283 | 4.0684 | 5.3 | 8.2 | 3.7 |  |  | 8.3299 | 22.2325 | 27.283 | 28.0155
46023.4313 | 9 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 24 | 26 | 2843.9 | 725.7 | 47.2 | 0.5 | 70.4 | 82.1 | 3.2 | 1746 | 3.2 | 16 | 180 | 60 | 0.9 | 3 | 40 | 42.1 | 44.8 | 211 | 0 | 0 | 18.9 | 22.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 27.7 | 43.45 | 2.7 | 1009.5432 | 4088.1912 | 5144.5619 | 1746 | 2.9465 | 3.9188 | 2.5 | 7.2 | 3.6 |  |  | 8.3444 | 22.2753 | 29.4648 | 27.064
46023.4316 | 9.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 24 | 24 | 2765.5 | 725.7 | 46.1 | 0.5 | 71.1 | 83.3 | 3.2 | 1662 | 2.9 | 16 | 180 | 60 | 1.1 | 1.5 | 40 | 42.1 | 44.8 | 209 | 0 | 0 | 19.3 | 22.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 27.7 | 43.45 | 2.7 | 1009.5432 | 4088.1912 | 5144.5619 | 1662 | 3.0954 | 3.8108 | 1 | 6.1 | 3.6 |  |  | 8.3583 | 22.3182 | 30.954 | 27.5875
46023.432 | 10 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 30 | 24 | 2736 | 735.5 | 45.6 | 0.9 | 71.2 | 83.5 | 3.2 | 1662 | 2.9 | 15 | 180 | 60 | 1.2 | 1.4 | 40 | 42.1 | 44.8 | 207 | 0 | 0 | 19.6 | 22.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 27.7 | 43.45 | 2.7 | 1009.5432 | 4088.1912 | 5144.5619 | 1662 | 3.0954 | 3.7199 | 0.5 | 5.6 | 3.6 |  |  | 8.3721 | 22.3611 | 30.954 | 28.983
46023.4323 | 10.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 27 | 30 | 26 | 2736 | 725.7 | 45.6 | 0.5 | 71.4 | 83.4 | 3.2 | 1516 | 3.1 | 15 | 180 | 60 | 1.2 | 1.2 | 40.1 | 42.2 | 45 | 207 | 0 | 0 | 19.9 | 22.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 27.5 | 43.6 | 2.8 | 1009.4664 | 4088.33 | 5296.3572 | 1516 | 3.4936 | 3.7702 | 0.7 | 5.5 | 3.4 |  |  | 8.3848 | 22.4052 | 34.9364 | 30.7185
46023.4327 | 11 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 29 | 30 | 28 | 2736 | 725.7 | 45.6 | 0.5 | 71.4 | 83 | 3.2 | 1516 | 3.2 | 15 | 180 | 60 | 1 | 1 | 40.1 | 42.2 | 45.1 | 207 | 80 | 700 | 20.3 | 22.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 27.7 | 43.65 | 2.9 | 1009.4407 | 4088.3762 | 5525.3296 | 1516 | 3.6447 | 3.7702 | 0.5 | 5.5 | 3.3 |  |  | 8.3974 | 22.4512 | 36.4468 | 32.5512
46023.433 | 11.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 30 | 30 | 30 | 2755.7 | 715.9 | 45.9 | 0.1 | 71.5 | 82.6 | 3.2 | 1634 | 3.9 | 17 | 180 | 60 | 0.9 | 0.8 | 40.1 | 42.2 | 45.8 | 207 | 80 | 2000 | 18.9 | 27.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 27.7 | 44 | 3.6 | 1009.2608 | 4088.7 | 6858.3504 | 1634 | 4.1973 | 3.8493 | 0.7 | 5.8 | 2.6 |  |  | 8.411 | 22.5084 | 41.9728 | 35.0528
46023.4334 | 12 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 30 | 25 | 30 | 2755.7 | 706.1 | 45.9 | 0.1 | 71.8 | 82.3 | 3.2 | 1634 | 3.8 | 17 | 180 | 59 | 0.6 | 0.7 | 40.1 | 42.2 | 46.1 | 207 | 80 | 2000 | 18.4 | 20.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 27.7 | 44.15 | 3.9 | 1009.1835 | 4088.8387 | 7429.5626 | 1634 | 4.5469 | 3.9027 | 0.6 | 5.8 | 2.3 |  |  | 8.4246 | 22.5703 | 45.4686 | 37.9557
46023.4337 | 12.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 28 | 25 | 28 | 2736 | 715.9 | 45.6 | 0.1 | 69.4 | 80.1 | 3.2 | 1953 | 3.6 | 17 | 179 | 56 | 0.6 | 0.6 | 40.5 | 42.4 | 46.3 | 207 | 77 | 2000 | 18.3 | 18.9 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 28.1 | 44.35 | 3.9 | 1009.0802 | 4089.0237 | 7536.4183 | 1953 | 3.8589 | 3.8218 | 0.5 | 5.1 | 2.1 |  |  | 8.4409 | 22.6331 | 38.5889 | 39.4827
46023.4341 | 13 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2716.4 | 725.7 | 45.3 | 0.5 | 65.4 | 76.1 | 3.2 | 1953 | 3.7 | 17 | 179 | 54 | 0.9 | 0.9 | 41.3 | 42.5 | 46.1 | 203 | 77 | 2000 | 19.2 | 19.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 27.5 | 44.3 | 3.6 | 1009.106 | 4088.9775 | 6808.2497 | 1953 | 3.486 | 3.7431 | 0.4 | 4 | 2.3 |  |  | 8.4572 | 22.6899 | 34.8605 | 39.4675
46023.4344 | 13.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2716.4 | 715.9 | 45.3 | 0.1 | 62 | 71.5 | 3.2 | 1870 | 3.7 | 18 | 179 | 53 | 0.9 | 0.8 | 43.1 | 42.7 | 46.3 | 203 | 76 | 2000 | 19.9 | 20.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 27.5 | 44.5 | 3.6 | 1009.0026 | 4089.1625 | 6807.8597 | 1870 | 3.6406 | 3.7944 | 0.7 | 2.2 | 2.1 |  |  | 8.4728 | 22.7466 | 36.4057 | 39.4593
46023.4348 | 14 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 29 | 31 | 28 | 2706.6 | 715.9 | 45.2 | 0.1 | 60.6 | 68.2 | 3.2 | 1870 | 3.7 | 17 | 179 | 53 | 0.8 | 0.7 | 43.6 | 42.7 | 46.1 | 201 | 76 | 2000 | 21.1 | 21.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 27.9 | 44.4 | 3.4 | 1009.0544 | 4089.07 | 6523.3544 | 1870 | 3.4884 | 3.7807 | 0.6 | 1.6 | 2.3 |  |  | 8.4883 | 22.8009 | 34.8842 | 38.0416
46023.4351 | 14.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 31 | 31 | 30 | 2706.6 | 715.9 | 45.2 | 0.1 | 60.8 | 67.4 | 3.2 | 1908 | 3.9 | 17 | 179 | 52 | 0.8 | 0.7 | 43.6 | 42.7 | 46.1 | 201 | 76 | 2000 | 21.1 | 21.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 27.9 | 44.4 | 3.4 | 1009.0544 | 4089.07 | 6523.3544 | 1908 | 3.4189 | 3.7807 | 0.6 | 1.6 | 2.3 |  |  | 8.5042 | 22.8553 | 34.1895 | 35.7858
46023.4355 | 15 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 32 | 34 | 31 | 2716.4 | 715.9 | 45.3 | 0.1 | 62.2 | 67.7 | 3.2 | 1908 | 4 | 17 | 182 | 52 | 0.6 | 0.6 | 43.8 | 42.7 | 46.1 | 202 | 80 | 2000 | 20 | 24.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 27.3 | 44.4 | 3.4 | 1009.0544 | 4089.07 | 6383.0672 | 1908 | 3.3454 | 3.7944 | 0.5 | 1.5 | 2.3 |  |  | 8.5201 | 22.9085 | 33.4542 | 34.7588
46023.4358 | 15.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 34 | 34 | 33 | 2765.5 | 706.1 | 46.1 | -0.2 | 64 | 69.7 | 3.2 | 2041 | 4.3 | 18 | 182 | 52 | 0.4 | 0.3 | 44.2 | 42.8 | 46.6 | 202 | 87 | 2000 | 20.4 | 22.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 27.3 | 44.7 | 3.8 | 1008.8989 | 4089.3475 | 7133.4015 | 2041 | 3.4951 | 3.9166 | 0.5 | 1.9 | 1.8 |  |  | 8.5371 | 22.9679 | 34.9505 | 34.7768
46023.4362 | 16 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 34 | 26 | 34 | 2785.1 | 696.3 | 46.4 | -0.6 | 65 | 71.5 | 3.2 | 2041 | 4.4 | 17 | 182 | 52 | 0.1 | 0 | 44.6 | 42.8 | 47.1 | 203 | 82 | 2000 | 18.6 | 19 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 27.7 | 44.95 | 4.3 | 1008.769 | 4089.5788 | 8189.6867 | 2041 | 4.0126 | 3.9999 | 0.6 | 1.8 | 1.3 |  |  | 8.5542 | 23.0362 | 40.1259 | 35.5209
46023.4365 | 16.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 32 | 26 | 32 | 2794.9 | 696.3 | 46.5 | -0.6 | 65 | 72.1 | 3.2 | 2041 | 4.2 | 18 | 182 | 51 | 0.1 | 0 | 44.6 | 43 | 47.1 | 203 | 81 | 2000 | 18.2 | 18.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 27.7 | 45.05 | 4.1 | 1008.717 | 4089.6712 | 7808.5447 | 2041 | 3.8258 | 4.0139 | 0.6 | 1.9 | 1.3 |  |  | 8.5712 | 23.1013 | 38.2584 | 36.1957
46023.4369 | 17 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 28 | 30 | 2785.1 | 706.1 | 46.4 | -0.2 | 63.5 | 71.4 | 3.2 | 2239 | 4 | 18 | 181 | 51 | 0.3 | 0.3 | 44.6 | 43.1 | 47.1 | 202 | 81 | 2000 | 19 | 19.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 27.5 | 45.1 | 4 | 1008.6909 | 4089.7175 | 7562.9783 | 2239 | 3.3778 | 3.9443 | 0.5 | 1.8 | 1.3 |  |  | 8.5898 | 23.1643 | 33.7784 | 36.1135
46023.4372 | 17.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2785.1 | 715.9 | 46.4 | 0.1 | 61.5 | 69.1 | 3.2 | 2239 | 3.9 | 18 | 181 | 51 | 0.5 | 0.5 | 44.8 | 43.3 | 47.1 | 202 | 81 | 2000 | 20.3 | 20.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 27.5 | 45.2 | 3.8 | 1008.6388 | 4089.81 | 7184.6204 | 2239 | 3.2089 | 3.8903 | 0.4 | 1.6 | 1.3 |  |  | 8.6085 | 23.2242 | 32.0885 | 35.8403
46023.4376 | 18 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 30 | 28 | 2785.1 | 715.9 | 46.4 | 0.1 | 60.5 | 67 | 3.2 | 2131 | 3.9 | 18 | 181 | 51 | 0.6 | 0.6 | 44.8 | 43.6 | 47 | 200 | 80 | 2000 | 21.8 | 22.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 28.1 | 45.3 | 3.4 | 1008.5866 | 4089.9025 | 6568.408 | 2131 | 3.0823 | 3.8903 | 0.5 | 1.6 | 1.4 |  |  | 8.6262 | 23.2789 | 30.8231 | 35.0149
46023.4379 | 18.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 30 | 30 | 2775.3 | 715.9 | 46.2 | 0.1 | 60.5 | 66.4 | 3.2 | 2131 | 4.1 | 18 | 181 | 51 | 0.6 | 0.6 | 45 | 43.5 | 47.1 | 200 | 80 | 2000 | 22.2 | 22.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 27.7 | 45.3 | 3.6 | 1008.5866 | 4089.9025 | 6855.7844 | 2131 | 3.2172 | 3.8767 | 0.5 | 1.2 | 1.3 |  |  | 8.644 | 23.336 | 32.1717 | 33.424
46023.4382 | 19 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 29 | 30 | 2785.1 | 715.9 | 46.4 | 0.1 | 61.7 | 66.8 | 3.3 | 1999 | 4.1 | 18 | 181 | 52 | 0.6 | 0.5 | 45 | 43.6 | 47.1 | 199 | 80 | 2000 | 21.2 | 21.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.4 | 27.7 | 45.35 | 3.5 | 1008.5604 | 4089.9488 | 6665.2487 | 1999 | 3.3343 | 3.8903 | 0.4 | 1.4 | 1.3 |  |  | 8.6607 | 23.3916 | 33.3429 | 32.4409
46023.4386 | 19.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 29 | 29 | 2775.3 | 715.9 | 46.2 | 0.1 | 62.5 | 68.2 | 3.3 | 1999 | 4 | 18 | 182 | 52 | 0.6 | 0.5 | 45 | 43.6 | 47.1 | 199 | 80 | 2000 | 21.6 | 22 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.3 | 27.9 | 45.35 | 3.5 | 1008.5604 | 4089.9488 | 6713.3733 | 1999 | 3.3584 | 3.8767 | 0.4 | 1.2 | 1.2 |  |  | 8.6773 | 23.4475 | 33.5837 | 32.402
46023.4389 | 20 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 31 | 29 | 2785.1 | 715.9 | 46.4 | 0.1 | 63.4 | 69.5 | 3.3 | 2072 | 4 | 18 | 182 | 52 | 0.7 | 0.6 | 45 | 43.8 | 47.1 | 200 | 80 | 2000 | 22.2 | 22.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.3 | 27.9 | 45.45 | 3.3 | 1008.5082 | 4090.0413 | 6329.567 | 2072 | 3.0548 | 3.8903 | 0.5 | 1.4 | 1.2 |  |  | 8.6946 | 23.5003 | 30.5481 | 32.0939
46023.4393 | 20.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 31 | 31 | 31 | 2794.9 | 706.1 | 46.5 | -0.2 | 64.2 | 70.7 | 3.3 | 2072 | 4.2 | 18 | 182 | 52 | 0.6 | 0.5 | 45.1 | 43.8 | 47.2 | 200 | 80 | 2000 | 21.7 | 22.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.3 | 27.7 | 45.5 | 3.4 | 1008.482 | 4090.0875 | 6474.5291 | 2072 | 3.1248 | 3.9582 | 0.7 | 1.4 | 1.1 |  |  | 8.7118 | 23.5542 | 31.2477 | 32.1788
46023.4396 | 21 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 31 | 33 | 31 | 2804.7 | 706.1 | 46.7 | -0.2 | 65.1 | 71.7 | 3.3 | 2045 | 4.2 | 18 | 182 | 52 | 0.5 | 0.4 | 45.1 | 43.8 | 47.2 | 199 | 80 | 2000 | 21 | 21.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.3 | 27.7 | 45.5 | 3.4 | 1008.482 | 4090.0875 | 6474.5291 | 2045 | 3.166 | 3.9721 | 0.6 | 1.6 | 1.1 |  |  | 8.7289 | 23.6082 | 31.6603 | 32.0765
46023.44 | 21.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 33 | 33 | 33 | 2834.1 | 706.1 | 47.1 | -0.2 | 65.7 | 72.7 | 3.3 | 2150 | 4.4 | 18 | 182 | 52 | 0.5 | 0.3 | 45.5 | 43.8 | 47.5 | 199 | 80 | 2000 | 20 | 20.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.3 | 27.7 | 45.65 | 3.7 | 1008.4034 | 4090.2263 | 7045.5011 | 2150 | 3.277 | 4.0137 | 0.5 | 1.6 | 0.8 |  |  | 8.7468 | 23.6669 | 32.7698 | 31.9619
46023.4403 | 22 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 33 | 27 | 33 | 2853.7 | 706.1 | 47.4 | -0.2 | 65.7 | 73.2 | 3.3 | 2150 | 4.4 | 18 | 182 | 51 | 0.2 | 0.1 | 45.6 | 44 | 47.7 | 199 | 80 | 2000 | 18.9 | 19.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.3 | 27.5 | 45.85 | 3.7 | 1008.2985 | 4090.4113 | 6994.2194 | 2150 | 3.2531 | 4.0415 | 0.3 | 1.8 | 0.6 |  |  | 8.7647 | 23.7252 | 32.5313 | 31.7514
46023.4407 | 22.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 31 | 27 | 31 | 2853.7 | 706.1 | 47.4 | -0.2 | 65 | 73 | 3.3 | 2246 | 4.2 | 18 | 182 | 51 | 0.3 | 0.2 | 45.6 | 44.2 | 47.8 | 199 | 80 | 2000 | 18.9 | 19.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.3 | 27.7 | 46 | 3.6 | 1008.2196 | 4090.55 | 6854.375 | 2246 | 3.0518 | 4.0415 | 0.4 | 1.8 | 0.5 |  |  | 8.7834 | 23.7823 | 30.5181 | 31.7454
46023.441 | 23 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 28 | 29 | 2843.9 | 706.1 | 47.2 | -0.2 | 63.5 | 71.5 | 3.3 | 2246 | 4 | 18 | 182 | 51 | 0.4 | 0.4 | 45.6 | 44.2 | 47.7 | 199 | 80 | 2000 | 19.9 | 20.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.3 | 27.7 | 45.95 | 3.5 | 1008.2459 | 4090.5037 | 6664.0742 | 2246 | 2.9671 | 4.0276 | 0.6 | 1.6 | 0.6 |  |  | 8.8022 | 23.8378 | 29.6709 | 31.4301
46023.4414 | 23.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2824.3 | 715.9 | 47.1 | 0.1 | 62.2 | 70.2 | 3.3 | 2117 | 3.9 | 19 | 182 | 51 | 0.7 | 0.6 | 45.6 | 44.4 | 47.7 | 199 | 80 | 2000 | 21.1 | 21.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.3 | 27.1 | 46.05 | 3.3 | 1008.1933 | 4090.5963 | 6146.9884 | 2117 | 2.9036 | 3.9451 | 0.5 | 1.5 | 0.6 |  |  | 8.8198 | 23.889 | 29.0363 | 30.9053
46023.4417 | 24 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 30 | 28 | 2834.1 | 715.9 | 47.1 | 0.1 | 62 | 68.8 | 3.3 | 2117 | 4 | 18 | 179 | 51 | 0.7 | 0.7 | 45.6 | 44.6 | 47.6 | 199 | 80 | 2000 | 22.5 | 23 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.3 | 27.9 | 46.1 | 3 | 1008.167 | 4090.6425 | 5753.0506 | 2117 | 2.7175 | 3.9588 | 0.6 | 1.5 | 0.7 |  |  | 8.8374 | 23.937 | 27.1755 | 29.7864
46023.4421 | 24.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 30 | 30 | 2834.1 | 715.9 | 47.1 | 0.1 | 62.8 | 68.7 | 3.4 | 2028 | 4.2 | 18 | 179 | 52 | 0.8 | 0.7 | 45.6 | 44.6 | 47.6 | 199 | 80 | 2000 | 22.8 | 23.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.3 | 27.9 | 46.1 | 3 | 1008.167 | 4090.6425 | 5753.0506 | 2028 | 2.8368 | 3.9588 | 0.6 | 1.5 | 0.7 |  |  | 8.8543 | 23.9849 | 28.3681 | 28.9538
46023.4424 | 25 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 31 | 30 | 2843.9 | 715.9 | 47.2 | 0.1 | 64.5 | 70.4 | 3.4 | 2028 | 4.2 | 19 | 179 | 52 | 0.8 | 0.6 | 45.8 | 44.8 | 47.7 | 199 | 80 | 2000 | 22.3 | 23 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.3 | 27.9 | 46.25 | 2.9 | 1008.0879 | 4090.7812 | 5561.0346 | 2028 | 2.7421 | 3.9725 | 0.5 | 1.4 | 0.6 |  |  | 8.8712 | 24.0313 | 27.4213 | 28.3344
46023.4428 | 25.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 31 | 31 | 31 | 2843.9 | 715.9 | 47.2 | 0.1 | 65.5 | 71.8 | 3.4 | 2134 | 4.3 | 18 | 179 | 52 | 0.7 | 0.6 | 45.8 | 44.8 | 47.7 | 199 | 80 | 2000 | 22 | 22.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.2 | 27.9 | 46.25 | 2.9 | 1008.0879 | 4090.7812 | 5561.0346 | 2134 | 2.6059 | 3.9725 | 0.5 | 1.4 | 0.5 |  |  | 8.889 | 24.0776 | 26.0592 | 27.6121
46023.4431 | 26 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 31 | 29 | 31 | 2863.5 | 715.9 | 47.6 | 0.1 | 66.7 | 73.8 | 3.4 | 2134 | 4.3 | 19 | 179 | 52 | 0.6 | 0.5 | 46.1 | 45 | 48 | 199 | 80 | 2000 | 21.2 | 21.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.2 | 27.7 | 46.5 | 3 | 1007.9558 | 4091.0125 | 5711.1303 | 2134 | 2.6763 | 3.9999 | 0.4 | 1.5 | 0.2 |  |  | 8.9068 | 24.1252 | 26.7626 | 27.1573
46023.4435 | 26.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 29 | 29 | 2853.7 | 715.9 | 47.4 | 0.1 | 67 | 74.7 | 3.4 | 2190 | 4.1 | 18 | 179 | 52 | 0.6 | 0.5 | 46.1 | 44.8 | 47.8 | 199 | 80 | 2000 | 21.2 | 21.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.2 | 27.5 | 46.3 | 3 | 1008.0615 | 4090.8275 | 5670.2328 | 2190 | 2.5891 | 3.9862 | 0.4 | 1.3 | 0.4 |  |  | 8.9251 | 24.1725 | 25.8915 | 26.9005
46023.4438 | 27 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 30 | 29 | 2843.9 | 715.9 | 47.2 | 0.1 | 66.8 | 74.8 | 3.5 | 2190 | 4.1 | 18 | 179 | 52 | 0.8 | 0.7 | 46.1 | 45 | 47.8 | 199 | 80 | 2000 | 22.4 | 23 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.2 | 27.5 | 46.4 | 2.8 | 1008.0087 | 4090.92 | 5292.0596 | 2190 | 2.4165 | 3.9725 | 0.6 | 1.1 | 0.4 |  |  | 8.9433 | 24.2166 | 24.1647 | 26.0598
46023.4442 | 27.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 30 | 30 | 2863.5 | 715.9 | 47.5 | 0.1 | 67.1 | 74.8 | 3.5 | 2100 | 4.2 | 19 | 179 | 53 | 0.8 | 0.7 | 46.1 | 45.1 | 48 | 199 | 80 | 2000 | 22.3 | 23 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.2 | 27.9 | 46.55 | 2.9 | 1007.9293 | 4091.0588 | 5560.5373 | 2100 | 2.6479 | 3.9999 | 0.6 | 1.4 | 0.2 |  |  | 8.9608 | 24.2629 | 26.4787 | 25.8713
46023.4445 | 28 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 28 | 30 | 2863.5 | 715.9 | 47.5 | 0.1 | 67.5 | 75.1 | 3.5 | 2100 | 4.2 | 19 | 179 | 53 | 0.8 | 0.7 | 46.1 | 45 | 48 | 198 | 80 | 2000 | 22.3 | 23 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.2 | 27.9 | 46.5 | 3 | 1007.9558 | 4091.0125 | 5752.3659 | 2100 | 2.7392 | 3.9999 | 0.6 | 1.4 | 0.2 |  |  | 8.9783 | 24.3108 | 27.3922 | 26.1379
46023.4448 | 28.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2843.9 | 715.9 | 47.2 | 0.1 | 68.2 | 75.8 | 3.5 | 2150 | 4 | 19 | 181 | 53 | 0.7 | 0.6 | 46.1 | 45.1 | 48 | 198 | 80 | 2000 | 22.7 | 23.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.2 | 27.7 | 46.55 | 2.9 | 1007.9293 | 4091.0588 | 5520.6768 | 2150 | 2.5678 | 3.9725 | 0.5 | 1.1 | 0.2 |  |  | 8.9962 | 24.3568 | 25.6776 | 25.9209
46023.4452 | 29 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 30 | 28 | 2843.9 | 725.7 | 47.2 | 0.5 | 68.5 | 76.4 | 3.5 | 2150 | 4 | 19 | 181 | 53 | 0.9 | 0.8 | 46.1 | 45.1 | 47.8 | 197 | 80 | 2000 | 24.2 | 27.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.2 | 27.7 | 46.45 | 2.7 | 1007.9822 | 4090.9662 | 5140.094 | 2150 | 2.3907 | 3.9188 | 0.3 | 1.1 | 0.4 |  |  | 9.0141 | 24.3997 | 23.9074 | 25.5241
46023.4455 | 29.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 30 | 30 | 2863.5 | 715.9 | 47.5 | 0.1 | 69.2 | 77 | 3.4 | 2066 | 4.3 | 19 | 181 | 54 | 0.9 | 0.8 | 46 | 45.3 | 47.8 | 197 | 86 | 2000 | 24.4 | 33.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.2 | 27.7 | 46.55 | 2.5 | 1007.9293 | 4091.0588 | 4759.2041 | 2066 | 2.3036 | 3.9999 | 0.7 | 1.5 | 0.4 |  |  | 9.0314 | 24.4393 | 23.0358 | 25.2984
46023.4459 | 30 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 28 | 30 | 2873.3 | 715.9 | 47.6 | 0.1 | 70.1 | 78 | 3.5 | 2066 | 4.3 | 19 | 181 | 54 | 0.9 | 0.8 | 46.1 | 45.3 | 48 | 197 | 96 | 2000 | 23.8 | 34.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.2 | 27.7 | 46.65 | 2.7 | 1007.8764 | 4091.1512 | 5139.7866 | 2066 | 2.4878 | 4.0135 | 0.7 | 1.5 | 0.2 |  |  | 9.0486 | 24.4822 | 24.878 | 24.9782
46023.4462 | 30.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2863.5 | 715.9 | 47.5 | 0.1 | 70.5 | 78.7 | 3.5 | 2165 | 4.1 | 19 | 179 | 55 | 0.9 | 0.8 | 46.3 | 45.3 | 48.3 | 197 | 94 | 2000 | 24.7 | 31.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.2 | 27.7 | 46.8 | 3 | 1007.7968 | 4091.29 | 5710.617 | 2165 | 2.6377 | 3.9999 | 0.7 | 1.2 | -0.1 |  |  | 9.0666 | 24.5298 | 26.377 | 24.7752
46023.4466 | 31 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 26 | 28 | 2863.5 | 725.7 | 47.5 | 0.5 | 70.8 | 79.1 | 3.5 | 2165 | 4.1 | 19 | 179 | 55 | 0.9 | 0.8 | 46.3 | 45.5 | 48.3 | 196 | 94 | 2000 | 25.6 | 31.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.2 | 27.7 | 46.9 | 2.8 | 1007.7438 | 4091.3825 | 5329.7489 | 2165 | 2.4618 | 3.9458 | 0.3 | 1.2 | -0.1 |  |  | 9.0847 | 24.5742 | 24.6178 | 24.5632
46023.4469 | 31.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2834.1 | 725.7 | 47.1 | 0.5 | 71 | 79.3 | 3.5 | 2088 | 3.8 | 19 | 179 | 55 | 1.2 | 1.1 | 46.3 | 45.5 | 48 | 196 | 97 | 2000 | 26.6 | 35.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.2 | 27.7 | 46.75 | 2.5 | 1007.8234 | 4091.2438 | 4758.919 | 2088 | 2.2792 | 3.9053 | 0.6 | 0.8 | 0.2 |  |  | 9.1021 | 24.6138 | 22.7918 | 24.3401
46023.4473 | 32 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 26 | 32 | 26 | 2834.1 | 735.5 | 47.1 | 0.9 | 71.1 | 79.2 | 3.5 | 2088 | 3.8 | 19 | 179 | 56 | 1.3 | 1.2 | 46 | 45.5 | 47.8 | 197 | 102 | 2000 | 28 | 38.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.2 | 28.1 | 46.65 | 2.3 | 1007.8764 | 4091.1512 | 4441.5618 | 2088 | 2.1272 | 3.8533 | 0.3 | 1.1 | 0.4 |  |  | 9.1195 | 24.6508 | 21.2718 | 23.9873
46023.4476 | 32.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 32 | 28 | 2853.7 | 725.7 | 47.4 | 0.5 | 71 | 79 | 3.5 | 1979 | 4.1 | 19 | 179 | 57 | 1.3 | 1.3 | 46 | 45.5 | 47.8 | 196 | 111 | 2000 | 27.2 | 41.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.2 | 28.1 | 46.65 | 2.3 | 1007.8764 | 4091.1512 | 4441.5618 | 1979 | 2.2443 | 3.9323 | 0.8 | 1.4 | 0.4 |  |  | 9.1359 | 24.6879 | 22.4435 | 23.5004
46023.448 | 33 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 30 | 30 | 2873.3 | 725.7 | 47.6 | 0.5 | 71 | 79 | 3.5 | 1979 | 4.3 | 19 | 179 | 58 | 1.2 | 1.1 | 46.1 | 45.6 | 48.3 | 196 | 111 | 2000 | 26.4 | 42.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.2 | 27.9 | 46.95 | 2.7 | 1007.7172 | 4091.4288 | 5176.4303 | 1979 | 2.6157 | 3.9593 | 0.6 | 1.5 | -0.1 |  |  | 9.1524 | 24.731 | 26.1568 | 23.4563
46023.4483 | 33.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 30 | 30 | 2883.1 | 725.7 | 47.8 | 0.5 | 71.2 | 79.2 | 3.5 | 2131 | 4.4 | 19 | 179 | 58 | 1 | 1 | 46.5 | 45.6 | 48.6 | 196 | 121 | 2000 | 25.5 | 41.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.2 | 27.9 | 47.1 | 3 | 1007.6374 | 4091.5675 | 5751.3289 | 2131 | 2.6989 | 3.9729 | 0.5 | 1.3 | -0.4 |  |  | 9.1702 | 24.7789 | 26.9889 | 23.9305
46023.4487 | 34 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 25 | 30 | 2902.8 | 725.7 | 48.1 | 0.5 | 71.5 | 79.7 | 3.6 | 2131 | 4.4 | 19 | 179 | 58 | 1 | 0.9 | 46.5 | 45.6 | 49 | 196 | 121 | 2000 | 25.6 | 35.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.1 | 28.1 | 47.3 | 3.4 | 1007.5308 | 4091.7525 | 6564.5004 | 2131 | 3.0805 | 4 | 0.4 | 1.6 | -0.9 |  |  | 9.188 | 24.8336 | 30.8048 | 25.5332
46023.449 | 34.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 25 | 28 | 2883.1 | 725.7 | 47.8 | 0.5 | 71.4 | 79.8 | 3.6 | 2219 | 4.1 | 19 | 179 | 58 | 1 | 1 | 46.6 | 45.6 | 49 | 196 | 121 | 2000 | 25.7 | 28.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.1 | 28.1 | 47.3 | 3.4 | 1007.5308 | 4091.7525 | 6564.5004 | 2219 | 2.9583 | 3.9729 | 0.5 | 1.2 | -0.9 |  |  | 9.2064 | 24.8883 | 29.5831 | 27.1954
46023.4494 | 35 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2863.5 | 735.5 | 47.5 | 0.9 | 70.5 | 79.1 | 3.6 | 2219 | 3.9 | 20 | 179 | 58 | 1.2 | 1.2 | 46.6 | 45.6 | 48.6 | 196 | 121 | 2000 | 27.2 | 28.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.1 | 27.5 | 47.1 | 3 | 1007.6374 | 4091.5675 | 5668.8726 | 2219 | 2.5547 | 3.8933 | 0.3 | 0.9 | -0.5 |  |  | 9.2249 | 24.9356 | 25.547 | 27.8161
46023.4497 | 35.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2863.5 | 735.5 | 47.5 | 0.9 | 70.2 | 78.4 | 3.6 | 2064 | 3.9 | 20 | 183 | 58 | 1.3 | 1.2 | 46.3 | 45.6 | 48.3 | 196 | 121 | 2000 | 28.3 | 31 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.1 | 28.1 | 46.95 | 2.7 | 1007.7172 | 4091.4288 | 5213.5374 | 2064 | 2.5259 | 3.8933 | 0.3 | 1.2 | -0.2 |  |  | 9.2421 | 24.979 | 25.2594 | 27.6366
46023.4501 | 36 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 26 | 32 | 26 | 2853.7 | 735.5 | 47.4 | 0.9 | 70.2 | 77.5 | 3.6 | 2064 | 3.9 | 20 | 183 | 58 | 1.5 | 1.4 | 46.3 | 45.8 | 48 | 196 | 129 | 2000 | 29.1 | 37.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.1 | 27.7 | 46.9 | 2.2 | 1007.7438 | 4091.3825 | 4187.6598 | 2064 | 2.0289 | 3.8799 | 0.5 | 1.1 | 0.1 |  |  | 9.2593 | 25.0139 | 20.289 | 26.2967
46023.4504 | 36.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 32 | 28 | 2863.5 | 735.5 | 47.5 | 0.9 | 70.2 | 77.2 | 3.6 | 2002 | 4.1 | 20 | 183 | 59 | 1.5 | 1.4 | 46.1 | 45.8 | 48 | 196 | 138 | 2000 | 28.7 | 40.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.1 | 27.7 | 46.9 | 2.2 | 1007.7438 | 4091.3825 | 4187.6598 | 2002 | 2.0917 | 3.8933 | 0.5 | 1.4 | 0.1 |  |  | 9.276 | 25.0488 | 20.9174 | 24.3192
46023.4507 | 37 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 30 | 30 | 2892.9 | 725.7 | 47.9 | 0.5 | 70.8 | 77.7 | 3.6 | 2002 | 4.4 | 19 | 183 | 60 | 1.3 | 1.2 | 46.3 | 45.8 | 48.6 | 196 | 138 | 2000 | 27.1 | 41.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.1 | 27.9 | 47.2 | 2.8 | 1007.5841 | 4091.66 | 5367.7446 | 2002 | 2.6812 | 3.9864 | 0.7 | 1.6 | -0.5 |  |  | 9.2927 | 25.0935 | 26.8119 | 23.7649
46023.4511 | 37.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 30 | 30 | 2902.8 | 725.7 | 48.1 | 0.5 | 71.2 | 78.2 | 3.6 | 2002 | 4.4 | 20 | 183 | 60 | 1.3 | 1.2 | 46.5 | 45.8 | 48.6 | 196 | 147 | 2000 | 26.5 | 40.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.1 | 27.7 | 47.2 | 2.8 | 1007.5841 | 4091.66 | 5329.2661 | 2002 | 2.662 | 4 | 0.7 | 1.6 | -0.5 |  |  | 9.3094 | 25.1379 | 26.6197 | 23.9795
46023.4514 | 38 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 25 | 30 | 2912.6 | 725.7 | 48.1 | 0.5 | 71.7 | 79.1 | 3.7 | 2151 | 4.4 | 20 | 183 | 60 | 1.1 | 1.1 | 46.6 | 45.8 | 49.2 | 196 | 147 | 2000 | 26.7 | 35.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48 | 28.1 | 47.5 | 3.4 | 1007.424 | 4091.9375 | 6564.1012 | 2151 | 3.0517 | 4.0135 | 0.6 | 1.5 | -1.2 |  |  | 9.3273 | 25.1926 | 30.5165 | 25.0309
46023.4518 | 38.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 25 | 28 | 2902.8 | 725.7 | 48.1 | 0.5 | 71.8 | 79.3 | 3.6 | 2151 | 4.2 | 20 | 183 | 60 | 1.2 | 1.1 | 46.8 | 46 | 49.2 | 196 | 147 | 2000 | 26.7 | 29 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48 | 28.1 | 47.6 | 3.2 | 1007.3705 | 4092.03 | 6177.7893 | 2151 | 2.8721 | 4 | 0.6 | 1.3 | -1.2 |  |  | 9.3452 | 25.2441 | 28.7205 | 26.7172
46023.4521 | 39 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 26 | 25 | 26 | 2873.3 | 735.5 | 47.6 | 0.9 | 71 | 78.8 | 3.7 | 2248 | 4 | 20 | 183 | 59 | 1.4 | 1.3 | 46.8 | 46 | 49 | 196 | 147 | 2000 | 28.2 | 29.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48 | 27.7 | 47.5 | 3 | 1007.424 | 4091.9375 | 5709.4077 | 2248 | 2.5398 | 3.9066 | 0.4 | 0.8 | -1 |  |  | 9.364 | 25.2917 | 25.3977 | 27.6133
46023.4525 | 39.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2863.5 | 735.5 | 47.5 | 0.9 | 70.4 | 77.7 | 3.6 | 2248 | 3.9 | 20 | 183 | 60 | 1.6 | 1.5 | 46.5 | 46 | 48.6 | 196 | 147 | 2000 | 30.5 | 34.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.1 | 27.7 | 47.3 | 2.6 | 1007.5308 | 4091.7525 | 4948.4542 | 2248 | 2.2013 | 3.8933 | 0.6 | 1 | -0.5 |  |  | 9.3827 | 25.3329 | 22.0127 | 26.6534
46023.4528 | 40 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 31 | 25 | 2863.5 | 745.3 | 47.5 | 1.3 | 70.2 | 77.2 | 3.6 | 2087 | 3.8 | 20 | 181 | 60 | 1.7 | 1.6 | 46.3 | 46.1 | 48.3 | 195 | 155 | 2000 | 30.7 | 38.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.1 | 27.7 | 47.2 | 2.2 | 1007.5841 | 4091.66 | 4187.2805 | 2087 | 2.0064 | 3.8421 | 0.3 | 1.2 | -0.2 |  |  | 9.4001 | 25.3678 | 20.0636 | 25.3422
46023.4532 | 40.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 31 | 27 | 2863.5 | 745.3 | 47.5 | 1.3 | 70.4 | 77 | 3.6 | 2087 | 4 | 20 | 181 | 62 | 1.8 | 1.7 | 46.3 | 46 | 48.3 | 194 | 165 | 2000 | 30.2 | 42.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.1 | 27.7 | 47.15 | 2.3 | 1007.6108 | 4091.6137 | 4377.6777 | 2087 | 2.0976 | 3.8421 | 0.4 | 1.2 | -0.2 |  |  | 9.4175 | 25.4043 | 20.9759 | 23.4341
46023.4535 | 41 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2892.9 | 735.5 | 47.9 | 0.9 | 70.8 | 77.4 | 3.7 | 1961 | 4.1 | 20 | 181 | 63 | 1.7 | 1.6 | 46.5 | 46.1 | 49 | 194 | 165 | 2000 | 29.3 | 42.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48.1 | 27.7 | 47.55 | 2.9 | 1007.3973 | 4091.9837 | 5519.01 | 1961 | 2.8144 | 3.9332 | 0.7 | 1.4 | -0.9 |  |  | 9.4338 | 25.4503 | 28.1439 | 23.3188
46023.4539 | 41.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2892.9 | 735.5 | 47.9 | 0.9 | 71.1 | 78 | 3.7 | 1961 | 4.1 | 20 | 181 | 63 | 1.6 | 1.6 | 46.5 | 46.1 | 49 | 194 | 171 | 2000 | 30 | 41.6 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48 | 28.1 | 47.55 | 2.9 | 1007.3973 | 4091.9837 | 5598.7069 | 1961 | 2.855 | 3.9332 | 0.7 | 1.4 | -1 |  |  | 9.4502 | 25.497 | 28.5503 | 23.9493
46023.4542 | 42 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 25 | 27 | 2892.9 | 735.5 | 47.9 | 0.9 | 71.4 | 78.4 | 3.7 | 2076 | 4.1 | 20 | 183 | 63 | 1.7 | 1.6 | 46.6 | 46.3 | 49 | 194 | 173 | 2000 | 30.2 | 40.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48 | 28.1 | 47.65 | 2.7 | 1007.3437 | 4092.0763 | 5212.4301 | 2076 | 2.5108 | 3.9332 | 0.7 | 1.3 | -1 |  |  | 9.4675 | 25.5404 | 25.108 | 24.5683
46023.4546 | 42.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2873.3 | 745.3 | 47.6 | 1.3 | 71.4 | 78.5 | 3.7 | 2076 | 3.8 | 20 | 183 | 63 | 1.7 | 1.6 | 46.6 | 46.1 | 49 | 194 | 175 | 2000 | 30.6 | 40.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48 | 27.7 | 47.55 | 2.9 | 1007.3973 | 4091.9837 | 5519.01 | 2076 | 2.6585 | 3.8552 | 0.3 | 1 | -1 |  |  | 9.4848 | 25.5864 | 26.5848 | 25.8726
46023.4549 | 43 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 26 | 25 | 2863.5 | 745.3 | 47.5 | 1.3 | 71.4 | 78.5 | 3.7 | 2087 | 3.8 | 20 | 183 | 63 | 1.9 | 1.8 | 46.5 | 46.1 | 48.6 | 194 | 175 | 2000 | 31.7 | 40.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48 | 27.9 | 47.35 | 2.5 | 1007.5041 | 4091.7987 | 4792.411 | 2087 | 2.2963 | 3.8421 | 0.5 | 1 | -0.6 |  |  | 9.5022 | 25.6263 | 22.9632 | 26.27
46023.4553 | 43.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2873.3 | 745.3 | 47.6 | 1.3 | 71.2 | 78.2 | 3.7 | 1978 | 3.9 | 20 | 183 | 64 | 1.9 | 1.8 | 46.5 | 46.1 | 48.3 | 194 | 178 | 2000 | 31.1 | 41.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48 | 27.7 | 47.2 | 2.2 | 1007.5841 | 4091.66 | 4187.2805 | 1978 | 2.1169 | 3.8552 | 0.5 | 1.1 | -0.3 |  |  | 9.5186 | 25.6612 | 21.1693 | 24.8751
46023.4556 | 44 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 26 | 25 | 26 | 2873.3 | 745.3 | 47.6 | 1.3 | 71.2 | 78.1 | 3.8 | 1978 | 4 | 20 | 183 | 64 | 1.9 | 1.8 | 46.5 | 46.1 | 48.6 | 194 | 180 | 2000 | 31 | 41.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48 | 27.7 | 47.35 | 2.5 | 1007.5041 | 4091.7987 | 4758.0568 | 1978 | 2.4055 | 3.8552 | 0.5 | 1.1 | -0.6 |  |  | 9.5351 | 25.7009 | 24.0549 | 23.976
46023.456 | 44.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2873.3 | 745.3 | 47.6 | 1.3 | 71.2 | 78.1 | 3.8 | 2014 | 3.8 | 20 | 180 | 64 | 1.9 | 1.9 | 46.5 | 46.1 | 48.6 | 193 | 176 | 2000 | 31.7 | 41.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48 | 27.5 | 47.35 | 2.5 | 1007.5041 | 4091.7987 | 4723.7026 | 2014 | 2.3454 | 3.8552 | 0.6 | 1.1 | -0.6 |  |  | 9.5519 | 25.7402 | 23.4543 | 23.6453
46023.4563 | 45 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2863.5 | 745.3 | 47.5 | 1.3 | 71.1 | 78.1 | 3.8 | 2014 | 3.8 | 20 | 180 | 64 | 2 | 1.9 | 46.5 | 46.1 | 48.6 | 192 | 176 | 2000 | 31.7 | 41.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48 | 27.9 | 47.35 | 2.5 | 1007.5041 | 4091.7987 | 4792.411 | 2014 | 2.3795 | 3.8421 | 0.6 | 1 | -0.6 |  |  | 9.5687 | 25.7802 | 23.7955 | 23.0874
46023.4567 | 45.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2863.5 | 745.3 | 47.5 | 1.3 | 71 | 78 | 3.8 | 1956 | 3.8 | 20 | 180 | 64 | 2 | 1.9 | 46.5 | 46.1 | 48.6 | 191 | 176 | 2000 | 31.7 | 41.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48 | 27.9 | 47.35 | 2.5 | 1007.5041 | 4091.7987 | 4792.411 | 1956 | 2.4501 | 3.8421 | 0.6 | 1 | -0.6 |  |  | 9.585 | 25.8201 | 24.5011 | 23.395
46023.457 | 46 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2873.3 | 745.3 | 47.6 | 1.3 | 71 | 78 | 3.8 | 1956 | 3.8 | 20 | 180 | 64 | 2 | 2 | 46.5 | 46.3 | 48.6 | 191 | 176 | 2000 | 31.8 | 41.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48 | 27.9 | 47.45 | 2.3 | 1007.4507 | 4091.8913 | 4408.8841 | 1956 | 2.254 | 3.8552 | 0.7 | 1.1 | -0.6 |  |  | 9.6013 | 25.8569 | 22.5403 | 23.6692
46023.4573 | 46.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2863.5 | 755.1 | 47.5 | 1.6 | 71 | 77.8 | 3.8 | 1957 | 3.8 | 20 | 179 | 64 | 2 | 2 | 46.5 | 46.1 | 48.6 | 191 | 176 | 2000 | 31.8 | 41.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 48 | 27.9 | 47.35 | 2.5 | 1007.5041 | 4091.7987 | 4792.411 | 1957 | 2.4489 | 3.7922 | 0.4 | 1 | -0.6 |  |  | 9.6176 | 25.8968 | 24.4886 | 23.756
46023.4577 | 47 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2873.3 | 745.3 | 47.6 | 1.3 | 71 | 77.8 | 3.9 | 1957 | 3.1 | 20 | 179 | 64 | 2 | 2 | 46.5 | 46.3 | 48.6 | 190 | 0 | 0 | 31.1 | 41.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.9 | 27.7 | 47.45 | 2.3 | 1007.4507 | 4091.8913 | 4377.2792 | 1957 | 2.2367 | 3.8552 | 0.7 | 1.1 | -0.7 |  |  | 9.6339 | 25.9333 | 22.3673 | 23.5385
46023.458 | 47.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2873.3 | 745.3 | 47.6 | 1.3 | 71 | 78 | 3.9 | 1858 | 3.1 | 16 | 179 | 63 | 2 | 2 | 46.3 | 46.1 | 48.3 | 190 | 0 | 0 | 27.7 | 41.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.9 | 27.9 | 47.2 | 2.2 | 1007.5841 | 4091.66 | 4217.5136 | 1858 | 2.2699 | 3.8552 | 0.7 | 1.3 | -0.4 |  |  | 9.6494 | 25.9684 | 22.6992 | 23.3193
46023.4584 | 48 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 27 | 25 | 2873.3 | 745.3 | 47.6 | 1.3 | 70.4 | 78.2 | 3.9 | 1858 | 3.1 | 16 | 179 | 63 | 2 | 1.9 | 46 | 46.1 | 48.3 | 190 | 0 | 0 | 22.7 | 40 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.9 | 27.9 | 47.2 | 2.2 | 1007.5841 | 4091.66 | 4217.5136 | 1858 | 2.2699 | 3.8552 | 0.6 | 1.6 | -0.4 |  |  | 9.6649 | 26.0036 | 22.6992 | 22.9589
46023.4587 | 48.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2902.8 | 745.3 | 47.9 | 1.3 | 69.8 | 78.4 | 3.9 | 1610 | 3.3 | 16 | 179 | 62 | 2 | 1.9 | 46 | 46.1 | 48.3 | 190 | 0 | 0 | 19.9 | 38.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.9 | 27.9 | 47.2 | 2.2 | 1007.5841 | 4091.66 | 4217.5136 | 1610 | 2.6196 | 3.8948 | 0.6 | 1.9 | -0.4 |  |  | 9.6783 | 26.0387 | 26.1957 | 23.69
46023.4591 | 49 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 27 | 23 | 27 | 2912.6 | 745.3 | 48.2 | 1.3 | 69.5 | 78.5 | 3.9 | 1610 | 3.3 | 16 | 181 | 63 | 1.9 | 1.8 | 45.8 | 46.1 | 48.6 | 190 | 0 | 0 | 19 | 37.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.9 | 27.7 | 47.35 | 2.5 | 1007.5041 | 4091.7987 | 4758.0568 | 1610 | 2.9553 | 3.908 | 0.5 | 2.4 | -0.7 |  |  | 9.6917 | 26.0784 | 29.5531 | 24.7029
46023.4594 | 49.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 23 | 25 | 2912.6 | 745.3 | 48.2 | 1.3 | 69.4 | 78.7 | 3.9 | 1704 | 3.2 | 16 | 181 | 63 | 1.9 | 1.8 | 45.3 | 46.3 | 49 | 190 | 0 | 0 | 18.9 | 36.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.9 | 27.5 | 47.65 | 2.7 | 1007.3437 | 4092.0763 | 5101.1327 | 1704 | 2.9936 | 3.908 | 0.5 | 2.9 | -1.1 |  |  | 9.7059 | 26.1209 | 29.9362 | 26.2167
46023.4598 | 50 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 23 | 22 | 23 | 2892.9 | 745.3 | 47.9 | 1.3 | 69.2 | 78.7 | 3.9 | 1704 | 2.9 | 16 | 181 | 63 | 1.9 | 1.9 | 44.6 | 46.3 | 48.6 | 190 | 0 | 0 | 19.2 | 34.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.9 | 27.5 | 47.45 | 2.3 | 1007.4507 | 4091.8913 | 4345.6743 | 1704 | 2.5503 | 3.8815 | 0.6 | 3.3 | -0.7 |  |  | 9.7201 | 26.1571 | 25.5028 | 26.7774
46023.4601 | 50.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 22 | 22 | 22 | 2873.3 | 755.1 | 47.6 | 1.6 | 69 | 78.7 | 3.9 | 1570 | 2.8 | 16 | 181 | 62 | 2 | 2 | 44.4 | 46.3 | 48.3 | 189 | 0 | 0 | 20 | 33.3 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.9 | 28.1 | 47.3 | 2 | 1007.5308 | 4091.7525 | 3861.4708 | 1570 | 2.4595 | 3.8052 | 0.4 | 3.2 | -0.4 |  |  | 9.7332 | 26.1893 | 24.5954 | 27.1566
46023.4605 | 51 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 22 | 23 | 22 | 2863.5 | 755.1 | 47.5 | 1.6 | 69 | 78.7 | 4 | 1570 | 2.8 | 16 | 182 | 62 | 2.2 | 2.2 | 44.4 | 46.3 | 48.3 | 188 | 0 | 0 | 20.8 | 32.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.8 | 27.9 | 47.3 | 2 | 1007.5308 | 4091.7525 | 3833.987 | 1570 | 2.442 | 3.7922 | 0.6 | 3.1 | -0.5 |  |  | 9.7463 | 26.2212 | 24.4203 | 26.8016
46023.4608 | 51.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 23 | 23 | 23 | 2873.3 | 755.1 | 47.6 | 1.6 | 69 | 78.7 | 4 | 1465 | 2.9 | 16 | 182 | 62 | 2.2 | 2.2 | 44.6 | 46.3 | 48.3 | 187 | 0 | 0 | 21.7 | 31.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.8 | 27.9 | 47.3 | 2 | 1007.5308 | 4091.7525 | 3833.987 | 1465 | 2.6171 | 3.8052 | 0.6 | 3 | -0.5 |  |  | 9.7585 | 26.2532 | 26.1706 | 26.125
46023.4612 | 0 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Stop | Heat | 0 | 0 | 0 | 0 | 2873.3 | 755.1 | 47.6 | 1.6 | 69.1 | 78.7 | 4 | 1465 | 2.9 | 16 | 182 | 62 | 2.2 | 2.1 | 45 | 46.3 | 48.3 | 0 | 0 | 0 | 22.3 | 30.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.8 | 27.9 | 47.3 | 2 | 1007.5308 | 4091.7525 | 3833.987 | 1465 | 2.6171 | 3.8052 | 0.5 | 2.6 | -0.5 |  |  | 9.7707 | 26.2851 | 26.1706 | 25.3719
46023.4615 | 0.5 | EHS MONO LOWTEMP | On | Off | On | Off | On | Stop | Heat | 0 | 0 | 0 | 0 | 2775.3 | 804.1 | 46.2 | 3.4 | 68.4 | 78.4 | 4 | 1129 | 0 | 0 | 182 | 57 | 3.2 | 3.2 | 44.6 | 47 | 47.2 | 0 | 0 | 0 | 23 | 29.8 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.8 | 28.1 | 47.1 | 0.2 | 1007.6374 | 4091.5675 | 386.1705 | 1129 | 0.34205 | 3.4514 | -0.2 | 1.6 | 0.6 |  |  | 9.7801 | 26.2883
46023.4619 | 1 | EHS MONO LOWTEMP | On | Off | On | Off | On | Stop | Heat | 0 | 0 | 0 | 0 | 1451.4 | 872.8 | 23 | 5.8 | 65.8 | 77.1 | 4 | 1129 | 0 | 0 | 182 | 53 | 5.5 | 6.1 | 38.8 | 47.1 | 47 | 0 | 0 | 0 | 23.5 | 29 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.8 | 27.7 | 47.05 | -0.1 | 1007.664 | 4091.5212 | -190.3396 | 1129 | -0.16859 | 1.6629 | 0.3 | -15.8 | 0.8 |  |  | 9.7895 | 26.2867
46023.4622 | 1.5 | EHS MONO LOWTEMP | Off | Off | On | Off | On | Stop | Heat | 0 | 0 | 0 | 0 | 892.4 | 912 | 6.4 | 7 | 62.4 | 75.2 | 4 | 201 | 0 | 0 | 168 | 52 | 6.3 | 7.9 | 30.7 | 46.1 | 47 | 0 | 0 | 0 | 23.8 | 28.2 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.8 | 27.7 | 46.55 | 0.9 | 1007.9293 | 4091.0588 | 1713.3135 | 201 | 8.5239 | 0.97851 | 0.9 | -24.3 | 0.8 |  |  | 9.7912 | 26.301
46023.4626 | 2 | EHS MONO LOWTEMP | Off | Off | On | Off | On | Stop | Heat | 0 | 0 | 0 | 0 | 863 | 892.4 | 5.4 | 6.4 | 60 | 73.1 | 4.1 | 201 | 0 | 0 | 168 | 51 | 6.5 | 8.7 | 27.5 | 42.5 | 47.1 | 0 | 0 | 0 | 23.7 | 27.3 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.8 | 0 | 44.8 | 4.6 | 1008.847 | 4089.44 | 0 | 201 | 0 | 0.96706 | 2.3 | -22.1 | 0.7 |  |  | 9.7929 | 26.301
46023.4629 | 2.5 | EHS MONO LOWTEMP | Off | Off | On | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 853.2 | 892.4 | 5.1 | 6.4 | 59 | 71.8 | 4.1 | 125 | 0 | 0 | 168 | 51 | 6.4 | 9 | 26.4 | 41.8 | 47.1 | 0 | 0 | 0 | 23.2 | 26.8 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.7 | 0 | 44.45 | 5.3 | 1009.0285 | 4089.1163 | 0 | 125 | 0 | 0.95607 | 2.6 | -21.3 | 0.6 |  |  | 9.7939 | 26.301
46023.4632 | 3 | EHS MONO LOWTEMP | Off | Off | On | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 853.2 | 892.4 | 5.1 | 6.4 | 57.6 | 70.1 | 4.2 | 125 | 0 | 0 | 168 | 50 | 6.3 | 9.5 | 25.3 | 41.1 | 47.1 | 0 | 0 | 0 | 21.6 | 26.1 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.7 | 0 | 44.1 | 6 | 1009.2093 | 4088.7925 | 0 | 125 | 0 | 0.95607 | 3.1 | -20.2 | 0.6 |  |  | 9.7949 | 26.301
46023.4636 | 3.5 | EHS MONO LOWTEMP | Off | Off | On | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 843.4 | 882.6 | 4.8 | 6.1 | 56.5 | 68.4 | 4.4 | 125 | 0 | 0 | 167 | 50 | 6.2 | 10 | 24.3 | 40.8 | 47.1 | 0 | 0 | 0 | 20 | 25.2 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.7 | 0 | 43.95 | 6.3 | 1009.2865 | 4088.6537 | 0 | 125 | 0 | 0.95559 | 3.9 | -19.5 | 0.6 |  |  | 9.796 | 26.301
46023.4639 | 4 | EHS MONO LOWTEMP | Off | Off | On | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 843.4 | 882.6 | 4.8 | 6.1 | 55.6 | 67.2 | 4.4 | 125 | 0 | 0 | 167 | 49 | 6.2 | 10.5 | 23.5 | 40.6 | 47.1 | 0 | 0 | 0 | 18.5 | 24.4 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.5 | 0 | 43.85 | 6.5 | 1009.338 | 4088.5613 | 0 | 125 | 0 | 0.95559 | 4.4 | -18.7 | 0.4 |  |  | 9.797 | 26.301
46023.4643 | 4.5 | EHS MONO LOWTEMP | Off | Off | On | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 843.4 | 882.6 | 4.8 | 6.1 | 54.8 | 66 | 4.6 | 125 | 0 | 0 | 167 | 49 | 6.2 | 10.9 | 22.7 | 41 | 47 | 0 | 0 | 0 | 17.1 | 23.6 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.5 | 0 | 44 | 6 | 1009.2608 | 4088.7 | 0 | 125 | 0 | 0.95559 | 4.8 | -17.9 | 0.5 |  |  | 9.7981 | 26.301
46023.4646 | 5 | EHS MONO LOWTEMP | Off | Off | On | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 843.4 | 882.6 | 4.8 | 6.1 | 54.1 | 65.4 | 4.6 | 125 | 0 | 0 | 167 | 49 | 6.2 | 11.2 | 22.2 | 41.3 | 47 | 2000 | 0 | 0 | 16.3 | 23.2 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.4 | 0 | 44.15 | 5.7 | 1009.1835 | 4088.8387 | 0 | 125 | 0 | 0.95559 | 5.1 | -17.4 | 0.4 |  |  | 9.7991 | 26.301
46023.465 | 5.5 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 863 | 892.4 | 5.4 | 6.4 | 53.4 | 64.5 | 4.7 | 125 | 0 | 0 | 167 | 46 | 6.5 | 11.7 | 21.5 | 41.8 | 46.8 | 2000 | 0 | 0 | 15.3 | 22.5 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.4 | 0 | 44.3 | 5 | 1009.106 | 4088.9775 | 0 | 125 | 0 | 0.96706 | 5.3 | -16.1 | 0.6 |  |  | 9.8002 | 26.301
46023.4653 | 6 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 853.2 | 882.6 | 5.1 | 6.1 | 52.6 | 63.7 | 4.7 | 125 | 0 | 0 | 168 | 45 | 6.4 | 12 | 21 | 42.1 | 46.6 | 2000 | 0 | 0 | 14.4 | 21.8 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.3 | 0 | 44.35 | 4.5 | 1009.0802 | 4089.0237 | 0 | 125 | 0 | 0.96669 | 5.9 | -15.9 | 0.7 |  |  | 9.8012 | 26.301
46023.4657 | 6.5 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 833.6 | 863 | 4.4 | 5.4 | 52 | 63 | 4.7 | 125 | 0 | 0 | 168 | 44 | 6.3 | 12.2 | 20.8 | 42.7 | 46.5 | 2000 | 0 | 0 | 13.7 | 21.2 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.3 | 0 | 44.6 | 3.8 | 1008.9508 | 4089.255 | 0 | 125 | 0 | 0.96593 | 6.8 | -16.4 | 0.8 |  |  | 9.8022 | 26.301
46023.466 | 7 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 833.6 | 863 | 4.4 | 5.4 | 51 | 62.2 | 4.7 | 125 | 0 | 0 | 168 | 44 | 6.1 | 12.5 | 21 | 43.3 | 46.5 | 2000 | 0 | 0 | 13 | 20.5 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.3 | 0 | 44.9 | 3.2 | 1008.795 | 4089.5325 | 0 | 125 | 0 | 0.96593 | 7.1 | -16.6 | 0.8 |  |  | 9.8033 | 26.301
46023.4664 | 7.5 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 823.8 | 853.2 | 4.1 | 5.1 | 50.5 | 62 | 4.7 | 125 | 0 | 0 | 168 | 44 | 6 | 12.6 | 21 | 43.5 | 46.3 | 2000 | 0 | 0 | 12.6 | 20.2 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.3 | 0 | 44.9 | 2.8 | 1008.795 | 4089.5325 | 0 | 125 | 0 | 0.96554 | 7.5 | -16.9 | 1 |  |  | 9.8043 | 26.301
46023.4667 | 8 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 823.8 | 853.2 | 4.1 | 5.1 | 50 | 61.2 | 4.7 | 125 | 0 | 0 | 168 | 43 | 6 | 12.8 | 21 | 44 | 46.1 | 2000 | 0 | 0 | 12.1 | 19.7 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.3 | 0 | 45.05 | 2.1 | 1008.717 | 4089.6712 | 0 | 125 | 0 | 0.96554 | 7.7 | -16.9 | 1.2 |  |  | 9.8054 | 26.301
46023.4671 | 8.5 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 813.9 | 853.2 | 3.7 | 5.1 | 49.3 | 60.8 | 4.7 | 125 | 0 | 0 | 168 | 43 | 5.9 | 13.1 | 20.8 | 44.2 | 46 | 2000 | 0 | 0 | 11.8 | 19.3 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.3 | 0 | 45.1 | 1.8 | 1008.6909 | 4089.7175 | 0 | 125 | 0 | 0.95394 | 8 | -17.1 | 1.3 |  |  | 9.8064 | 26.301
46023.4674 | 9 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 813.9 | 843.4 | 3.7 | 4.8 | 48.8 | 60.3 | 4.7 | 125 | 0 | 0 | 168 | 43 | 5.9 | 13.4 | 20.8 | 44.6 | 45.8 | 2000 | 0 | 0 | 11.3 | 18.8 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.3 | 0 | 45.2 | 1.2 | 1008.6388 | 4089.81 | 0 | 125 | 0 | 0.96502 | 8.6 | -17.1 | 1.5 |  |  | 9.8074 | 26.301
46023.4678 | 9.5 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 813.9 | 843.4 | 3.7 | 4.8 | 48.1 | 59.8 | 4.8 | 125 | 0 | 0 | 168 | 43 | 5.8 | 13.6 | 20.8 | 44.8 | 45.6 | 2000 | 0 | 0 | 11 | 18.5 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.3 | 0 | 45.2 | 0.8 | 1008.6388 | 4089.81 | 0 | 125 | 0 | 0.96502 | 8.8 | -17.1 | 1.7 |  |  | 9.8085 | 26.301
46023.4681 | 0 | EHS MONO LOWTEMP | Off | Off | On | Off | On | Safety Start | Heat | 0 | 20 | 40 | 11 | 813.9 | 843.4 | 3.7 | 4.8 | 47.6 | 59.7 | 4.8 | 125 | 0 | 0 | 168 | 42 | 5.8 | 13.8 | 20.7 | 42.8 | 44.2 | 125 | 0 | 0 | 10.8 | 18.3 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.2 | 0 | 43.5 | 1.4 | 1009.5176 | 4088.2375 | 0 | 125 | 0 | 0.96502 | 9 | -17 | 3 |  |  | 9.8095 | 26.301
46023.4685 | 0.5 | EHS MONO LOWTEMP | On | Off | On | Off | On | Safety Start | Heat | 0 | 40 | 40 | 40 | 1980.9 | 784.5 | 33 | 2.7 | 49.6 | 59.1 | 4.8 | 125 | 3.1 | 12 | 183 | 42 | 6.1 | 8.2 | 26.4 | 43.8 | 44.6 | 125 | 0 | 0 | 10.5 | 17.8 | 520 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.2 | 27.9 | 44.2 | 0.8 | 1009.1577 | 4088.885 | 1534.9947 | 125 | 12.28 | 2.525 | 5.5 | 6.6 | 2.6 |  |  | 9.8106 | 26.3138
46023.4688 | 1 | EHS MONO LOWTEMP | On | Off | On | Off | On | Safety Start | Heat | 0 | 40 | 40 | 40 | 2588.9 | 774.7 | 43.4 | 2.3 | 58.8 | 60.6 | 4.6 | 138 | 4.2 | 14 | 183 | 47 | 3 | 3.3 | 38.2 | 42.8 | 44.4 | 337 | 0 | 700 | 10.4 | 17.6 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.2 | 27.9 | 43.6 | 1.6 | 1009.4664 | 4088.33 | 3070.5115 | 138 | 22.2501 | 3.3418 | 1 | 5.2 | 2.8 |  |  | 9.8117 | 26.3394
46023.4692 | 1.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Safety Start | Heat | 0 | 39 | 25 | 40 | 2569.3 | 774.7 | 43.1 | 2.3 | 63.2 | 64.8 | 4.5 | 138 | 4.6 | 16 | 183 | 52 | 3.2 | 3.3 | 40.6 | 42 | 43.5 | 212 | 150 | 2000 | 13.9 | 24.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.4 | 27.7 | 42.75 | 1.5 | 1009.9002 | 4087.5437 | 2858.6477 | 138 | 20.7148 | 3.3165 | 1 | 2.5 | 3.9 |  |  | 9.8129 | 26.3632
46023.4695 | 2 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Safety Start | Heat | 0 | 25 | 25 | 25 | 2569.3 | 745.3 | 43.1 | 1.3 | 64.4 | 67.2 | 4.5 | 1886 | 3.3 | 17 | 183 | 55 | 2 | 2.2 | 41.8 | 42 | 44.8 | 212 | 157 | 2000 | 17.5 | 34.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.5 | 27.7 | 43.4 | 2.8 | 1009.5688 | 4088.145 | 5335.1761 | 1886 | 2.8288 | 3.4473 | 0.9 | 1.3 | 2.7 |  |  | 9.8286 | 26.4077 | 28.2883
46023.4698 | 2.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Safety Start | Heat | 0 | 25 | 25 | 25 | 2559.5 | 755.1 | 42.9 | 1.6 | 63.5 | 69 | 4.4 | 1886 | 3.3 | 17 | 183 | 57 | 2.1 | 3.8 | 42 | 41.8 | 44.2 | 212 | 157 | 2000 | 26.1 | 38.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.5 | 27.9 | 43 | 2.4 | 1009.773 | 4087.775 | 4606.5409 | 1886 | 2.4425 | 3.3896 | 2.2 | 0.9 | 3.3 |  |  | 9.8443 | 26.4461 | 24.4249
46023.4702 | 3 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Safety Start | Heat | 0 | 25 | 25 | 25 | 2569.3 | 764.9 | 43.1 | 2 | 62.7 | 69 | 4.4 | 1954 | 3.3 | 17 | 180 | 58 | 2.2 | 5 | 42 | 42 | 44.4 | 212 | 158 | 2000 | 26.7 | 39.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.5 | 27.9 | 43.2 | 2.4 | 1009.671 | 4087.96 | 4606.2841 | 1954 | 2.3574 | 3.359 | 3 | 1.1 | 3.1 |  |  | 9.8606 | 26.4845 | 23.5736
46023.4705 | 3.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Safety Start | Heat | 0 | 25 | 25 | 25 | 2588.9 | 764.9 | 43.4 | 2 | 62.1 | 68.7 | 4.4 | 1954 | 3.3 | 17 | 180 | 59 | 2.4 | 4.6 | 42.1 | 42 | 44.4 | 212 | 163 | 2000 | 27.2 | 39.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.5 | 27.7 | 43.2 | 2.4 | 1009.671 | 4087.96 | 4573.2641 | 1954 | 2.3405 | 3.3846 | 2.6 | 1.3 | 3.1 |  |  | 9.8769 | 26.5226 | 23.4046
46023.4709 | 4 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2588.9 | 764.9 | 43.4 | 2 | 62 | 68.5 | 4.4 | 1692 | 3.3 | 17 | 180 | 59 | 2.4 | 2.8 | 42.2 | 42 | 44.4 | 211 | 163 | 2000 | 27.5 | 39.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.5 | 28.1 | 43.2 | 2.4 | 1009.671 | 4087.96 | 4639.304 | 1692 | 2.7419 | 3.3846 | 0.8 | 1.2 | 3.1 |  |  | 9.891 | 26.5612 | 27.4191
46023.4712 | 4.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 20 | 25 | 2598.7 | 764.9 | 43.5 | 2 | 62.1 | 68.5 | 4.4 | 1692 | 3.3 | 17 | 180 | 59 | 2.5 | 2.6 | 42.2 | 42.1 | 44.6 | 210 | 0 | 0 | 27.6 | 39.4 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.5 | 27.7 | 43.35 | 2.5 | 1009.5944 | 4088.0988 | 4763.6169 | 1692 | 2.8154 | 3.3974 | 0.6 | 1.3 | 2.9 |  |  | 9.9051 | 26.6009 | 28.1538
46023.4716 | 5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 23 | 21 | 23 | 2608.6 | 764.9 | 43.7 | 2 | 62.4 | 68.8 | 4.4 | 1700 | 2.7 | 14 | 180 | 59 | 2.5 | 2.5 | 42.4 | 42.1 | 44.6 | 211 | 0 | 0 | 25.4 | 39.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.5 | 27.7 | 43.35 | 2.5 | 1009.5944 | 4088.0988 | 4763.6169 | 1700 | 2.8021 | 3.4104 | 0.5 | 1.3 | 2.9 |  |  | 9.9192 | 26.6406 | 28.0213
46023.4719 | 5.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 21 | 21 | 21 | 2608.6 | 764.9 | 43.7 | 2 | 62.4 | 69.1 | 4.4 | 1512 | 2.6 | 14 | 180 | 58 | 2.6 | 2.5 | 42.2 | 42.2 | 44.6 | 210 | 0 | 0 | 21.5 | 38 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.5 | 27.9 | 43.4 | 2.4 | 1009.5688 | 4088.145 | 4606.0262 | 1512 | 3.0463 | 3.4104 | 0.5 | 1.5 | 2.9 |  |  | 9.9318 | 26.679 | 30.4631
46023.4723 | 6 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 22 | 25 | 22 | 2608.6 | 774.7 | 43.7 | 2.3 | 61.8 | 69.2 | 4.4 | 1512 | 2.6 | 14 | 180 | 58 | 2.7 | 2.7 | 42.2 | 42.2 | 44.6 | 210 | 0 | 0 | 18.5 | 36.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.5 | 28.1 | 43.4 | 2.4 | 1009.5688 | 4088.145 | 4639.0443 | 1512 | 3.0682 | 3.3672 | 0.4 | 1.5 | 2.9 |  |  | 9.9444 | 26.7177 | 30.6815
46023.4726 | 6.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 25 | 24 | 2618.4 | 764.9 | 43.8 | 2 | 61.4 | 69 | 4.4 | 1319 | 2.8 | 14 | 180 | 58 | 2.6 | 2.5 | 42.2 | 42.2 | 44.8 | 208 | 0 | 0 | 17.4 | 35.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.5 | 28.1 | 43.5 | 2.6 | 1009.5176 | 4088.2375 | 5025.4902 | 1319 | 3.8101 | 3.4232 | 0.5 | 1.6 | 2.7 |  |  | 9.9554 | 26.7595 | 38.1008 | 31.0841
46023.473 | 7 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2638 | 764.9 | 44.2 | 2 | 61.1 | 68.7 | 4.5 | 1319 | 2.9 | 15 | 180 | 58 | 2.4 | 2.4 | 42.2 | 42.2 | 45 | 209 | 0 | 0 | 17.3 | 34.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.5 | 28.1 | 43.6 | 2.8 | 1009.4664 | 4088.33 | 5411.9141 | 1319 | 4.103 | 3.4488 | 0.4 | 2 | 2.5 |  |  | 9.9664 | 26.8046 | 41.0304 | 33.6594
46023.4733 | 7.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2638 | 755.1 | 44.2 | 1.6 | 60.8 | 68.5 | 4.5 | 1457 | 2.9 | 15 | 180 | 59 | 2.3 | 2.3 | 42.2 | 42.4 | 45.1 | 208 | 0 | 0 | 17.6 | 33.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.5 | 28.1 | 43.75 | 2.7 | 1009.3894 | 4088.4688 | 5218.4106 | 1457 | 3.5816 | 3.4936 | 0.7 | 2 | 2.4 |  |  | 9.9786 | 26.8481 | 35.8161 | 35.2184
46023.4737 | 8 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2657.6 | 755.1 | 44.5 | 1.6 | 60.6 | 68.7 | 4.5 | 1457 | 3 | 15 | 180 | 59 | 2.3 | 2.3 | 42.2 | 42.4 | 45.1 | 207 | 0 | 0 | 18.5 | 32 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.5 | 28.1 | 43.75 | 2.7 | 1009.3894 | 4088.4688 | 5218.4106 | 1457 | 3.5816 | 3.5195 | 0.7 | 2.3 | 2.4 |  |  | 9.9907 | 26.8916 | 35.8161 | 36.289
46023.474 | 8.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2657.6 | 755.1 | 44.5 | 1.6 | 60.6 | 68.7 | 4.5 | 1502 | 3 | 15 | 180 | 59 | 2.3 | 2.2 | 42.4 | 42.5 | 45.3 | 207 | 0 | 0 | 19.4 | 30.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.5 | 27.5 | 43.9 | 2.8 | 1009.3123 | 4088.6075 | 5295.9082 | 1502 | 3.5259 | 3.5195 | 0.6 | 2.1 | 2.2 |  |  | 10.0032 | 26.9357 | 35.259 | 37.2045
46023.4744 | 9 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2667.4 | 755.1 | 44.6 | 1.6 | 60.8 | 69 | 4.5 | 1502 | 3.1 | 14 | 180 | 59 | 2.2 | 2.2 | 42.1 | 42.5 | 45.5 | 207 | 0 | 0 | 20 | 30.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.5 | 27.5 | 44 | 3 | 1009.2608 | 4088.7 | 5674.0264 | 1502 | 3.7776 | 3.5325 | 0.6 | 2.5 | 2 |  |  | 10.0157 | 26.983 | 37.7765 | 37.1396
46023.4747 | 9.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2677.2 | 755.1 | 44.7 | 1.6 | 61 | 69.5 | 4.5 | 1557 | 3.1 | 15 | 179 | 59 | 2.1 | 2.1 | 41.5 | 42.5 | 45.5 | 206 | 0 | 0 | 20.8 | 29.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.5 | 27.9 | 44 | 3 | 1009.2608 | 4088.7 | 5756.5577 | 1557 | 3.6972 | 3.5455 | 0.5 | 3.2 | 2 |  |  | 10.0287 | 27.031 | 36.9721 | 36.328
46023.4751 | 10 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2687 | 755.1 | 44.9 | 1.6 | 61.4 | 70.1 | 4.5 | 1557 | 3.1 | 15 | 179 | 59 | 2.1 | 2 | 41.1 | 42.7 | 45.6 | 207 | 0 | 0 | 21.6 | 28.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.5 | 27.9 | 44.15 | 2.9 | 1009.1835 | 4088.8387 | 5564.435 | 1557 | 3.5738 | 3.5585 | 0.4 | 3.8 | 1.9 |  |  | 10.0417 | 27.0774 | 35.7382 | 36.3124
46023.4754 | 10.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2706.6 | 755.1 | 45.2 | 1.6 | 62 | 71 | 4.5 | 1592 | 3.1 | 15 | 179 | 59 | 2.1 | 2 | 41 | 42.8 | 45.8 | 207 | 0 | 0 | 22.2 | 28.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.5 | 27.9 | 44.3 | 3 | 1009.106 | 4088.9775 | 5756.0656 | 1592 | 3.6156 | 3.5844 | 0.4 | 4.2 | 1.7 |  |  | 10.055 | 27.1253 | 36.1562 | 36.3804
46023.4758 | 11 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2706.6 | 755.1 | 45.2 | 1.6 | 62.7 | 72 | 4.5 | 1592 | 3.1 | 15 | 179 | 59 | 2.1 | 2.1 | 41 | 42.8 | 45.8 | 207 | 0 | 0 | 22.6 | 27.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.5 | 27.7 | 44.3 | 3 | 1009.106 | 4088.9775 | 5714.8035 | 1592 | 3.5897 | 3.5844 | 0.5 | 4.2 | 1.7 |  |  | 10.0682 | 27.173 | 35.897 | 36.508
46023.4761 | 11.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2716.4 | 755.1 | 45.3 | 1.6 | 63.1 | 72.5 | 4.5 | 1602 | 3.1 | 15 | 179 | 59 | 2.1 | 2 | 41 | 42.8 | 45.8 | 208 | 0 | 0 | 23 | 27.1 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.5 | 27.9 | 44.3 | 3 | 1009.106 | 4088.9775 | 5756.0656 | 1602 | 3.593 | 3.5974 | 0.4 | 4.3 | 1.7 |  |  | 10.0816 | 27.2209 | 35.9305 | 36.1388
46023.4764 | 12 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 28 | 29 | 28 | 2736 | 755.1 | 45.6 | 1.6 | 63.5 | 73.2 | 4.5 | 1602 | 3.3 | 15 | 181 | 59 | 2.1 | 2.1 | 41 | 42.8 | 45.8 | 208 | 0 | 0 | 23.2 | 26.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.5 | 27.9 | 44.3 | 3 | 1009.106 | 4088.9775 | 5756.0656 | 1602 | 3.593 | 3.6234 | 0.5 | 4.6 | 1.7 |  |  | 10.0949 | 27.2689 | 35.9305 | 35.9305
46023.4768 | 12.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 29 | 29 | 29 | 2765.5 | 745.3 | 46.1 | 1.3 | 64.2 | 74.1 | 4.6 | 1643 | 3.4 | 15 | 181 | 59 | 2 | 2 | 41 | 42.8 | 46 | 208 | 0 | 0 | 23.4 | 26.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.5 | 27.9 | 44.4 | 3.2 | 1009.0544 | 4089.07 | 6139.6277 | 1643 | 3.7368 | 3.7106 | 0.7 | 5.1 | 1.5 |  |  | 10.1086 | 27.3201 | 37.3684 | 36.2565
46023.4771 | 13 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2785.1 | 745.3 | 46.4 | 1.3 | 65.1 | 75.1 | 4.6 | 1643 | 3.3 | 15 | 181 | 60 | 1.9 | 1.9 | 41 | 43.1 | 46.1 | 208 | 0 | 0 | 23.5 | 26.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.4 | 28.1 | 44.6 | 3 | 1008.9508 | 4089.255 | 5796.8292 | 1643 | 3.5282 | 3.7369 | 0.6 | 5.4 | 1.3 |  |  | 10.1223 | 27.3684 | 35.282 | 36.0817
46023.4775 | 13.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2794.9 | 745.3 | 46.5 | 1.3 | 65.8 | 76 | 4.6 | 1718 | 3.3 | 16 | 181 | 60 | 2 | 2 | 41.1 | 43 | 46.1 | 208 | 0 | 0 | 23.6 | 25.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.4 | 27.7 | 44.55 | 3.1 | 1008.9767 | 4089.2087 | 5904.874 | 1718 | 3.4371 | 3.75 | 0.7 | 5.4 | 1.3 |  |  | 10.1366 | 27.4176 | 34.3706 | 35.7764
46023.4778 | 14 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 29 | 30 | 29 | 2814.5 | 745.3 | 47.1 | 1.3 | 66.2 | 76.8 | 4.6 | 1718 | 3.4 | 16 | 180 | 60 | 2 | 2 | 41.1 | 43 | 46 | 208 | 0 | 0 | 23.7 | 25.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.4 | 27.9 | 44.5 | 3 | 1009.0026 | 4089.1625 | 5755.736 | 1718 | 3.3503 | 3.7763 | 0.7 | 6 | 1.4 |  |  | 10.1509 | 27.4655 | 33.5025 | 35.2908
46023.4782 | 14.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 30 | 30 | 30 | 2892.9 | 745.3 | 47.9 | 1.3 | 67.2 | 77.8 | 4.6 | 1742 | 3.6 | 16 | 180 | 60 | 1.9 | 1.9 | 41.1 | 43.1 | 46.1 | 214 | 0 | 0 | 23.8 | 25.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.4 | 27.9 | 44.6 | 3 | 1008.9508 | 4089.255 | 5755.5706 | 1742 | 3.304 | 3.8815 | 0.6 | 6.8 | 1.3 |  |  | 10.1655 | 27.5135 | 33.04 | 34.7127
46023.4785 | 15 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 31 | 32 | 31 | 2922.4 | 745.3 | 48.3 | 1.3 | 68.4 | 79 | 4.6 | 1742 | 4.1 | 18 | 180 | 61 | 2 | 1.9 | 41.1 | 43.1 | 46.3 | 223 | 80 | 2000 | 22.1 | 26.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.4 | 27.7 | 44.7 | 3.2 | 1008.8989 | 4089.3475 | 6095.0907 | 1742 | 3.4989 | 3.9211 | 0.6 | 7.2 | 1.1 |  |  | 10.18 | 27.5643 | 34.989 | 34.2368
46023.4789 | 15.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 32 | 32 | 32 | 2892.9 | 735.5 | 47.9 | 0.9 | 70 | 80.4 | 4.6 | 1959 | 4.2 | 18 | 180 | 60 | 1.7 | 1.7 | 41.3 | 43.1 | 47.1 | 224 | 80 | 2000 | 19.6 | 24.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.4 | 27.9 | 45.1 | 4 | 1008.6909 | 4089.7175 | 7672.9852 | 1959 | 3.9168 | 3.9332 | 0.8 | 6.6 | 0.3 |  |  | 10.1963 | 27.6282 | 39.1679 | 35.014
46023.4792 | 16 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 31 | 25 | 31 | 2843.9 | 735.5 | 47.2 | 0.9 | 70.4 | 80.8 | 4.6 | 1959 | 4.1 | 18 | 180 | 58 | 1.5 | 1.5 | 41.3 | 43.1 | 47.2 | 220 | 73 | 2000 | 18.3 | 19 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.4 | 27.7 | 45.15 | 4.1 | 1008.6648 | 4089.7638 | 7808.3178 | 1959 | 3.9859 | 3.8666 | 0.6 | 5.9 | 0.2 |  |  | 10.2126 | 27.6933 | 39.8587 | 36.1116
46023.4796 | 16.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 29 | 25 | 29 | 2824.3 | 735.5 | 46.9 | 0.9 | 69 | 79.7 | 4.6 | 2113 | 3.8 | 17 | 180 | 56 | 1.6 | 1.6 | 41.3 | 43.3 | 47.2 | 220 | 70 | 2000 | 18.4 | 18.9 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.4 | 27.7 | 45.25 | 3.9 | 1008.6127 | 4089.8562 | 7427.2081 | 2113 | 3.515 | 3.84 | 0.7 | 5.6 | 0.2 |  |  | 10.2302 | 27.7552 | 35.1501 | 36.4411
46023.4799 | 17 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 27 | 26 | 27 | 2785.1 | 745.3 | 46.4 | 1.3 | 66.2 | 77 | 4.6 | 2113 | 3.6 | 17 | 180 | 54 | 1.9 | 1.9 | 41.6 | 43.3 | 47.1 | 220 | 69 | 2000 | 19.2 | 19.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.4 | 27.9 | 45.2 | 3.8 | 1008.6388 | 4089.81 | 7289.124 | 2113 | 3.4497 | 3.7369 | 0.6 | 4.8 | 0.3 |  |  | 10.2478 | 27.8159 | 34.4966 | 36.7324
46023.4803 | 17.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2765.5 | 755.1 | 46.1 | 1.6 | 64 | 73.8 | 4.6 | 1878 | 3.5 | 18 | 180 | 53 | 2.1 | 2 | 43.3 | 43.5 | 47 | 220 | 69 | 2000 | 20.6 | 21.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.4 | 27.9 | 45.25 | 3.5 | 1008.6127 | 4089.8562 | 6713.5691 | 1878 | 3.5749 | 3.6624 | 0.4 | 2.8 | 0.4 |  |  | 10.2635 | 27.8719 | 35.7485 | 36.8843
46023.4806 | 18 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 27 | 28 | 27 | 2736 | 755.1 | 45.6 | 1.6 | 62.4 | 71 | 4.6 | 1878 | 3.6 | 17 | 180 | 53 | 2.2 | 2.1 | 44.2 | 43.6 | 46.8 | 218 | 69 | 2000 | 23.5 | 25.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.4 | 27.9 | 45.2 | 3.2 | 1008.6388 | 4089.81 | 6138.2097 | 1878 | 3.2685 | 3.6234 | 0.5 | 1.4 | 0.6 |  |  | 10.2791 | 27.923 | 32.6848 | 35.5877
46023.481 | 18.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2736 | 755.1 | 45.6 | 1.6 | 62.7 | 70 | 4.6 | 1878 | 3.7 | 17 | 181 | 53 | 2.2 | 2 | 44.4 | 43.6 | 46.6 | 218 | 75 | 2000 | 23.5 | 33.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.4 | 27.9 | 45.1 | 3 | 1008.6909 | 4089.7175 | 5754.7389 | 1878 | 3.0643 | 3.6234 | 0.4 | 1.2 | 0.8 |  |  | 10.2948 | 27.971 | 30.6429 | 33.7446
46023.4813 | 19 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 29 | 32 | 29 | 2736 | 755.1 | 45.6 | 1.6 | 64 | 70.5 | 4.6 | 1843 | 3.8 | 17 | 181 | 54 | 2.2 | 2.1 | 44.4 | 43.8 | 46.6 | 217 | 92 | 2000 | 23.5 | 39.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.4 | 27.9 | 45.2 | 2.8 | 1008.6388 | 4089.81 | 5370.9335 | 1843 | 2.9142 | 3.6234 | 0.5 | 1.2 | 0.8 |  |  | 10.3102 | 28.0158 | 29.1423 | 32.543
46023.4817 | 19.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 31 | 32 | 31 | 2755.7 | 755.1 | 45.9 | 1.6 | 65.1 | 72 | 4.7 | 1843 | 4.1 | 17 | 181 | 56 | 2.2 | 2.1 | 44.4 | 43.8 | 46.8 | 217 | 92 | 2000 | 22.7 | 42.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.4 | 27.9 | 45.3 | 3 | 1008.5866 | 4089.9025 | 5754.4039 | 1843 | 3.1223 | 3.6495 | 0.5 | 1.5 | 0.6 |  |  | 10.3255 | 28.0637 | 31.223 | 31.8883
46023.482 | 20 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 31 | 30 | 31 | 2785.1 | 745.3 | 46.4 | 1.3 | 66.2 | 73.4 | 4.7 | 1936 | 4.2 | 18 | 181 | 58 | 2 | 1.9 | 45 | 43.8 | 47.1 | 216 | 105 | 2000 | 22.6 | 42.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.3 | 28.1 | 45.45 | 3.3 | 1008.5082 | 4090.0413 | 6374.9402 | 1936 | 3.2928 | 3.7369 | 0.6 | 1.4 | 0.2 |  |  | 10.3416 | 28.1168 | 32.9284 | 31.3243
46023.4823 | 20.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 30 | 30 | 2794.9 | 745.3 | 46.5 | 1.3 | 66.7 | 74.6 | 4.7 | 1936 | 4.2 | 18 | 181 | 58 | 2 | 1.8 | 45.1 | 43.8 | 47.2 | 216 | 112 | 2000 | 24.4 | 41 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.3 | 28.1 | 45.5 | 3.4 | 1008.482 | 4090.0875 | 6568.0241 | 1936 | 3.3926 | 3.75 | 0.5 | 1.4 | 0.1 |  |  | 10.3578 | 28.1716 | 33.9257 | 31.5725
46023.4827 | 21 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 25 | 29 | 2794.9 | 745.3 | 46.5 | 1.3 | 67 | 75.1 | 4.7 | 2125 | 4.1 | 19 | 182 | 58 | 2 | 1.9 | 45.1 | 44 | 47.2 | 217 | 112 | 2000 | 25 | 38.8 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.3 | 27.9 | 45.6 | 3.2 | 1008.4296 | 4090.18 | 6137.4922 | 2125 | 2.8882 | 3.75 | 0.6 | 1.4 | 0.1 |  |  | 10.3755 | 28.2227 | 28.8823 | 31.2204
46023.483 | 21.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 25 | 27 | 2775.3 | 755.1 | 46.2 | 1.6 | 67.2 | 75.7 | 4.6 | 2125 | 3.8 | 18 | 182 | 57 | 2 | 1.9 | 45.1 | 44 | 47.2 | 217 | 112 | 2000 | 26.3 | 37.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.4 | 27.7 | 45.6 | 3.2 | 1008.4296 | 4090.18 | 6093.4958 | 2125 | 2.8675 | 3.6754 | 0.3 | 1.1 | 0.2 |  |  | 10.3932 | 28.2735 | 28.6753 | 31.127
46023.4834 | 22 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2765.5 | 755.1 | 46.1 | 1.6 | 67.2 | 75.7 | 4.7 | 2092 | 3.8 | 18 | 182 | 58 | 2.3 | 2.1 | 45 | 44 | 47 | 215 | 113 | 2000 | 28.1 | 39 | 540 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.3 | 28.1 | 45.5 | 3 | 1008.482 | 4090.0875 | 5795.3154 | 2092 | 2.7702 | 3.6624 | 0.5 | 1.1 | 0.3 |  |  | 10.4106 | 28.3218 | 27.7023 | 30.4228
46023.4837 | 22.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2755.7 | 755.1 | 45.9 | 1.6 | 67.2 | 75.5 | 4.7 | 2092 | 3.8 | 18 | 182 | 58 | 2.4 | 2.2 | 45 | 44.2 | 47 | 215 | 119 | 2000 | 27.7 | 41.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.3 | 28.1 | 45.6 | 2.8 | 1008.4296 | 4090.18 | 5408.8025 | 2092 | 2.5855 | 3.6495 | 0.6 | 0.9 | 0.3 |  |  | 10.4281 | 28.3669 | 25.8547 | 29.0081
46023.4841 | 23 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 29 | 28 | 2765.5 | 755.1 | 46.1 | 1.6 | 67.4 | 75.4 | 4.7 | 1941 | 3.9 | 18 | 182 | 59 | 2.4 | 2.3 | 44.8 | 44.2 | 47 | 214 | 127 | 2000 | 27.3 | 42.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.3 | 28.1 | 45.6 | 2.8 | 1008.4296 | 4090.18 | 5408.8025 | 1941 | 2.7866 | 3.6624 | 0.7 | 1.3 | 0.3 |  |  | 10.4442 | 28.4119 | 27.8661 | 27.7961
46023.4844 | 23.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 29 | 29 | 2775.3 | 755.1 | 46.2 | 1.6 | 67.5 | 75.4 | 4.7 | 1941 | 4 | 18 | 182 | 60 | 2.3 | 2.2 | 45 | 44.2 | 47.1 | 215 | 127 | 2000 | 26.5 | 42.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.3 | 27.9 | 45.65 | 2.9 | 1008.4034 | 4090.2263 | 5562.0206 | 1941 | 2.8655 | 3.6754 | 0.6 | 1.2 | 0.2 |  |  | 10.4604 | 28.4583 | 28.6554 | 27.7507
46023.4848 | 24 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 30 | 30 | 2785.1 | 755.1 | 46.4 | 1.6 | 67.8 | 75.8 | 4.7 | 1962 | 4.2 | 18 | 182 | 61 | 2.2 | 2.1 | 45.1 | 44.2 | 47.2 | 216 | 135 | 2000 | 26.4 | 42.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.3 | 27.9 | 45.7 | 3 | 1008.3772 | 4090.2725 | 5753.7299 | 1962 | 2.9326 | 3.6884 | 0.5 | 1.3 | 0.1 |  |  | 10.4768 | 28.5062 | 29.3258 | 27.8809
46023.4851 | 24.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 30 | 30 | 30 | 2804.7 | 755.1 | 46.7 | 1.6 | 68.2 | 76.1 | 4.7 | 1962 | 4.2 | 19 | 182 | 61 | 2.1 | 2 | 45.3 | 44.2 | 47.3 | 216 | 141 | 2000 | 26.1 | 41.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.3 | 27.7 | 45.75 | 3.1 | 1008.351 | 4090.3187 | 5902.8139 | 1962 | 3.0086 | 3.7143 | 0.4 | 1.4 | 0 |  |  | 10.4931 | 28.5554 | 30.0857 | 28.3575
46023.4855 | 25 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 29 | 28 | 29 | 2794.9 | 745.3 | 46.5 | 1.3 | 68.5 | 76.5 | 4.7 | 2088 | 4.1 | 19 | 182 | 60 | 2 | 2 | 45.3 | 44.2 | 47.3 | 215 | 144 | 2000 | 26.4 | 39.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.3 | 28.1 | 45.75 | 3.1 | 1008.351 | 4090.3187 | 5988.053 | 2088 | 2.8678 | 3.75 | 0.7 | 1.2 | 0 |  |  | 10.5105 | 28.6053 | 28.6784 | 28.9223
46023.4858 | 25.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2785.1 | 755.1 | 46.4 | 1.6 | 68.5 | 76.7 | 4.7 | 2088 | 4 | 19 | 183 | 60 | 2.2 | 2 | 45.3 | 44.2 | 47.3 | 215 | 144 | 2000 | 27.7 | 37.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.3 | 27.7 | 45.75 | 3.1 | 1008.351 | 4090.3187 | 5902.8139 | 2088 | 2.827 | 3.6884 | 0.4 | 1.1 | 0 |  |  | 10.5279 | 28.6545 | 28.2702 | 29.0031
46023.4862 | 26 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2785.1 | 755.1 | 46.4 | 1.6 | 68.5 | 76.5 | 4.7 | 2110 | 4 | 18 | 183 | 60 | 2.2 | 2.1 | 45.3 | 44.4 | 47.3 | 214 | 144 | 2000 | 28 | 38.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.3 | 27.7 | 45.85 | 2.9 | 1008.2985 | 4090.4113 | 5521.8245 | 2110 | 2.617 | 3.6884 | 0.5 | 1.1 | 0 |  |  | 10.5455 | 28.7005 | 26.1698 | 28.506
46023.4865 | 26.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2794.9 | 755.1 | 46.5 | 1.6 | 68.5 | 76.4 | 4.7 | 2110 | 4 | 19 | 183 | 60 | 2.3 | 2.2 | 45.3 | 44.6 | 47.3 | 214 | 150 | 2000 | 28 | 40.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.3 | 27.9 | 45.95 | 2.7 | 1008.2459 | 4090.5037 | 5177.9753 | 2110 | 2.454 | 3.7014 | 0.6 | 1.2 | 0 |  |  | 10.5631 | 28.7437 | 24.5402 | 27.5488
46023.4869 | 27 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2785.1 | 755.1 | 46.4 | 1.6 | 68.7 | 76.4 | 4.7 | 2030 | 4 | 19 | 183 | 61 | 2.2 | 2.1 | 45.3 | 44.4 | 47.3 | 213 | 156 | 2000 | 28.1 | 41.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.3 | 28.1 | 45.85 | 2.9 | 1008.2985 | 4090.4113 | 5601.562 | 2030 | 2.7594 | 3.6884 | 0.5 | 1.1 | 0 |  |  | 10.58 | 28.7904 | 27.5939 | 27.0505
46023.4872 | 27.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2785.1 | 755.1 | 46.4 | 1.6 | 68.8 | 76.5 | 4.7 | 2030 | 4 | 19 | 183 | 61 | 2.3 | 2.2 | 45.3 | 44.6 | 47.3 | 212 | 156 | 2000 | 28.2 | 41.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.3 | 27.7 | 45.95 | 2.7 | 1008.2459 | 4090.5037 | 5140.8572 | 2030 | 2.5324 | 3.6884 | 0.6 | 1.1 | 0 |  |  | 10.5969 | 28.8332 | 25.3244 | 26.3797
46023.4876 | 28 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2794.9 | 755.1 | 46.5 | 1.6 | 69 | 76.5 | 4.7 | 2035 | 4 | 19 | 182 | 62 | 2.3 | 2.2 | 45.3 | 44.6 | 47.3 | 212 | 161 | 2000 | 28.5 | 41.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.3 | 27.7 | 45.95 | 2.7 | 1008.2459 | 4090.5037 | 5140.8572 | 2035 | 2.5262 | 3.7014 | 0.6 | 1.2 | 0 |  |  | 10.6139 | 28.876 | 25.2622 | 25.7781
46023.4879 | 28.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2794.9 | 755.1 | 46.5 | 1.6 | 69.1 | 76.7 | 4.7 | 2035 | 4 | 19 | 182 | 62 | 2.3 | 2.2 | 45.3 | 44.8 | 47.3 | 211 | 166 | 2000 | 28.6 | 41.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.3 | 27.9 | 46.05 | 2.5 | 1008.1933 | 4090.5963 | 4794.2798 | 2035 | 2.3559 | 3.7014 | 0.6 | 1.2 | 0 |  |  | 10.6308 | 28.916 | 23.5591 | 25.256
46023.4883 | 29 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2804.7 | 764.9 | 46.7 | 2 | 69.1 | 76.7 | 4.7 | 2039 | 4 | 19 | 182 | 63 | 2.5 | 2.3 | 45.5 | 44.8 | 47.5 | 210 | 170 | 2000 | 28.8 | 41 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.3 | 27.9 | 46.15 | 2.7 | 1008.1406 | 4090.6887 | 5177.6687 | 2039 | 2.5393 | 3.6668 | 0.3 | 1.2 | -0.2 |  |  | 10.6478 | 28.9591 | 25.3932 | 25.4266
46023.4886 | 29.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2804.7 | 764.9 | 46.7 | 2 | 69.1 | 76.7 | 4.8 | 2048 | 4 | 19 | 182 | 63 | 2.5 | 2.3 | 45.5 | 44.8 | 47.5 | 209 | 170 | 2000 | 29 | 40.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.2 | 27.7 | 46.15 | 2.7 | 1008.1406 | 4090.6887 | 5140.5528 | 2048 | 2.51 | 3.6668 | 0.3 | 1.2 | -0.3 |  |  | 10.6649 | 29.002 | 25.1004 | 24.9279
46023.4889 | 30 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 26 | 27 | 2804.7 | 764.9 | 46.7 | 2 | 69.1 | 76.5 | 4.8 | 2048 | 3.9 | 19 | 183 | 63 | 2.4 | 2.3 | 45.5 | 44.8 | 47.5 | 209 | 173 | 2000 | 29.2 | 40 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.2 | 27.7 | 46.15 | 2.7 | 1008.1406 | 4090.6887 | 5140.5528 | 2048 | 2.51 | 3.6668 | 0.3 | 1.2 | -0.3 |  |  | 10.682 | 29.0448 | 25.1004 | 24.883
46023.4893 | 30.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2794.9 | 764.9 | 46.5 | 2 | 69.1 | 76.5 | 4.8 | 2027 | 3.8 | 19 | 183 | 63 | 2.5 | 2.4 | 45.5 | 45 | 47.5 | 209 | 175 | 2000 | 30.1 | 39.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.2 | 27.9 | 46.25 | 2.5 | 1008.0879 | 4090.7812 | 4793.9954 | 2027 | 2.3651 | 3.6539 | 0.4 | 1 | -0.3 |  |  | 10.6988 | 29.0848 | 23.6507 | 24.5607
46023.4896 | 31 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2794.9 | 764.9 | 46.5 | 2 | 69 | 76.2 | 4.8 | 2027 | 3.8 | 19 | 183 | 64 | 2.6 | 2.5 | 45.5 | 45 | 47.3 | 207 | 179 | 2000 | 30.4 | 40.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.2 | 27.7 | 46.15 | 2.3 | 1008.1406 | 4090.6887 | 4378.9895 | 2027 | 2.1603 | 3.6539 | 0.5 | 1 | -0.1 |  |  | 10.7157 | 29.1213 | 21.6033 | 24.1696
46023.49 | 31.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2794.9 | 764.9 | 46.5 | 2 | 68.8 | 76 | 4.8 | 1936 | 3.8 | 19 | 183 | 63 | 2.7 | 2.6 | 45.5 | 45 | 47.3 | 208 | 179 | 2000 | 30.5 | 41.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.2 | 27.5 | 46.15 | 2.3 | 1008.1406 | 4090.6887 | 4347.3722 | 1936 | 2.2455 | 3.6539 | 0.6 | 1 | -0.1 |  |  | 10.7319 | 29.1575 | 22.4554 | 23.582
46023.4903 | 32 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 28 | 27 | 2794.9 | 764.9 | 46.5 | 2 | 68.7 | 75.8 | 4.8 | 1936 | 3.9 | 19 | 183 | 63 | 2.7 | 2.6 | 45.5 | 45 | 47.5 | 207 | 180 | 2000 | 30.7 | 41 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.2 | 27.5 | 46.25 | 2.5 | 1008.0879 | 4090.7812 | 4725.2642 | 1936 | 2.4407 | 3.6539 | 0.6 | 1 | -0.3 |  |  | 10.748 | 29.1969 | 24.4074 | 23.4434
46023.4907 | 32.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2824.3 | 764.9 | 46.9 | 2 | 68.7 | 75.7 | 4.8 | 1977 | 4.1 | 19 | 179 | 63 | 2.6 | 2.5 | 45.6 | 45.1 | 47.6 | 206 | 184 | 2000 | 30 | 41 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.2 | 27.9 | 46.35 | 2.5 | 1008.0351 | 4090.8738 | 4793.8527 | 1977 | 2.4248 | 3.6924 | 0.5 | 1.3 | -0.4 |  |  | 10.7645 | 29.2368 | 24.2481 | 23.273
46023.491 | 33 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 27 | 26 | 27 | 2814.5 | 764.9 | 46.9 | 2 | 69 | 75.7 | 4.8 | 1977 | 4 | 19 | 179 | 63 | 2.5 | 2.4 | 45.6 | 45 | 47.6 | 206 | 184 | 2000 | 29.8 | 39.4 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.2 | 27.9 | 46.3 | 2.6 | 1008.0615 | 4090.8275 | 4985.681 | 1977 | 2.5218 | 3.6796 | 0.4 | 1.3 | -0.4 |  |  | 10.781 | 29.2784 | 25.2184 | 23.5865
46023.4914 | 33.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2804.7 | 764.9 | 46.7 | 2 | 69 | 75.8 | 4.8 | 2045 | 3.8 | 19 | 179 | 63 | 2.6 | 2.5 | 45.6 | 45.1 | 47.6 | 206 | 184 | 2000 | 30.6 | 38.7 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.2 | 27.9 | 46.35 | 2.5 | 1008.0351 | 4090.8738 | 4793.8527 | 2045 | 2.3442 | 3.6668 | 0.5 | 1.1 | -0.4 |  |  | 10.798 | 29.3183 | 23.4418 | 23.9542
46023.4917 | 34 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2804.7 | 764.9 | 46.7 | 2 | 68.8 | 75.7 | 4.8 | 2045 | 3.8 | 19 | 179 | 63 | 2.7 | 2.6 | 45.6 | 45.3 | 47.6 | 206 | 180 | 2000 | 31.1 | 39.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.2 | 28.1 | 46.45 | 2.3 | 1007.9822 | 4090.9662 | 4441.8274 | 2045 | 2.172 | 3.6668 | 0.6 | 1.1 | -0.4 |  |  | 10.815 | 29.3553 | 21.7204 | 23.8072
46023.4921 | 34.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2804.7 | 774.7 | 46.7 | 2.3 | 68.8 | 75.5 | 4.8 | 1958 | 3.8 | 19 | 180 | 63 | 2.8 | 2.6 | 45.6 | 45.1 | 47.6 | 205 | 180 | 2000 | 30.8 | 40.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.2 | 27.7 | 46.35 | 2.5 | 1008.0351 | 4090.8738 | 4759.4882 | 1958 | 2.4308 | 3.6204 | 0.3 | 1.1 | -0.4 |  |  | 10.8314 | 29.395 | 24.3079 | 23.7873
46023.4924 | 35 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2804.7 | 774.7 | 46.7 | 2.3 | 68.8 | 75.7 | 4.8 | 1958 | 3.8 | 19 | 180 | 63 | 2.8 | 2.7 | 45.6 | 45.1 | 47.6 | 205 | 180 | 2000 | 30.8 | 41.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.2 | 27.9 | 46.35 | 2.5 | 1008.0351 | 4090.8738 | 4793.8527 | 1958 | 2.4483 | 3.6204 | 0.4 | 1.1 | -0.4 |  |  | 10.8477 | 29.4349 | 24.4834 | 23.8344
46023.4928 | 35.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2814.5 | 774.7 | 46.7 | 2.3 | 68.8 | 75.7 | 4.9 | 1950 | 3.8 | 19 | 180 | 63 | 2.8 | 2.7 | 45.6 | 45.1 | 47.6 | 205 | 180 | 2000 | 30.8 | 41.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.2 | 27.9 | 46.35 | 2.5 | 1008.0351 | 4090.8738 | 4793.8527 | 1950 | 2.4584 | 3.633 | 0.4 | 1.1 | -0.4 |  |  | 10.8639 | 29.4749 | 24.5839 | 23.7075
46023.4931 | 36 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2814.5 | 774.7 | 46.8 | 2.3 | 68.8 | 75.7 | 4.9 | 1950 | 3.8 | 19 | 180 | 63 | 2.9 | 2.7 | 45.6 | 45.1 | 47.6 | 205 | 180 | 2000 | 30.8 | 41.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.2 | 28.1 | 46.35 | 2.5 | 1008.0351 | 4090.8738 | 4828.2173 | 1950 | 2.476 | 3.633 | 0.4 | 1.2 | -0.4 |  |  | 10.8802 | 29.5151 | 24.7601 | 23.9711
46023.4935 | 36.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2814.5 | 774.7 | 46.8 | 2.3 | 68.8 | 75.7 | 4.9 | 1952 | 3.8 | 19 | 180 | 63 | 2.9 | 2.8 | 45.6 | 45.1 | 47.6 | 205 | 180 | 2000 | 31 | 41.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.2 | 28.1 | 46.35 | 2.5 | 1008.0351 | 4090.8738 | 4828.2173 | 1952 | 2.4735 | 3.633 | 0.5 | 1.2 | -0.4 |  |  | 10.8964 | 29.5553 | 24.7347 | 24.574
46023.4938 | 37 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2814.5 | 774.7 | 46.8 | 2.3 | 68.8 | 75.7 | 4.9 | 1952 | 3.8 | 19 | 181 | 63 | 2.8 | 2.7 | 45.6 | 45.3 | 47.6 | 205 | 180 | 2000 | 31 | 41.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.2 | 27.9 | 46.45 | 2.3 | 1007.9822 | 4090.9662 | 4410.213 | 1952 | 2.2593 | 3.633 | 0.4 | 1.2 | -0.4 |  |  | 10.9127 | 29.5921 | 22.5933 | 24.2311
46023.4942 | 37.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2814.5 | 774.7 | 46.8 | 2.3 | 69 | 75.7 | 4.9 | 1955 | 3.8 | 19 | 181 | 64 | 2.9 | 2.7 | 45.6 | 45.3 | 47.6 | 205 | 180 | 2000 | 31 | 41.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.2 | 27.9 | 46.45 | 2.3 | 1007.9822 | 4090.9662 | 4410.213 | 1955 | 2.2559 | 3.633 | 0.4 | 1.2 | -0.4 |  |  | 10.929 | 29.6289 | 22.5586 | 23.8461
46023.4945 | 38 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2814.5 | 774.7 | 46.8 | 2.3 | 69 | 75.8 | 4.9 | 1955 | 3.8 | 19 | 181 | 64 | 2.9 | 2.8 | 45.6 | 45.3 | 47.6 | 205 | 180 | 2000 | 31 | 41.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.2 | 27.5 | 46.45 | 2.3 | 1007.9822 | 4090.9662 | 4346.9842 | 1955 | 2.2235 | 3.633 | 0.5 | 1.2 | -0.4 |  |  | 10.9453 | 29.6651 | 22.2352 | 23.3764
46023.4948 | 38.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2814.5 | 774.7 | 46.8 | 2.3 | 69 | 75.8 | 4.9 | 1957 | 3.8 | 19 | 181 | 64 | 2.9 | 2.8 | 45.6 | 45.3 | 47.6 | 205 | 180 | 2000 | 31 | 41.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.2 | 27.9 | 46.45 | 2.3 | 1007.9822 | 4090.9662 | 4410.213 | 1957 | 2.2536 | 3.633 | 0.5 | 1.2 | -0.4 |  |  | 10.9616 | 29.7018 | 22.5356 | 22.9315
46023.4952 | 39 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2824.3 | 774.7 | 46.9 | 2.3 | 69 | 75.8 | 4.9 | 1957 | 3.8 | 19 | 180 | 64 | 2.9 | 2.8 | 45.6 | 45.3 | 47.6 | 205 | 180 | 2000 | 31 | 41.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.2 | 28.3 | 46.45 | 2.3 | 1007.9822 | 4090.9662 | 4473.4419 | 1957 | 2.2859 | 3.6457 | 0.5 | 1.3 | -0.4 |  |  | 10.9779 | 29.7391 | 22.8587 | 22.5563
46023.4955 | 39.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2834.1 | 774.7 | 47.1 | 2.3 | 69.1 | 75.8 | 4.9 | 1959 | 3.9 | 19 | 180 | 64 | 2.9 | 2.8 | 45.8 | 45.5 | 47.7 | 205 | 180 | 2000 | 31.1 | 41.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.2 | 28.3 | 46.6 | 2.2 | 1007.9029 | 4091.105 | 4278.7526 | 1959 | 2.1842 | 3.6583 | 0.5 | 1.3 | -0.5 |  |  | 10.9942 | 29.7748 | 21.8415 | 22.4059
46023.4959 | 40 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2824.3 | 774.7 | 46.9 | 2.3 | 69.1 | 76 | 5 | 1959 | 3.7 | 19 | 180 | 64 | 2.9 | 2.8 | 45.8 | 45.5 | 47.7 | 205 | 180 | 2000 | 31.1 | 41.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.2 | 27.9 | 46.6 | 2.2 | 1007.9029 | 4091.105 | 4218.2755 | 1959 | 2.1533 | 3.6457 | 0.5 | 1.1 | -0.5 |  |  | 11.0106 | 29.8099 | 21.5328 | 22.2008
46023.4962 | 40.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2824.3 | 774.7 | 46.9 | 2.3 | 69.1 | 76 | 5 | 1938 | 3.7 | 19 | 180 | 64 | 3 | 2.9 | 45.8 | 45.5 | 47.6 | 204 | 176 | 2000 | 31.7 | 41.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.1 | 28.1 | 46.55 | 2.1 | 1007.9293 | 4091.0588 | 4055.4604 | 1938 | 2.0926 | 3.6457 | 0.6 | 1.1 | -0.5 |  |  | 11.0267 | 29.8437 | 20.926 | 21.9389
46023.4966 | 41 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2824.3 | 774.7 | 46.9 | 2.3 | 69.1 | 76 | 5 | 1938 | 3.7 | 19 | 180 | 64 | 3 | 2.9 | 45.8 | 45.5 | 47.6 | 205 | 176 | 2000 | 31.7 | 41.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.1 | 28.3 | 46.55 | 2.1 | 1007.9293 | 4091.0588 | 4084.3249 | 1938 | 2.1075 | 3.6457 | 0.6 | 1.1 | -0.5 |  |  | 11.0429 | 29.8777 | 21.0749 | 21.6468
46023.4969 | 41.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2824.3 | 774.7 | 46.9 | 2.3 | 69.1 | 75.8 | 5 | 1898 | 3.7 | 19 | 181 | 64 | 3 | 3 | 45.8 | 45.5 | 47.7 | 204 | 176 | 2000 | 31.7 | 41.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.1 | 28.3 | 46.6 | 2.2 | 1007.9029 | 4091.105 | 4278.7526 | 1898 | 2.2543 | 3.6457 | 0.7 | 1.1 | -0.6 |  |  | 11.0587 | 29.9134 | 22.5435 | 21.5838
46023.4973 | 42 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2834.1 | 774.7 | 47.1 | 2.3 | 69 | 75.8 | 5 | 1898 | 3.7 | 19 | 181 | 64 | 3 | 3 | 45.8 | 45.5 | 47.7 | 204 | 176 | 2000 | 31.8 | 41.6 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.1 | 28.1 | 46.6 | 2.2 | 1007.9029 | 4091.105 | 4248.5141 | 1898 | 2.2384 | 3.6583 | 0.7 | 1.3 | -0.6 |  |  | 11.0745 | 29.9488 | 22.3842 | 21.6923
46023.4976 | 42.5 | EHS MONO LOWTEMP | On | Off | Off | Off | Off | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2834.1 | 774.7 | 47.1 | 2.3 | 69 | 75.8 | 5 | 1898 | 3.7 | 19 | 181 | 64 | 3 | 3 | 45.8 | 45.5 | 47.7 | 204 | 176 | 2000 | 31.8 | 41.8 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.1 | 27.7 | 46.6 | 2.2 | 1007.9029 | 4091.105 | 4188.037 | 1898 | 2.2066 | 3.6583 | 0.7 | 1.3 | -0.6 |  |  | 11.0903 | 29.9837 | 22.0655 | 21.7988
46023.498 | 43 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 24 | 24 | 2824.3 | 784.5 | 46.9 | 2.7 | 69 | 75.8 | 5 | 1899 | 2.9 | 15 | 181 | 63 | 3 | 3 | 45.8 | 45.5 | 47.7 | 204 | 0 | 0 | 29.2 | 41.3 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.1 | 27.9 | 46.6 | 2.2 | 1007.9029 | 4091.105 | 4218.2755 | 1899 | 2.2213 | 3.6001 | 0.3 | 1.1 | -0.6 |  |  | 11.1061 | 30.0189 | 22.2131 | 22.0563
46023.4983 | 43.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 24 | 24 | 2834.1 | 784.5 | 47.1 | 2.7 | 68.8 | 76 | 5 | 1899 | 3 | 16 | 181 | 62 | 3.1 | 3 | 45.6 | 45.5 | 47.6 | 203 | 0 | 0 | 25.6 | 40.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.1 | 27.9 | 46.55 | 2.1 | 1007.9293 | 4091.0588 | 4026.596 | 1899 | 2.1204 | 3.6126 | 0.3 | 1.5 | -0.5 |  |  | 11.1219 | 30.0524 | 21.2038 | 22.082
46023.4987 | 44 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2834.1 | 784.5 | 47.1 | 2.7 | 68.1 | 76.1 | 5 | 1684 | 3.1 | 16 | 181 | 62 | 3.1 | 3 | 45.5 | 45.5 | 47.6 | 203 | 0 | 0 | 21.8 | 39.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.1 | 28.1 | 46.55 | 2.1 | 1007.9293 | 4091.0588 | 4055.4604 | 1684 | 2.4082 | 3.6126 | 0.3 | 1.6 | -0.5 |  |  | 11.136 | 30.0862 | 24.0823 | 22.3898
46023.499 | 44.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2843.9 | 774.7 | 47.2 | 2.3 | 67.7 | 76 | 5 | 1684 | 3.1 | 16 | 181 | 62 | 3 | 3 | 45.5 | 45.5 | 47.7 | 203 | 0 | 0 | 20.1 | 38 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.1 | 27.9 | 46.6 | 2.2 | 1007.9029 | 4091.105 | 4218.2755 | 1684 | 2.5049 | 3.671 | 0.7 | 1.7 | -0.6 |  |  | 11.15 | 30.1214 | 25.0491 | 22.9228
46023.4994 | 45 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 24 | 24 | 2843.9 | 774.7 | 47.2 | 2.3 | 67.2 | 76 | 5 | 1553 | 3 | 16 | 181 | 62 | 3 | 3 | 45.5 | 45.5 | 47.7 | 203 | 0 | 0 | 19.7 | 36.5 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.1 | 27.7 | 46.6 | 2.2 | 1007.9029 | 4091.105 | 4188.037 | 1553 | 2.6967 | 3.671 | 0.7 | 1.7 | -0.6 |  |  | 11.163 | 30.1563 | 26.9674 | 23.9032
46023.4997 | 45.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 24 | 24 | 2843.9 | 784.5 | 47.2 | 2.7 | 67 | 75.8 | 5 | 1553 | 3 | 16 | 181 | 62 | 3 | 3 | 45.5 | 45.6 | 47.7 | 203 | 0 | 0 | 19.8 | 35.1 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47.1 | 27.7 | 46.65 | 2.1 | 1007.8764 | 4091.1512 | 3997.6118 | 1553 | 2.5741 | 3.6251 | 0.3 | 1.7 | -0.6 |  |  | 11.1759 | 30.1896 | 25.7412 | 24.6088
46023.5001 | 46 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 23 | 23 | 23 | 2843.9 | 784.5 | 47.2 | 2.7 | 66.7 | 75.7 | 5.1 | 1566 | 3 | 16 | 181 | 62 | 3 | 3 | 45.3 | 45.6 | 47.7 | 203 | 0 | 0 | 20.2 | 34.2 | 550 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47 | 27.7 | 46.65 | 2.1 | 1007.8764 | 4091.1512 | 3997.6118 | 1566 | 2.5528 | 3.6251 | 0.3 | 1.9 | -0.7 |  |  | 11.1889 | 30.2229 | 25.5275 | 25.4735
46023.5004 | 46.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 23 | 23 | 23 | 2834.1 | 784.5 | 47.1 | 2.7 | 66.4 | 75.5 | 5.1 | 1566 | 2.9 | 16 | 181 | 62 | 3.1 | 3.1 | 45.1 | 45.6 | 47.7 | 203 | 0 | 0 | 21.1 | 33.1 | 500 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47 | 28.1 | 46.65 | 2.1 | 1007.8764 | 4091.1512 | 4055.3391 | 1566 | 2.5896 | 3.6126 | 0.4 | 2 | -0.7 |  |  | 11.202 | 30.2567 | 25.8962 | 25.8363
46023.5008 | 47 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 22 | 22 | 22 | 2824.3 | 784.5 | 46.9 | 2.7 | 66.2 | 75.2 | 5.1 | 1509 | 2.7 | 16 | 181 | 62 | 3.1 | 3.1 | 45.1 | 45.6 | 47.6 | 203 | 0 | 0 | 22 | 32.2 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47 | 28.1 | 46.6 | 2 | 1007.9029 | 4091.105 | 3862.2855 | 1509 | 2.5595 | 3.6001 | 0.4 | 1.8 | -0.6 |  |  | 11.2146 | 30.2889 | 25.595 | 25.9455
46023.5011 | 47.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 22 | 22 | 22 | 2834.1 | 784.5 | 47.1 | 2.7 | 66.1 | 75.1 | 5.1 | 1509 | 2.8 | 16 | 181 | 62 | 3.1 | 3.1 | 45.1 | 45.6 | 47.6 | 202 | 0 | 0 | 22.7 | 31.2 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47 | 27.9 | 46.6 | 2 | 1007.9029 | 4091.105 | 3834.7959 | 1509 | 2.5413 | 3.6126 | 0.4 | 2 | -0.6 |  |  | 11.2271 | 30.3208 | 25.4128 | 25.6345
46023.5014 | 0 | EHS MONO LOWTEMP | Off | Off | Off | Off | On | Stop | Heat | 0 | 0 | 0 | 0 | 2716.4 | 823.8 | 45.3 | 3.7 | 66.1 | 75 | 5.1 | 1427 | 0 | 0 | 165 | 59 | 3.7 | 3.6 | 45.1 | 45.6 | 47.3 | 0 | 0 | 0 | 23.4 | 30.6 | 470 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47 | 27.9 | 46.45 | 1.7 | 1007.9822 | 4090.9662 | 3259.7227 | 1427 | 2.2843 | 3.2974 | -0.1 | 0.2 | -0.3 |  |  | 11.239 | 30.348 | 22.8432 | 25.0549
46023.5018 | 0.5 | EHS MONO LOWTEMP | Off | Off | On | Off | On | Stop | Heat | 0 | 0 | 0 | 0 | 2265.3 | 902.2 | 38.1 | 6.7 | 65.1 | 74.6 | 5.1 | 1427 | 0 | 0 | 165 | 55 | 5 | 5 | 43.8 | 46.3 | 46.5 | 0 | 0 | 0 | 23.8 | 30.1 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47 | 28.1 | 46.4 | 0.2 | 1008.0087 | 4090.92 | 386.2516 | 1427 | 0.27067 | 2.5109 | -1.7 | -5.7 | 0.5 |  |  | 11.2509 | 30.3512
46023.5021 | 1 | EHS MONO LOWTEMP | Off | Off | On | Off | On | Stop | Heat | 0 | 0 | 0 | 0 | 1059.1 | 931.6 | 12.4 | 7.4 | 61.8 | 73.1 | 5.1 | 722 | 0 | 0 | 165 | 53 | 7 | 8 | 34.8 | 46.5 | 46.5 | 0 | 0 | 0 | 24.5 | 29.5 | 40 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47 | 28.1 | 46.5 | 0 | 1007.9558 | 4091.0125 | 0 | 722 | 0 | 1.1369 | 0.6 | -22.4 | 0.5 |  |  | 11.2569 | 30.3512
46023.5025 | 1.5 | EHS MONO LOWTEMP | Off | Off | On | Off | On | Stop | Heat | 0 | 0 | 0 | 0 | 912 | 941.4 | 7 | 8 | 58.8 | 71.1 | 5.2 | 722 | 0 | 0 | 165 | 52 | 7.7 | 9.2 | 29.5 | 44.8 | 46.5 | 0 | 0 | 0 | 24.7 | 28.7 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47 | 0 | 45.65 | 1.7 | 1008.4034 | 4090.2263 | 0 | 722 | 0 | 0.96877 | 1.2 | -22.5 | 0.5 |  |  | 11.263 | 30.3512
46023.5028 | 2 | EHS MONO LOWTEMP | Off | Off | On | Off | On | Stop | Heat | 0 | 0 | 0 | 0 | 892.4 | 921.8 | 6.4 | 7.4 | 57 | 69.2 | 5.3 | 166 | 0 | 0 | 165 | 51 | 7.6 | 9.7 | 27.5 | 42.7 | 46.5 | 0 | 0 | 0 | 24.2 | 28 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 47 | 0 | 44.6 | 3.8 | 1008.9508 | 4089.255 | 0 | 166 | 0 | 0.96811 | 2.3 | -21.1 | 0.5 |  |  | 11.2644 | 30.3512
46023.5032 | 2.5 | EHS MONO LOWTEMP | Off | Off | On | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 882.6 | 912 | 6.1 | 7 | 56.1 | 68.1 | 5.4 | 166 | 0 | 0 | 165 | 51 | 7.3 | 10.2 | 26.6 | 42 | 46.5 | 0 | 0 | 0 | 23.3 | 27.5 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 0 | 44.25 | 4.5 | 1009.1319 | 4088.9313 | 0 | 166 | 0 | 0.96776 | 3.2 | -20.5 | 0.3 |  |  | 11.2657 | 30.3512
46023.5035 | 3 | EHS MONO LOWTEMP | Off | Off | On | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 872.8 | 912 | 5.8 | 7 | 55 | 66.5 | 5.5 | 90 | 0 | 0 | 165 | 50 | 7 | 10.7 | 25.7 | 41.3 | 46.5 | 0 | 0 | 0 | 21.7 | 26.7 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 0 | 43.9 | 5.2 | 1009.3123 | 4088.6075 | 0 | 90 | 0 | 0.95702 | 3.7 | -19.9 | 0.3 |  |  | 11.2665 | 30.3512
46023.5039 | 3.5 | EHS MONO LOWTEMP | Off | Off | On | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 882.6 | 912 | 6.1 | 7 | 54 | 65.1 | 5.5 | 90 | 0 | 0 | 165 | 50 | 7.1 | 11.2 | 24.8 | 41 | 46.5 | 0 | 0 | 0 | 20 | 26.1 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 0 | 43.75 | 5.5 | 1009.3894 | 4088.4688 | 0 | 90 | 0 | 0.96776 | 4.2 | -18.7 | 0.3 |  |  | 11.2672 | 30.3512
46023.5042 | 4 | EHS MONO LOWTEMP | Off | Off | On | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 872.8 | 912 | 5.8 | 7 | 53.2 | 64 | 5.6 | 90 | 0 | 0 | 165 | 49 | 7.1 | 11.7 | 24.1 | 40.8 | 46.5 | 0 | 0 | 0 | 18.6 | 25.3 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.7 | 0 | 43.65 | 5.7 | 1009.4407 | 4088.3762 | 0 | 90 | 0 | 0.95702 | 4.7 | -18.3 | 0.2 |  |  | 11.268 | 30.3512
46023.5046 | 4.5 | EHS MONO LOWTEMP | Off | Off | On | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 872.8 | 902.2 | 5.8 | 6.7 | 52.5 | 63 | 5.7 | 90 | 0 | 0 | 165 | 49 | 7.1 | 12.1 | 23.4 | 41 | 46.5 | 0 | 0 | 0 | 17.2 | 24.6 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.6 | 0 | 43.75 | 5.5 | 1009.3894 | 4088.4688 | 0 | 90 | 0 | 0.96741 | 5.4 | -17.6 | 0.1 |  |  | 11.2687 | 30.3512
46023.5049 | 5 | EHS MONO LOWTEMP | Off | Off | On | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 902.2 | 912 | 6.7 | 7 | 52 | 62.2 | 5.8 | 90 | 0 | 0 | 166 | 49 | 7 | 12.3 | 22.8 | 41.1 | 46.3 | 2000 | 0 | 0 | 16.5 | 24.3 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.6 | 0 | 43.7 | 5.2 | 1009.415 | 4088.4225 | 0 | 90 | 0 | 0.98925 | 5.3 | -16.1 | 0.3 |  |  | 11.2695 | 30.3512
46023.5053 | 5.5 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 892.4 | 921.8 | 6.4 | 7.4 | 51 | 61.5 | 5.8 | 90 | 0 | 0 | 166 | 46 | 7.5 | 12.8 | 22.4 | 41.5 | 46.3 | 2000 | 0 | 0 | 15.6 | 23.7 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 0 | 43.9 | 4.8 | 1009.3123 | 4088.6075 | 0 | 90 | 0 | 0.96811 | 5.4 | -16 | 0.2 |  |  | 11.2702 | 30.3512
46023.5056 | 6 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 882.6 | 912 | 6.1 | 7 | 50.3 | 60.6 | 5.7 | 90 | 0 | 0 | 166 | 45 | 7.3 | 13.2 | 22.1 | 41.8 | 46.1 | 2000 | 0 | 0 | 14.8 | 23.1 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 0 | 43.95 | 4.3 | 1009.2865 | 4088.6537 | 0 | 90 | 0 | 0.96776 | 6.2 | -16 | 0.4 |  |  | 11.271 | 30.3512
46023.506 | 6.5 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 872.8 | 902.2 | 5.8 | 6.7 | 49.8 | 60 | 5.8 | 90 | 0 | 0 | 166 | 45 | 7.3 | 13.4 | 22 | 42.4 | 46 | 2000 | 0 | 0 | 14.1 | 22.5 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 0 | 44.2 | 3.6 | 1009.1577 | 4088.885 | 0 | 90 | 0 | 0.96741 | 6.7 | -16.2 | 0.5 |  |  | 11.2717 | 30.3512
46023.5063 | 7 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 863 | 892.4 | 5.4 | 6.4 | 49.1 | 59.4 | 5.8 | 90 | 0 | 0 | 168 | 45 | 7.2 | 13.7 | 22 | 42.8 | 45.8 | 2000 | 0 | 0 | 13.5 | 22 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 0 | 44.3 | 3 | 1009.106 | 4088.9775 | 0 | 90 | 0 | 0.96706 | 7.3 | -16.6 | 0.7 |  |  | 11.2725 | 30.3512
46023.5067 | 7.5 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 863 | 892.4 | 5.4 | 6.4 | 48.8 | 59.1 | 5.8 | 90 | 0 | 0 | 168 | 44 | 7.2 | 13.9 | 21.8 | 43.1 | 45.8 | 2000 | 0 | 0 | 13.2 | 21.6 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 0 | 44.45 | 2.7 | 1009.0285 | 4089.1163 | 0 | 90 | 0 | 0.96706 | 7.5 | -16.4 | 0.7 |  |  | 11.2732 | 30.3512
46023.507 | 8 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 863 | 892.4 | 5.4 | 6.4 | 48.1 | 58.5 | 5.9 | 90 | 0 | 0 | 168 | 44 | 7.2 | 14.2 | 21.6 | 43.3 | 45.6 | 2000 | 0 | 0 | 12.8 | 21.2 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 0 | 44.45 | 2.3 | 1009.0285 | 4089.1163 | 0 | 90 | 0 | 0.96706 | 7.8 | -16.2 | 0.9 |  |  | 11.274 | 30.3512
46023.5073 | 8.5 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 863 | 892.4 | 5.4 | 6.4 | 47.6 | 58.2 | 5.9 | 90 | 0 | 0 | 168 | 44 | 7.2 | 14.4 | 21.4 | 43.6 | 45.5 | 2000 | 0 | 0 | 12.4 | 20.7 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 0 | 44.55 | 1.9 | 1008.9767 | 4089.2087 | 0 | 90 | 0 | 0.96706 | 8 | -16 | 1 |  |  | 11.2747 | 30.3512
46023.5077 | 9 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 853.2 | 882.6 | 5.1 | 6.1 | 47 | 57.8 | 5.9 | 90 | 0 | 0 | 168 | 44 | 7.1 | 14.6 | 21.4 | 43.8 | 45.3 | 2000 | 0 | 0 | 12.1 | 20.3 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 0 | 44.55 | 1.5 | 1008.9767 | 4089.2087 | 0 | 90 | 0 | 0.96669 | 8.5 | -16.3 | 1.2 |  |  | 11.2755 | 30.3512
46023.508 | 9.5 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 843.4 | 882.6 | 4.8 | 6.1 | 46.4 | 57.3 | 6 | 90 | 0 | 0 | 168 | 43 | 7.1 | 14.8 | 21.3 | 44 | 45.1 | 2000 | 0 | 0 | 11.9 | 20 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 0 | 44.55 | 1.1 | 1008.9767 | 4089.2087 | 0 | 90 | 0 | 0.95559 | 8.7 | -16.5 | 1.4 |  |  | 11.2762 | 30.3512
46023.5084 | 10 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 843.4 | 872.8 | 4.8 | 5.8 | 45.8 | 57.1 | 6 | 90 | 0 | 0 | 168 | 43 | 7 | 15 | 21.3 | 44.2 | 45.1 | 2000 | 0 | 0 | 11.8 | 19.8 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.4 | 0 | 44.65 | 0.9 | 1008.9249 | 4089.3012 | 0 | 90 | 0 | 0.96632 | 9.2 | -16.5 | 1.3 |  |  | 11.277 | 30.3512
46023.5087 | 10.5 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 843.4 | 872.8 | 4.8 | 5.8 | 45.5 | 56.8 | 5.9 | 90 | 0 | 0 | 168 | 43 | 7 | 15.2 | 21.3 | 44.4 | 45 | 2000 | 0 | 0 | 11.6 | 19.5 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.4 | 0 | 44.7 | 0.6 | 1008.8989 | 4089.3475 | 0 | 90 | 0 | 0.96632 | 9.4 | -16.5 | 1.4 |  |  | 11.2777 | 30.3512
46023.5091 | 11 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 843.4 | 872.8 | 4.8 | 5.8 | 45 | 56.5 | 5.9 | 90 | 0 | 0 | 168 | 43 | 7 | 15.4 | 21.3 | 44.4 | 44.8 | 2000 | 0 | 0 | 11.4 | 19.2 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 0 | 44.6 | 0.4 | 1008.9508 | 4089.255 | 0 | 90 | 0 | 0.96632 | 9.6 | -16.5 | 1.7 |  |  | 11.2785 | 30.3512
46023.5094 | 11.5 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 843.4 | 872.8 | 4.8 | 5.8 | 44.4 | 56.4 | 5.9 | 90 | 0 | 0 | 168 | 43 | 6.9 | 15.6 | 21.2 | 44.4 | 44.6 | 2000 | 0 | 0 | 11.3 | 19 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 0 | 44.5 | 0.2 | 1009.0026 | 4089.1625 | 0 | 90 | 0 | 0.96632 | 9.8 | -16.4 | 1.9 |  |  | 11.2792 | 30.3512
46023.5098 | 12 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 843.4 | 872.8 | 4.8 | 5.8 | 43.8 | 56.1 | 5.9 | 90 | 0 | 0 | 168 | 42 | 6.8 | 15.9 | 21.2 | 44.4 | 44.4 | 2000 | 0 | 0 | 11.1 | 18.7 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 0 | 44.4 | 0 | 1009.0544 | 4089.07 | 0 | 90 | 0 | 0.96632 | 10.1 | -16.4 | 2.1 |  |  | 11.28 | 30.3512
46023.5101 | 12.5 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 843.4 | 872.8 | 4.8 | 5.8 | 43.6 | 56 | 5.9 | 90 | 0 | 0 | 168 | 42 | 6.8 | 16 | 21.1 | 44.4 | 44.2 | 2000 | 0 | 0 | 11 | 18.5 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 0 | 44.3 | -0.2 | 1009.106 | 4088.9775 | 0 | 90 | 0 | 0.96632 | 10.2 | -16.3 | 2.3 |  |  | 11.2807 | 30.3512
46023.5105 | 0 | EHS MONO LOWTEMP | Off | Off | On | Off | On | Safety Start | Heat | 0 | 21 | 40 | 22 | 843.4 | 863 | 4.4 | 5.4 | 43.1 | 55.6 | 5.9 | 90 | 0 | 0 | 168 | 43 | 6.7 | 16.2 | 21.1 | 43.3 | 43.1 | 125 | 0 | 0 | 11 | 18.4 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 0 | 43.2 | -0.2 | 1009.671 | 4087.96 | 0 | 90 | 0 | 0.97729 | 10.8 | -16.7 | 3.4 |  |  | 11.2815 | 30.3512
46023.5108 | 0.5 | EHS MONO LOWTEMP | On | Off | On | Off | On | Safety Start | Heat | 0 | 40 | 40 | 40 | 2441.8 | 794.3 | 40.6 | 3.4 | 48.3 | 55.3 | 5.9 | 305 | 3.8 | 14 | 168 | 43 | 7 | 7.1 | 30 | 42.4 | 42.7 | 125 | 0 | 0 | 10.9 | 18.2 | 480 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.5 | 42.55 | 0.3 | 1010.0017 | 4087.3587 | 567.6329 | 305 | 1.8611 | 3.0742 | 3.7 | 10.6 | 3.8 | 4.7303 |  | 11.284 | 30.3559
46023.5112 | 1 | EHS MONO LOWTEMP | On | Off | On | Off | On | Safety Start | Heat | 0 | 40 | 40 | 40 | 2510.5 | 794.3 | 42.3 | 3 | 57.1 | 58.4 | 5.8 | 305 | 3.9 | 14 | 182 | 49 | 3.6 | 3.9 | 38.8 | 41.6 | 43.3 | 348 | 80 | 700 | 10.9 | 18.2 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.5 | 42.45 | 1.7 | 1010.0523 | 4087.2663 | 3216.6749 | 305 | 10.5465 | 3.1606 | 0.9 | 3.5 | 3.2 | 26.8056 |  | 11.2866 | 30.3827
46023.5115 | 1.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Safety Start | Heat | 0 | 34 | 25 | 35 | 2461.5 | 813.9 | 41.4 | 3.7 | 59.8 | 61.4 | 5.7 | 2036 | 4.2 | 15 | 182 | 52 | 4 | 4.1 | 39.8 | 40.6 | 42.5 | 219 | 150 | 2000 | 13.9 | 23 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.5 | 41.55 | 1.9 | 1010.5057 | 4086.4338 | 3595.9885 | 2036 | 1.7662 | 3.0243 | 0.4 | 1.6 | 4 | 29.9666 |  | 11.3035 | 30.4127
46023.5119 | 2 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Safety Start | Heat | 0 | 25 | 25 | 25 | 2490.9 | 774.7 | 41.8 | 2.3 | 61.2 | 64.5 | 5.6 | 2036 | 3.1 | 16 | 182 | 55 | 2.7 | 3 | 41.1 | 40.5 | 43.1 | 219 | 156 | 2000 | 21.4 | 35.8 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.7 | 27.7 | 41.8 | 2.6 | 1010.3802 | 4086.665 | 4956.2791 | 2036 | 2.4343 | 3.2153 | 0.7 | 0.7 | 3.6 | 41.3023 |  | 11.3205 | 30.454 | 24.3432
46023.5122 | 2.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Safety Start | Heat | 0 | 25 | 25 | 25 | 2510.5 | 784.5 | 42.2 | 2.7 | 60.3 | 65.7 | 5.5 | 2036 | 3.1 | 16 | 182 | 56 | 3 | 4.8 | 41 | 40.8 | 43.3 | 219 | 156 | 2000 | 26.2 | 37.7 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.5 | 42.05 | 2.5 | 1010.2544 | 4086.8962 | 4730.9223 | 2036 | 2.3236 | 3.2001 | 2.1 | 1.2 | 3.5 | 39.4244 |  | 11.3375 | 30.4934 | 23.2364
46023.5126 | 3 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Safety Start | Heat | 0 | 25 | 25 | 25 | 2520.3 | 784.5 | 42.3 | 2.7 | 59.5 | 65.7 | 5.5 | 1747 | 3.1 | 16 | 182 | 57 | 3.1 | 6.1 | 41.1 | 40.8 | 43.3 | 219 | 156 | 2000 | 26.6 | 38.4 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.9 | 42.05 | 2.5 | 1010.2544 | 4086.8962 | 4799.7357 | 1747 | 2.7474 | 3.2126 | 3.4 | 1.2 | 3.5 | 39.9978 |  | 11.352 | 30.5334 | 27.4742
46023.5129 | 3.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2530.1 | 784.5 | 42.5 | 2.7 | 59.4 | 65.7 | 5.5 | 1747 | 3.1 | 16 | 182 | 58 | 3.3 | 4.2 | 41.3 | 40.8 | 43.3 | 219 | 161 | 2000 | 27.1 | 38.7 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.9 | 42.05 | 2.5 | 1010.2544 | 4086.8962 | 4799.7357 | 1747 | 2.7474 | 3.2251 | 1.5 | 1.2 | 3.5 | 39.9978 |  | 11.3666 | 30.5734 | 27.4742
46023.5133 | 4 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2530.1 | 784.5 | 42.5 | 2.7 | 59.4 | 65.7 | 5.5 | 1594 | 3.1 | 16 | 182 | 58 | 3.2 | 3.5 | 41.5 | 41 | 43.5 | 218 | 161 | 2000 | 27.3 | 38.7 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.5 | 42.25 | 2.5 | 1010.1535 | 4087.0813 | 4730.6638 | 1594 | 2.9678 | 3.2251 | 0.8 | 1 | 3.3 | 39.4222 |  | 11.3799 | 30.6129 | 29.6779
46023.5136 | 4.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 22 | 22 | 21 | 2539.9 | 784.5 | 42.6 | 2.7 | 59.5 | 66 | 5.5 | 1594 | 3.1 | 16 | 182 | 58 | 3.3 | 3.3 | 41.5 | 41.1 | 43.6 | 217 | 0 | 0 | 27.7 | 38.7 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.5 | 42.35 | 2.5 | 1010.1029 | 4087.1737 | 4730.5342 | 1594 | 2.9677 | 3.2376 | 0.6 | 1.1 | 3.2 | 39.4211 |  | 11.3932 | 30.6523 | 29.6771
46023.5139 | 5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 22 | 22 | 22 | 2539.9 | 794.3 | 42.6 | 3 | 59.7 | 66.2 | 5.5 | 1606 | 2.4 | 14 | 182 | 58 | 3.4 | 3.4 | 41.5 | 41.1 | 43.5 | 216 | 0 | 0 | 21.8 | 38.4 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.5 | 42.3 | 2.4 | 1010.1282 | 4087.1275 | 4541.3751 | 1606 | 2.8278 | 3.1977 | 0.4 | 1.1 | 3.3 | 37.8448 |  | 11.4065 | 30.6901 | 28.2776
46023.5143 | 5.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 27 | 24 | 2549.7 | 794.3 | 42.8 | 3 | 59.4 | 66.2 | 5.5 | 1606 | 2.5 | 14 | 180 | 57 | 3.4 | 3.4 | 41.5 | 41.1 | 43.5 | 215 | 0 | 0 | 18.3 | 37.1 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.5 | 42.3 | 2.4 | 1010.1282 | 4087.1275 | 4541.3751 | 1606 | 2.8278 | 3.21 | 0.4 | 1.3 | 3.3 | 37.8448 |  | 11.4199 | 30.728 | 28.2776
46023.5146 | 6 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 27 | 26 | 2569.3 | 784.5 | 43.1 | 2.7 | 59.1 | 66.2 | 5.4 | 1297 | 2.7 | 14 | 180 | 57 | 3.2 | 3.2 | 41.5 | 41.3 | 43.6 | 216 | 0 | 0 | 16.6 | 36.2 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.7 | 42.45 | 2.3 | 1010.0523 | 4087.2663 | 4383.6226 | 1297 | 3.3798 | 3.2751 | 0.5 | 1.6 | 3.2 | 36.5302 |  | 11.4307 | 30.7645 | 33.7982
46023.515 | 6.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 27 | 23 | 27 | 2588.9 | 774.7 | 43.4 | 2.3 | 58.8 | 66.2 | 5.4 | 1297 | 2.9 | 14 | 180 | 58 | 3 | 3 | 41.5 | 41.3 | 44.2 | 215 | 0 | 0 | 15.8 | 35.1 | 480 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 28.1 | 42.75 | 2.9 | 1009.9002 | 4087.5437 | 5606.5271 | 1297 | 4.3227 | 3.3418 | 0.7 | 1.9 | 2.6 | 46.7211 |  | 11.4415 | 30.8112 | 43.2269 | 32.6515
46023.5153 | 7 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 23 | 25 | 2588.9 | 774.7 | 43.4 | 2.3 | 58.8 | 66.2 | 5.5 | 1382 | 2.8 | 14 | 180 | 58 | 2.9 | 2.8 | 41.5 | 41.5 | 44.2 | 215 | 0 | 0 | 15.9 | 33.7 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 28.1 | 42.85 | 2.7 | 1009.8493 | 4087.6363 | 5219.7255 | 1382 | 3.7769 | 3.3418 | 0.5 | 1.9 | 2.6 | 43.4977 |  | 11.4531 | 30.8547 | 37.7694 | 34.2699
46023.5157 | 7.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 23 | 27 | 23 | 2579.1 | 774.7 | 43.2 | 2.3 | 58.8 | 66.5 | 5.5 | 1382 | 2.6 | 14 | 182 | 58 | 3 | 3 | 41.3 | 41.5 | 44.2 | 214 | 0 | 0 | 16.6 | 32.6 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.9 | 42.85 | 2.7 | 1009.8493 | 4087.6363 | 5182.5744 | 1382 | 3.7501 | 3.3292 | 0.7 | 1.9 | 2.6 | 43.1881 |  | 11.4646 | 30.8979 | 37.5005 | 36.1145
46023.516 | 8 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 27 | 25 | 2588.9 | 784.5 | 43.4 | 2.7 | 58.8 | 66.7 | 5.4 | 1454 | 2.7 | 14 | 182 | 58 | 3.1 | 3.1 | 41.3 | 41.5 | 44.2 | 213 | 0 | 0 | 17.6 | 31.4 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.7 | 42.85 | 2.7 | 1009.8493 | 4087.6363 | 5145.4234 | 1454 | 3.5388 | 3.3001 | 0.4 | 2.1 | 2.6 | 42.8785 |  | 11.4767 | 30.9408 | 35.3881 | 37.5366
46023.5164 | 8.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2588.9 | 774.7 | 43.4 | 2.3 | 59 | 66.8 | 5.4 | 1454 | 2.8 | 14 | 182 | 58 | 3 | 3 | 41.3 | 41.6 | 44.2 | 214 | 0 | 0 | 18.3 | 30.8 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.9 | 42.9 | 2.6 | 1009.8239 | 4087.6825 | 4990.558 | 1454 | 3.4323 | 3.3418 | 0.7 | 2.1 | 2.6 | 41.588 |  | 11.4888 | 30.9824 | 34.323 | 37.6416
46023.5167 | 9 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2608.6 | 774.7 | 43.7 | 2.3 | 59 | 67.1 | 5.4 | 1372 | 2.9 | 14 | 182 | 58 | 2.9 | 2.8 | 41.3 | 41.6 | 44.6 | 213 | 0 | 0 | 19.3 | 30.1 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.9 | 43.1 | 3 | 1009.722 | 4087.8675 | 5758.0158 | 1372 | 4.1968 | 3.3672 | 0.5 | 2.4 | 2.2 | 47.9835 |  | 11.5002 | 31.0304 | 41.968 | 37.3898
46023.5171 | 9.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 27 | 21 | 27 | 2618.4 | 764.9 | 43.8 | 2 | 59.2 | 67.5 | 5.4 | 1372 | 2.9 | 14 | 182 | 58 | 2.8 | 2.7 | 40.6 | 41.8 | 44.8 | 213 | 0 | 0 | 20.2 | 29.3 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 28.1 | 43.3 | 3 | 1009.6199 | 4088.0525 | 5798.9679 | 1372 | 4.2267 | 3.4232 | 0.7 | 3.2 | 2 | 48.3247 |  | 11.5117 | 31.0787 | 42.2665 | 38.2892
46023.5174 | 10 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 21 | 25 | 2618.4 | 774.7 | 43.8 | 2.3 | 59.7 | 68.2 | 5.5 | 1508 | 2.8 | 14 | 180 | 58 | 2.8 | 2.7 | 40.3 | 41.8 | 44.8 | 212 | 0 | 0 | 21 | 28.6 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.9 | 43.3 | 3 | 1009.6199 | 4088.0525 | 5757.6941 | 1508 | 3.8181 | 3.3799 | 0.4 | 3.5 | 2 | 47.9808 |  | 11.5242 | 31.1267 | 38.181 | 38.4253
46023.5178 | 10.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 24 | 24 | 2608.6 | 774.7 | 43.7 | 2.3 | 60.1 | 69.1 | 5.5 | 1508 | 2.6 | 14 | 180 | 58 | 3 | 2.9 | 40.1 | 41.8 | 44.6 | 211 | 0 | 0 | 21.6 | 28 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.9 | 43.2 | 2.8 | 1009.671 | 4087.96 | 5373.9981 | 1508 | 3.5637 | 3.3672 | 0.6 | 3.6 | 2.2 | 44.7833 |  | 11.5368 | 31.1714 | 35.6366 | 38.475
46023.5181 | 11 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 24 | 24 | 2608.6 | 774.7 | 43.7 | 2.3 | 60.5 | 69.4 | 5.5 | 1473 | 2.6 | 14 | 180 | 58 | 3 | 3 | 40.1 | 42 | 44.6 | 210 | 0 | 0 | 22 | 27.6 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.9 | 43.3 | 2.6 | 1009.6199 | 4088.0525 | 4990.0015 | 1473 | 3.3876 | 3.3672 | 0.7 | 3.6 | 2.2 | 41.5833 |  | 11.5491 | 31.213 | 33.8765 | 38.3857
46023.5185 | 11.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 27 | 24 | 2608.6 | 784.5 | 43.7 | 2.7 | 60.8 | 69.8 | 5.5 | 1473 | 2.6 | 14 | 180 | 58 | 3 | 3 | 40.1 | 42 | 44.6 | 209 | 0 | 0 | 22.4 | 27.1 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.9 | 43.3 | 2.6 | 1009.6199 | 4088.0525 | 4990.0015 | 1473 | 3.3876 | 3.3252 | 0.3 | 3.6 | 2.2 | 41.5833 |  | 11.5614 | 31.2546 | 33.8765 | 36.7674
46023.5188 | 12 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 27 | 26 | 2618.4 | 774.7 | 43.8 | 2.3 | 61 | 70.1 | 5.5 | 1378 | 2.7 | 14 | 180 | 58 | 3 | 3 | 40.3 | 42 | 44.8 | 208 | 0 | 0 | 22.8 | 26.6 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.7 | 43.4 | 2.8 | 1009.5688 | 4088.145 | 5335.1761 | 1378 | 3.8717 | 3.3799 | 0.7 | 3.5 | 2 | 44.4598 |  | 11.5728 | 31.2991 | 38.7168 | 36.0575
46023.5192 | 12.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 27 | 21 | 27 | 2657.6 | 774.7 | 44.5 | 2.3 | 61.1 | 70.4 | 5.5 | 1378 | 2.9 | 15 | 182 | 58 | 2.9 | 2.8 | 40.3 | 42.1 | 45 | 209 | 0 | 0 | 23.1 | 26.3 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 28.1 | 43.55 | 2.9 | 1009.492 | 4088.2838 | 5605.2756 | 1378 | 4.0677 | 3.4305 | 0.5 | 4.2 | 1.8 | 46.7106 |  | 11.5843 | 31.3458 | 40.6769 | 36.5566
46023.5195 | 13 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 21 | 25 | 2657.6 | 774.7 | 44.5 | 2.3 | 61.4 | 70.5 | 5.5 | 1434 | 2.8 | 14 | 182 | 58 | 2.8 | 2.7 | 40.3 | 42.1 | 45.1 | 209 | 0 | 0 | 23.2 | 26.1 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 28.1 | 43.6 | 3 | 1009.4664 | 4088.33 | 5798.4794 | 1434 | 4.0436 | 3.4305 | 0.4 | 4.2 | 1.7 | 48.3207 |  | 11.5963 | 31.3941 | 40.4357 | 37.5165
46023.5198 | 13.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 23 | 23 | 23 | 2638 | 774.7 | 44.2 | 2.3 | 61.7 | 71 | 5.5 | 1434 | 2.7 | 15 | 182 | 59 | 2.9 | 2.8 | 40.3 | 42.2 | 45 | 208 | 0 | 0 | 23.3 | 25.8 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 28.1 | 43.6 | 2.8 | 1009.4664 | 4088.33 | 5411.9141 | 1434 | 3.774 | 3.4052 | 0.5 | 3.9 | 1.8 | 45.0993 |  | 11.6082 | 31.4392 | 37.74 | 38.2892
46023.5202 | 14 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 23 | 23 | 23 | 2628.2 | 784.5 | 44 | 2.7 | 61.8 | 71.4 | 5.5 | 1486 | 2.5 | 14 | 182 | 58 | 3.1 | 3 | 40.3 | 42.2 | 45 | 208 | 0 | 0 | 23.5 | 25.5 | 480 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.5 | 43.6 | 2.8 | 1009.4664 | 4088.33 | 5296.3572 | 1486 | 3.5642 | 3.3502 | 0.3 | 3.7 | 1.8 | 44.1363 |  | 11.6206 | 31.4833 | 35.6417 | 38.6422
46023.5205 | 14.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 23 | 25 | 23 | 2628.2 | 784.5 | 44 | 2.7 | 62 | 71.5 | 5.5 | 1486 | 2.5 | 14 | 182 | 58 | 3.1 | 3.1 | 40.5 | 42.4 | 45 | 207 | 0 | 0 | 23.5 | 25.3 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.9 | 43.7 | 2.6 | 1009.415 | 4088.4225 | 4989.4405 | 1486 | 3.3576 | 3.3502 | 0.4 | 3.5 | 1.8 | 41.5787 |  | 11.633 | 31.5249 | 33.5763 | 37.6141
46023.5209 | 15 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2638 | 784.5 | 44.2 | 2.7 | 62 | 71.7 | 5.5 | 1350 | 2.7 | 14 | 182 | 58 | 3.1 | 3.1 | 40.5 | 42.4 | 45 | 208 | 0 | 0 | 23.6 | 25.2 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.9 | 43.7 | 2.6 | 1009.415 | 4088.4225 | 4989.4405 | 1350 | 3.6959 | 3.3627 | 0.4 | 3.7 | 1.8 | 41.5787 |  | 11.6442 | 31.5665 | 36.9588 | 36.8705
46023.5212 | 15.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 27 | 25 | 2638 | 774.7 | 44.2 | 2.3 | 62.1 | 71.7 | 5.5 | 1350 | 2.7 | 14 | 182 | 58 | 3.1 | 3 | 40.6 | 42.2 | 45.1 | 207 | 0 | 0 | 23.6 | 25 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.9 | 43.65 | 2.9 | 1009.4407 | 4088.3762 | 5565.2236 | 1350 | 4.1224 | 3.4052 | 0.7 | 3.6 | 1.7 | 46.3769 |  | 11.6555 | 31.6129 | 41.2239 | 37.0281
46023.5216 | 16 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2657.6 | 774.7 | 44.5 | 2.3 | 62.1 | 71.7 | 5.5 | 1388 | 2.8 | 15 | 182 | 59 | 3 | 3 | 40.8 | 42.2 | 45.1 | 207 | 0 | 0 | 23.7 | 24.8 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.9 | 43.65 | 2.9 | 1009.4407 | 4088.3762 | 5565.2236 | 1388 | 4.0095 | 3.4305 | 0.7 | 3.7 | 1.7 | 46.3769 |  | 11.6671 | 31.6592 | 40.0953 | 37.4992
46023.5219 | 16.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 27 | 26 | 27 | 2677.2 | 774.7 | 44.7 | 2.3 | 62.2 | 71.7 | 5.5 | 1490 | 3 | 15 | 182 | 59 | 2.8 | 2.8 | 40.6 | 42.4 | 45.3 | 208 | 0 | 0 | 23.7 | 24.7 | 480 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.9 | 43.85 | 2.9 | 1009.338 | 4088.5613 | 5564.9091 | 1490 | 3.7348 | 3.4558 | 0.5 | 4.1 | 1.5 | 46.3742 |  | 11.6795 | 31.7056 | 37.3484 | 37.8405
46023.5223 | 17 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2677.2 | 774.7 | 44.7 | 2.3 | 62.5 | 72.1 | 5.5 | 1490 | 2.9 | 15 | 182 | 59 | 2.8 | 2.7 | 40.6 | 42.4 | 45.5 | 208 | 0 | 0 | 23.7 | 24.6 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.9 | 43.95 | 3.1 | 1009.2865 | 4088.6537 | 5948.5274 | 1490 | 3.9923 | 3.4558 | 0.4 | 4.1 | 1.3 | 49.5711 |  | 11.6919 | 31.7552 | 39.923 | 39.1099
46023.5226 | 17.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 25 | 26 | 2687 | 774.7 | 44.9 | 2.3 | 62.7 | 72.5 | 5.5 | 1523 | 2.9 | 15 | 182 | 59 | 2.8 | 2.8 | 40.6 | 42.5 | 45.5 | 207 | 0 | 0 | 23.7 | 24.5 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 28.1 | 44 | 3 | 1009.2608 | 4088.7 | 5797.8233 | 1523 | 3.8068 | 3.4684 | 0.5 | 4.3 | 1.3 | 48.3152 |  | 11.7046 | 31.8035 | 38.0684 | 39.3318
46023.523 | 18 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2687 | 774.7 | 44.9 | 2.3 | 62.8 | 72.7 | 5.5 | 1523 | 2.8 | 15 | 182 | 59 | 2.9 | 2.8 | 40.6 | 42.5 | 45.5 | 207 | 0 | 0 | 23.7 | 24.5 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.7 | 44 | 3 | 1009.2608 | 4088.7 | 5715.292 | 1523 | 3.7527 | 3.4684 | 0.5 | 4.3 | 1.3 | 47.6274 |  | 11.7173 | 31.8511 | 37.5265 | 38.5923
46023.5233 | 18.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 27 | 25 | 2687 | 774.7 | 44.9 | 2.3 | 63.1 | 73.1 | 5.5 | 1480 | 2.8 | 15 | 182 | 59 | 3 | 3 | 40.6 | 42.5 | 45.3 | 207 | 0 | 0 | 23.8 | 24.4 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.7 | 43.9 | 2.8 | 1009.3123 | 4088.6075 | 5334.4239 | 1480 | 3.6043 | 3.4684 | 0.7 | 4.3 | 1.5 | 44.4535 |  | 11.7296 | 31.8956 | 36.0434 | 37.782
46023.5237 | 19 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2696.8 | 774.7 | 45 | 2.3 | 63.4 | 73.5 | 5.5 | 1480 | 2.9 | 15 | 180 | 59 | 3 | 3 | 40.6 | 42.5 | 45.5 | 207 | 0 | 0 | 23.8 | 24.4 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 28.1 | 44 | 3 | 1009.2608 | 4088.7 | 5797.8233 | 1480 | 3.9174 | 3.4811 | 0.7 | 4.4 | 1.3 | 48.3152 |  | 11.7419 | 31.9439 | 39.1745 | 38.1472
46023.524 | 19.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 27 | 26 | 27 | 2716.4 | 774.7 | 45.3 | 2.3 | 63.8 | 74 | 5.5 | 1514 | 3 | 15 | 180 | 59 | 2.9 | 2.8 | 40.6 | 42.5 | 45.6 | 207 | 0 | 0 | 23.8 | 24.3 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.9 | 44.05 | 3.1 | 1009.235 | 4088.7463 | 5948.3584 | 1514 | 3.9289 | 3.5064 | 0.5 | 4.7 | 1.2 | 49.5697 |  | 11.7546 | 31.9935 | 39.289 | 38.0204
46023.5244 | 20 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 26 | 26 | 2726.2 | 774.7 | 45.5 | 2.3 | 64.4 | 74.5 | 5.5 | 1514 | 2.9 | 15 | 180 | 59 | 2.8 | 2.8 | 40.8 | 42.7 | 45.6 | 207 | 0 | 0 | 23.8 | 24.3 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.9 | 44.15 | 2.9 | 1009.1835 | 4088.8387 | 5564.435 | 1514 | 3.6753 | 3.519 | 0.5 | 4.7 | 1.2 | 46.3703 |  | 11.7672 | 32.0398 | 36.7532 | 37.7573
46023.5247 | 20.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 28 | 26 | 2745.8 | 774.7 | 45.8 | 2.3 | 64.5 | 74.8 | 5.5 | 1551 | 2.9 | 15 | 180 | 60 | 2.9 | 2.8 | 40.8 | 42.8 | 45.6 | 207 | 0 | 0 | 23.8 | 24.3 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.9 | 44.2 | 2.8 | 1009.1577 | 4088.885 | 5372.4813 | 1551 | 3.4639 | 3.5443 | 0.5 | 5 | 1.2 | 44.7707 |  | 11.7801 | 32.0846 | 34.6388 | 37.1798
46023.5251 | 21 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2765.5 | 774.7 | 46.1 | 2.3 | 65.1 | 75.2 | 5.5 | 1551 | 3 | 15 | 180 | 60 | 2.8 | 2.8 | 40.8 | 42.7 | 45.6 | 207 | 0 | 0 | 23.8 | 24.3 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.9 | 44.15 | 2.9 | 1009.1835 | 4088.8387 | 5564.435 | 1551 | 3.5876 | 3.5698 | 0.5 | 5.3 | 1.2 | 46.3703 |  | 11.793 | 32.131 | 35.8764 | 37.1464
46023.5254 | 21.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 28 | 27 | 28 | 2794.9 | 764.9 | 46.5 | 2 | 65.7 | 76 | 5.5 | 1596 | 3.2 | 15 | 183 | 60 | 2.7 | 2.6 | 41 | 42.8 | 45.8 | 210 | 0 | 0 | 23.8 | 24.2 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.7 | 44.3 | 3 | 1009.106 | 4088.9775 | 5714.8035 | 1596 | 3.5807 | 3.6539 | 0.6 | 5.5 | 1 | 47.6234 |  | 11.8063 | 32.1786 | 35.807 | 36.4729
46023.5258 | 22 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2824.3 | 764.9 | 46.9 | 2 | 66.5 | 76.8 | 5.5 | 1596 | 3.1 | 16 | 183 | 60 | 2.7 | 2.7 | 41 | 42.8 | 45.8 | 210 | 0 | 0 | 23.8 | 24.2 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.7 | 44.3 | 3 | 1009.106 | 4088.9775 | 5714.8035 | 1596 | 3.5807 | 3.6924 | 0.7 | 5.9 | 1 | 47.6234 |  | 11.8196 | 32.2262 | 35.807 | 35.7765
46023.5261 | 22.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 27 | 28 | 27 | 2843.9 | 774.7 | 47.2 | 2.3 | 67.2 | 77.8 | 5.6 | 1648 | 3.1 | 15 | 183 | 60 | 2.8 | 2.7 | 41 | 42.8 | 45.8 | 215 | 0 | 0 | 23.8 | 24.2 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.8 | 27.7 | 44.3 | 3 | 1009.106 | 4088.9775 | 5714.8035 | 1648 | 3.4677 | 3.671 | 0.4 | 6.2 | 1 | 47.6234 |  | 11.8334 | 32.2739 | 34.6772 | 35.3613
46023.5264 | 23 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2883.1 | 764.9 | 47.8 | 2 | 67.8 | 78.4 | 5.6 | 1648 | 3.3 | 16 | 183 | 61 | 2.8 | 2.8 | 41 | 43 | 45.8 | 220 | 0 | 0 | 23.8 | 24.2 | 480 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.7 | 27.7 | 44.4 | 2.8 | 1009.0544 | 4089.07 | 5333.664 | 1648 | 3.2364 | 3.7693 | 0.8 | 6.8 | 0.9 | 44.4472 |  | 11.8471 | 32.3183 | 32.3645 | 34.9064
46023.5268 | 23.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 28 | 27 | 28 | 2922.4 | 764.9 | 48.3 | 2 | 68.8 | 79.3 | 5.6 | 1648 | 3.3 | 16 | 182 | 61 | 2.8 | 2.7 | 41.1 | 43.1 | 46 | 225 | 0 | 0 | 23.8 | 24.2 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.7 | 27.7 | 44.55 | 2.9 | 1008.9767 | 4089.2087 | 5523.9144 | 1648 | 3.3519 | 3.8206 | 0.7 | 7.2 | 0.7 | 46.0326 |  | 11.8608 | 32.3643 | 33.5189 | 34.4349
46023.5271 | 24 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2922.4 | 774.7 | 48.3 | 2.3 | 69.8 | 80.4 | 5.6 | 1692 | 3.2 | 16 | 182 | 61 | 2.8 | 2.7 | 41.3 | 43.1 | 46 | 228 | 0 | 0 | 23.8 | 24.2 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.7 | 27.9 | 44.55 | 2.9 | 1008.9767 | 4089.2087 | 5563.7982 | 1692 | 3.2883 | 3.7723 | 0.4 | 7 | 0.7 | 46.365 |  | 11.8749 | 32.4107 | 32.883 | 33.8501
46023.5275 | 24.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2892.9 | 774.7 | 47.9 | 2.3 | 70.4 | 81.4 | 5.6 | 1692 | 3.2 | 16 | 182 | 61 | 2.9 | 2.8 | 41.3 | 43.1 | 46.1 | 229 | 0 | 0 | 23.8 | 24.2 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.7 | 27.9 | 44.6 | 3 | 1008.9508 | 4089.255 | 5755.5706 | 1692 | 3.4016 | 3.7342 | 0.5 | 6.6 | 0.6 | 47.9631 |  | 11.889 | 32.4587 | 34.0164 | 33.492
46023.5278 | 25 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 27 | 27 | 27 | 2863.5 | 774.7 | 47.5 | 2.3 | 71 | 82.3 | 5.6 | 1706 | 3.2 | 16 | 182 | 61 | 2.9 | 2.9 | 41.5 | 43.3 | 46.1 | 230 | 0 | 0 | 23.8 | 24.2 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.7 | 28.1 | 44.7 | 2.8 | 1008.8989 | 4089.3475 | 5410.2182 | 1706 | 3.1713 | 3.6963 | 0.6 | 6 | 0.6 | 45.0852 |  | 11.9032 | 32.5037 | 31.7129 | 32.8991
46023.5282 | 25.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 27 | 28 | 27 | 2863.5 | 774.7 | 47.5 | 2.3 | 71.2 | 82.6 | 5.6 | 1706 | 3.2 | 16 | 182 | 61 | 3 | 2.9 | 41.5 | 43.3 | 46.1 | 231 | 0 | 0 | 23.8 | 24.2 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.7 | 27.9 | 44.7 | 2.8 | 1008.8989 | 4089.3475 | 5371.7113 | 1706 | 3.1487 | 3.6963 | 0.6 | 6 | 0.6 | 44.7643 |  | 11.9175 | 32.5485 | 31.4872 | 32.7237
46023.5285 | 26 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2863.5 | 774.7 | 47.5 | 2.3 | 71.5 | 83 | 5.7 | 1665 | 3.3 | 16 | 183 | 61 | 3 | 2.9 | 41.5 | 43.3 | 46.3 | 232 | 0 | 0 | 23.8 | 24.2 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.6 | 28.1 | 44.8 | 3 | 1008.847 | 4089.44 | 5796.4951 | 1665 | 3.4814 | 3.6963 | 0.6 | 6 | 0.3 | 48.3041 |  | 11.9313 | 32.5968 | 34.8138 | 32.9826
46023.5289 | 26.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 28 | 22 | 28 | 2863.5 | 774.7 | 47.5 | 2.3 | 71.8 | 83.1 | 5.7 | 1665 | 3.3 | 16 | 183 | 61 | 2.9 | 2.9 | 41.5 | 43.3 | 46.5 | 233 | 0 | 0 | 24 | 24.3 | 480 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.6 | 28.1 | 44.9 | 3.2 | 1008.795 | 4089.5325 | 6182.7494 | 1665 | 3.7134 | 3.6963 | 0.6 | 6 | 0.1 | 51.5229 |  | 11.9452 | 32.6483 | 37.1336 | 33.8328
46023.5292 | 27 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 22 | 26 | 2853.7 | 774.7 | 47.4 | 2.3 | 72 | 83.2 | 5.7 | 1686 | 3.2 | 16 | 183 | 61 | 3 | 2.8 | 41.6 | 43.6 | 46.6 | 233 | 0 | 0 | 24 | 24.3 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.6 | 27.7 | 45.1 | 3 | 1008.6909 | 4089.7175 | 5713.4863 | 1686 | 3.3888 | 3.6836 | 0.5 | 5.8 | 0 | 47.6124 |  | 11.9593 | 32.696 | 33.8878 | 33.8071
46023.5296 | 27.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 23 | 25 | 2804.7 | 784.5 | 46.8 | 2.7 | 71.8 | 83.3 | 5.7 | 1686 | 2.9 | 16 | 183 | 61 | 3.1 | 3 | 41.6 | 43.5 | 46.5 | 233 | 0 | 0 | 24 | 24.3 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.6 | 27.9 | 45 | 3 | 1008.743 | 4089.625 | 5754.9059 | 1686 | 3.4133 | 3.5751 | 0.3 | 5.2 | 0.1 | 47.9575 |  | 11.9733 | 32.7439 | 34.1335 | 34.2912
46023.5299 | 28 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 23 | 23 | 23 | 2755.7 | 794.3 | 45.9 | 3 | 71.4 | 83.1 | 5.7 | 1649 | 2.7 | 15 | 180 | 61 | 3.3 | 3.2 | 41.8 | 43.5 | 46.3 | 233 | 0 | 0 | 24.1 | 24.4 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.6 | 27.9 | 44.9 | 2.8 | 1008.795 | 4089.5325 | 5371.4011 | 1649 | 3.2574 | 3.4693 | 0.2 | 4.1 | 0.3 | 44.7617 |  | 11.987 | 32.7887 | 32.5737 | 34.5085
46023.5303 | 28.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 23 | 25 | 23 | 2736 | 794.3 | 45.6 | 3 | 71.1 | 82.5 | 5.7 | 1649 | 2.7 | 15 | 180 | 61 | 3.5 | 3.4 | 41.8 | 43.6 | 46.3 | 229 | 0 | 0 | 24.1 | 24.4 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.6 | 27.7 | 44.95 | 2.7 | 1008.769 | 4089.5788 | 5142.3614 | 1649 | 3.1185 | 3.4445 | 0.4 | 3.8 | 0.3 | 42.853 |  | 12.0008 | 32.8315 | 31.1847 | 33.7827
46023.5306 | 29 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 24 | 2736 | 794.3 | 45.6 | 3 | 70.7 | 81.7 | 5.7 | 1438 | 2.8 | 15 | 180 | 60 | 3.6 | 3.5 | 41.8 | 43.6 | 46.3 | 229 | 0 | 0 | 24.1 | 24.4 | 480 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.6 | 27.7 | 44.95 | 2.7 | 1008.769 | 4089.5788 | 5142.3614 | 1438 | 3.5761 | 3.4445 | 0.5 | 3.8 | 0.3 | 42.853 |  | 12.0128 | 32.8744 | 35.7605 | 33.508
46023.531 | 29.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 23 | 25 | 2736 | 784.5 | 45.6 | 2.7 | 70.1 | 80.7 | 5.7 | 1438 | 2.9 | 15 | 180 | 60 | 3.4 | 3.3 | 41.8 | 43.6 | 46.5 | 228 | 0 | 0 | 24.1 | 24.4 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.6 | 27.5 | 45.05 | 2.9 | 1008.717 | 4089.6712 | 5483.2388 | 1438 | 3.8131 | 3.4876 | 0.6 | 3.8 | 0.1 | 45.6937 |  | 12.0248 | 32.9201 | 38.131 | 34.3567
46023.5313 | 30 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 23 | 23 | 24 | 2736 | 784.5 | 45.6 | 2.7 | 69.7 | 80 | 5.7 | 1441 | 2.7 | 15 | 180 | 60 | 3.4 | 3.3 | 42 | 43.6 | 46.5 | 228 | 0 | 0 | 24.1 | 24.4 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.6 | 27.5 | 45.05 | 2.9 | 1008.717 | 4089.6712 | 5483.2388 | 1441 | 3.8052 | 3.4876 | 0.6 | 3.6 | 0.1 | 45.6937 |  | 12.0368 | 32.9658 | 38.0516 | 35.1403
46023.5317 | 30.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 23 | 24 | 23 | 2716.4 | 794.3 | 45.3 | 3 | 69.1 | 79.2 | 5.7 | 1441 | 2.6 | 15 | 180 | 60 | 3.5 | 3.4 | 42.7 | 43.8 | 46.5 | 226 | 0 | 0 | 24.1 | 24.5 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.6 | 27.9 | 45.15 | 2.7 | 1008.6648 | 4089.7638 | 5179.1898 | 1441 | 3.5942 | 3.4199 | 0.4 | 2.6 | 0.1 | 43.1599 |  | 12.0488 | 33.0089 | 35.9416 | 35.8139
46023.532 | 31 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 24 | 24 | 2726.2 | 794.3 | 45.5 | 3 | 68.4 | 78.2 | 5.7 | 1442 | 2.7 | 15 | 180 | 60 | 3.6 | 3.5 | 43.3 | 43.6 | 46.3 | 227 | 0 | 0 | 24.1 | 24.5 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.6 | 27.7 | 44.95 | 2.7 | 1008.769 | 4089.5788 | 5142.3614 | 1442 | 3.5661 | 3.4322 | 0.5 | 2.2 | 0.3 | 42.853 |  | 12.0608 | 33.0518 | 35.6613 | 36.7092
46023.5324 | 31.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 25 | 24 | 2726.2 | 794.3 | 45.5 | 3 | 67.7 | 77.1 | 5.7 | 1442 | 2.8 | 15 | 180 | 60 | 3.6 | 3.5 | 43.6 | 43.8 | 46.5 | 227 | 0 | 0 | 24.1 | 24.5 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.6 | 28.1 | 45.15 | 2.7 | 1008.6648 | 4089.7638 | 5216.3166 | 1442 | 3.6174 | 3.4322 | 0.5 | 1.9 | 0.1 | 43.4693 |  | 12.0728 | 33.0952 | 36.1742 | 36.792
46023.5327 | 32 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2736 | 794.3 | 45.6 | 3 | 66.8 | 76.1 | 5.7 | 1417 | 2.9 | 15 | 180 | 60 | 3.5 | 3.4 | 43.6 | 43.8 | 46.5 | 226 | 0 | 0 | 24.2 | 24.6 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.6 | 28.1 | 45.15 | 2.7 | 1008.6648 | 4089.7638 | 5216.3166 | 1417 | 3.6812 | 3.4445 | 0.4 | 2 | 0.1 | 43.4693 |  | 12.0846 | 33.1387 | 36.8124 | 36.5282
46023.533 | 32.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 23 | 25 | 2745.8 | 794.3 | 45.8 | 3 | 66.2 | 75.4 | 5.8 | 1417 | 2.9 | 15 | 180 | 61 | 3.4 | 3.4 | 43.6 | 43.8 | 46.6 | 227 | 0 | 0 | 24.3 | 24.7 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.6 | 28.1 | 45.2 | 2.8 | 1008.6388 | 4089.81 | 5409.4348 | 1417 | 3.8175 | 3.4569 | 0.4 | 2.2 | 0 | 45.0786 |  | 12.0964 | 33.1838 | 38.1753 | 36.553
46023.5334 | 33 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 23 | 23 | 24 | 2736 | 794.3 | 45.6 | 3 | 65.5 | 74.5 | 5.8 | 1472 | 2.8 | 15 | 180 | 61 | 3.4 | 3.4 | 43.8 | 43.8 | 46.6 | 226 | 0 | 0 | 24.4 | 24.8 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 28.1 | 45.2 | 2.8 | 1008.6388 | 4089.81 | 5409.4348 | 1472 | 3.6749 | 3.4445 | 0.4 | 1.8 | -0.1 | 45.0786 |  | 12.1087 | 33.2289 | 36.7489 | 36.7144
46023.5337 | 33.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 23 | 25 | 23 | 2726.2 | 794.3 | 45.5 | 3 | 65 | 74 | 5.7 | 1472 | 2.6 | 15 | 180 | 61 | 3.5 | 3.5 | 43.8 | 43.8 | 46.5 | 225 | 0 | 0 | 24.4 | 25 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.6 | 28.1 | 45.15 | 2.7 | 1008.6648 | 4089.7638 | 5216.3166 | 1472 | 3.5437 | 3.4322 | 0.5 | 1.7 | 0.1 | 43.4693 |  | 12.121 | 33.2723 | 35.4369 | 36.6695
46023.5341 | 34 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 24 | 2736 | 794.3 | 45.6 | 3 | 64.5 | 73.2 | 5.7 | 1442 | 2.8 | 15 | 180 | 61 | 3.6 | 3.6 | 43.8 | 43.8 | 46.5 | 224 | 0 | 0 | 24.6 | 25.1 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.6 | 28.1 | 45.15 | 2.7 | 1008.6648 | 4089.7638 | 5216.3166 | 1442 | 3.6174 | 3.4445 | 0.6 | 1.8 | 0.1 | 43.4693 |  | 12.133 | 33.3158 | 36.1742 | 36.6695
46023.5344 | 34.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2745.8 | 784.5 | 45.8 | 3 | 64.2 | 72.8 | 5.8 | 1442 | 2.9 | 15 | 180 | 61 | 3.4 | 3.4 | 43.8 | 43.8 | 46.6 | 223 | 0 | 0 | 24.6 | 25.2 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.6 | 28.1 | 45.2 | 2.8 | 1008.6388 | 4089.81 | 5409.4348 | 1442 | 3.7513 | 3.5001 | 0.4 | 2 | 0 | 45.0786 |  | 12.145 | 33.3609 | 37.5134 | 36.8097
46023.5348 | 35 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2745.8 | 784.5 | 45.8 | 2.7 | 64.1 | 72.5 | 5.8 | 1439 | 2.9 | 15 | 182 | 61 | 3.4 | 3.3 | 43.8 | 43.8 | 46.6 | 223 | 0 | 0 | 24.7 | 25.3 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 28.3 | 45.2 | 2.8 | 1008.6388 | 4089.81 | 5447.9361 | 1439 | 3.7859 | 3.5001 | 0.6 | 2 | -0.1 | 45.3995 |  | 12.157 | 33.4063 | 37.8592 | 36.7465
46023.5351 | 35.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2745.8 | 784.5 | 45.8 | 2.7 | 63.8 | 72.4 | 5.8 | 1439 | 2.8 | 15 | 182 | 61 | 3.4 | 3.3 | 43.8 | 43.8 | 46.6 | 222 | 0 | 0 | 24.7 | 25.4 | 480 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.7 | 45.2 | 2.8 | 1008.6388 | 4089.81 | 5332.4322 | 1439 | 3.7057 | 3.5001 | 0.6 | 2 | -0.1 | 44.4369 |  | 12.169 | 33.4507 | 37.0565 | 36.808
46023.5355 | 36 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2745.8 | 794.3 | 45.8 | 3 | 63.8 | 72.4 | 5.8 | 1493 | 2.9 | 15 | 182 | 61 | 3.4 | 3.3 | 43.8 | 44 | 46.6 | 223 | 0 | 0 | 24.8 | 25.4 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.7 | 45.3 | 2.6 | 1008.5866 | 4089.9025 | 4951.3999 | 1493 | 3.3164 | 3.4569 | 0.3 | 2 | -0.1 | 41.2617 |  | 12.1814 | 33.492 | 33.1641 | 36.3535
46023.5358 | 36.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2745.8 | 784.5 | 45.8 | 2.7 | 63.7 | 72.4 | 5.8 | 1493 | 2.9 | 15 | 182 | 61 | 3.4 | 3.3 | 43.8 | 44 | 46.6 | 222 | 0 | 0 | 25 | 25.5 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 28.1 | 45.3 | 2.6 | 1008.5866 | 4089.9025 | 5022.9002 | 1493 | 3.3643 | 3.5001 | 0.6 | 2 | -0.1 | 41.8575 |  | 12.1938 | 33.5338 | 33.643 | 35.8472
46023.5362 | 37 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2745.8 | 794.3 | 45.8 | 3 | 63.7 | 72.4 | 5.8 | 1492 | 2.9 | 15 | 182 | 61 | 3.5 | 3.3 | 43.8 | 44 | 46.6 | 221 | 0 | 0 | 25 | 25.5 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.5 | 45.3 | 2.6 | 1008.5866 | 4089.9025 | 4915.6497 | 1492 | 3.2947 | 3.4569 | 0.3 | 2 | -0.1 | 40.9637 |  | 12.2063 | 33.5748 | 32.9467 | 34.9339
46023.5365 | 37.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2745.8 | 794.3 | 45.8 | 3 | 63.7 | 72.4 | 5.8 | 1492 | 2.9 | 15 | 181 | 61 | 3.5 | 3.3 | 44 | 44 | 46.6 | 220 | 0 | 0 | 25 | 25.5 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.7 | 45.3 | 2.6 | 1008.5866 | 4089.9025 | 4951.3999 | 1492 | 3.3186 | 3.4569 | 0.3 | 1.8 | -0.1 | 41.2617 |  | 12.2187 | 33.6161 | 33.1863 | 33.9993
46023.5369 | 38 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2745.8 | 794.3 | 45.8 | 3 | 63.7 | 72.4 | 5.8 | 1493 | 2.9 | 15 | 181 | 61 | 3.4 | 3.4 | 44 | 44 | 46.6 | 219 | 0 | 0 | 25 | 25.6 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.7 | 45.3 | 2.6 | 1008.5866 | 4089.9025 | 4951.3999 | 1493 | 3.3164 | 3.4569 | 0.4 | 1.8 | -0.1 | 41.2617 |  | 12.2312 | 33.6573 | 33.1641 | 33.2208
46023.5372 | 38.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2745.8 | 794.3 | 45.8 | 3 | 63.5 | 72.5 | 5.8 | 1493 | 2.9 | 15 | 181 | 61 | 3.4 | 3.4 | 44 | 44 | 46.6 | 218 | 0 | 0 | 25 | 25.6 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.7 | 45.3 | 2.6 | 1008.5866 | 4089.9025 | 4951.3999 | 1493 | 3.3164 | 3.4569 | 0.4 | 1.8 | -0.1 | 41.2617 |  | 12.2436 | 33.6986 | 33.1641 | 33.2208
46023.5376 | 39 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2745.8 | 794.3 | 45.8 | 3 | 63.5 | 72.5 | 5.8 | 1494 | 2.9 | 15 | 181 | 61 | 3.4 | 3.4 | 44 | 44 | 46.6 | 217 | 0 | 0 | 25.1 | 25.6 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.9 | 45.3 | 2.6 | 1008.5866 | 4089.9025 | 4987.1501 | 1494 | 3.3381 | 3.4569 | 0.4 | 1.8 | -0.1 | 41.5596 |  | 12.256 | 33.7402 | 33.3812 | 33.1685
46023.5379 | 39.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2745.8 | 794.3 | 45.8 | 3 | 63.5 | 72.5 | 5.8 | 1494 | 2.9 | 15 | 181 | 61 | 3.4 | 3.4 | 44 | 44 | 46.6 | 216 | 0 | 0 | 25.1 | 25.6 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.9 | 45.3 | 2.6 | 1008.5866 | 4089.9025 | 4987.1501 | 1494 | 3.3381 | 3.4569 | 0.4 | 1.8 | -0.1 | 41.5596 |  | 12.2685 | 33.7817 | 33.3812 | 33.2554
46023.5383 | 40 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2745.8 | 784.5 | 45.8 | 2.7 | 63.5 | 72.5 | 5.8 | 1493 | 2.9 | 15 | 181 | 61 | 3.4 | 3.4 | 44 | 44 | 46.6 | 215 | 0 | 0 | 25.1 | 25.6 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.7 | 45.3 | 2.6 | 1008.5866 | 4089.9025 | 4951.3999 | 1493 | 3.3164 | 3.5001 | 0.7 | 1.8 | -0.1 | 41.2617 |  | 12.2809 | 33.823 | 33.1641 | 33.2509
46023.5386 | 40.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2745.8 | 784.5 | 45.8 | 2.7 | 63.4 | 72.5 | 5.8 | 1493 | 2.9 | 15 | 181 | 61 | 3.4 | 3.3 | 43.8 | 43.8 | 46.6 | 216 | 0 | 0 | 25.1 | 25.6 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.7 | 45.2 | 2.8 | 1008.6388 | 4089.81 | 5332.4322 | 1493 | 3.5716 | 3.5001 | 0.6 | 2 | -0.1 | 44.4369 |  | 12.2934 | 33.8674 | 35.7162 | 33.7614
46023.5389 | 41 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2745.8 | 784.5 | 45.8 | 2.7 | 63.4 | 72.7 | 5.8 | 1493 | 2.9 | 15 | 181 | 61 | 3.4 | 3.3 | 43.8 | 44 | 46.8 | 215 | 0 | 0 | 25.1 | 25.6 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.5 | 45.4 | 2.8 | 1008.5343 | 4089.995 | 5293.622 | 1493 | 3.5456 | 3.5001 | 0.6 | 2 | -0.3 | 44.1135 |  | 12.3058 | 33.9115 | 35.4563 | 34.2198
46023.5393 | 41.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2745.8 | 784.5 | 45.8 | 2.7 | 63.4 | 72.5 | 5.8 | 1493 | 2.9 | 15 | 181 | 61 | 3.4 | 3.3 | 43.8 | 44 | 46.8 | 214 | 0 | 0 | 25.1 | 25.6 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.5 | 45.4 | 2.8 | 1008.5343 | 4089.995 | 5293.622 | 1493 | 3.5456 | 3.5001 | 0.6 | 2 | -0.3 | 44.1135 |  | 12.3183 | 33.9556 | 35.4563 | 34.6348
46023.5396 | 42 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 23 | 24 | 2736 | 794.3 | 45.6 | 3 | 63.2 | 72.7 | 5.8 | 1494 | 2.8 | 15 | 179 | 61 | 3.4 | 3.3 | 43.6 | 43.8 | 46.6 | 213 | 0 | 0 | 25.1 | 25.6 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.5 | 45.2 | 2.8 | 1008.6388 | 4089.81 | 5293.9308 | 1494 | 3.5435 | 3.4445 | 0.3 | 2 | -0.1 | 44.1161 |  | 12.3307 | 33.9998 | 35.4346 | 35.0455
46023.54 | 42.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 23 | 23 | 23 | 2736 | 794.3 | 45.6 | 3 | 63.2 | 72.7 | 5.8 | 1442 | 2.7 | 15 | 179 | 61 | 3.5 | 3.5 | 43.6 | 43.8 | 46.5 | 212 | 0 | 0 | 25.1 | 25.6 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.9 | 45.15 | 2.7 | 1008.6648 | 4089.7638 | 5179.1898 | 1442 | 3.5917 | 3.4445 | 0.5 | 2 | 0 | 43.1599 |  | 12.3427 | 34.0429 | 35.9167 | 35.596
46023.5403 | 43 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 25 | 24 | 2736 | 794.3 | 45.6 | 3 | 63.1 | 72.7 | 5.8 | 1442 | 2.8 | 15 | 179 | 61 | 3.6 | 3.6 | 43.6 | 43.8 | 46.5 | 213 | 0 | 0 | 25.1 | 25.6 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.9 | 45.15 | 2.7 | 1008.6648 | 4089.7638 | 5179.1898 | 1442 | 3.5917 | 3.4445 | 0.6 | 2 | 0 | 43.1599 |  | 12.3547 | 34.0861 | 35.9167 | 35.6361
46023.5407 | 43.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2745.8 | 794.3 | 45.8 | 3 | 63.1 | 72.5 | 5.8 | 1438 | 2.9 | 15 | 179 | 61 | 3.5 | 3.4 | 43.8 | 43.8 | 46.6 | 213 | 0 | 0 | 25.1 | 25.6 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.9 | 45.2 | 2.8 | 1008.6388 | 4089.81 | 5370.9335 | 1438 | 3.735 | 3.4569 | 0.4 | 2 | -0.1 | 44.7578 |  | 12.3667 | 34.1308 | 37.35 | 36.0149
46023.541 | 44 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2745.8 | 794.3 | 45.8 | 3 | 63.1 | 72.4 | 5.8 | 1438 | 2.9 | 15 | 181 | 61 | 3.4 | 3.4 | 43.6 | 43.8 | 46.6 | 212 | 0 | 0 | 25.1 | 25.6 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.9 | 45.2 | 2.8 | 1008.6388 | 4089.81 | 5370.9335 | 1438 | 3.735 | 3.4569 | 0.4 | 2.2 | -0.1 | 44.7578 |  | 12.3787 | 34.1756 | 37.35 | 36.3936
46023.5414 | 44.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2745.8 | 794.3 | 45.8 | 3 | 63.1 | 72.4 | 5.8 | 1492 | 2.9 | 15 | 181 | 61 | 3.4 | 3.4 | 43.1 | 43.8 | 46.6 | 212 | 0 | 0 | 25.1 | 25.6 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.9 | 45.2 | 2.8 | 1008.6388 | 4089.81 | 5370.9335 | 1492 | 3.5998 | 3.4569 | 0.4 | 2.7 | -0.1 | 44.7578 |  | 12.3911 | 34.2203 | 35.9982 | 36.5063
46023.5417 | 45 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2765.5 | 784.5 | 46.1 | 2.7 | 63.1 | 72.4 | 5.8 | 1492 | 2.9 | 15 | 181 | 61 | 3.4 | 3.3 | 43 | 44 | 46.8 | 213 | 0 | 0 | 25.1 | 25.6 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 28.1 | 45.4 | 2.8 | 1008.5343 | 4089.995 | 5409.1193 | 1492 | 3.6254 | 3.5252 | 0.6 | 3.1 | -0.3 | 45.076 |  | 12.4036 | 34.2654 | 36.2542 | 36.5738
46023.5421 | 45.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2755.7 | 784.5 | 45.9 | 2.7 | 63.2 | 72.7 | 5.8 | 1495 | 2.9 | 15 | 181 | 61 | 3.4 | 3.3 | 42.8 | 44 | 46.8 | 212 | 0 | 0 | 25.1 | 25.6 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 28.1 | 45.4 | 2.8 | 1008.5343 | 4089.995 | 5409.1193 | 1495 | 3.6181 | 3.5127 | 0.6 | 3.1 | -0.3 | 45.076 |  | 12.416 | 34.3105 | 36.1814 | 36.6268
46023.5424 | 46 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 24 | 23 | 24 | 2745.8 | 794.3 | 45.8 | 3 | 63.5 | 73.1 | 5.8 | 1495 | 2.8 | 15 | 181 | 61 | 3.3 | 3.3 | 42.8 | 44 | 46.8 | 211 | 0 | 0 | 25.1 | 25.5 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.9 | 45.4 | 2.8 | 1008.5343 | 4089.995 | 5370.6202 | 1495 | 3.5924 | 3.4569 | 0.3 | 3 | -0.3 | 44.7552 |  | 12.4285 | 34.3553 | 35.9239 | 36.3415
46023.5428 | 0 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Stop | Heat | 0 | 0 | 0 | 0 | 2638 | 863 | 44.2 | 5.4 | 63.2 | 73.4 | 5.8 | 1009 | 0 | 0 | 168 | 56 | 5 | 4.9 | 42.8 | 45 | 45.3 | 0 | 0 | 0 | 25.1 | 25.5 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 28.1 | 45.15 | 0.3 | 1008.6648 | 4089.7638 | 579.5907 | 1009 | 0.57442 | 3.0568 | -0.5 | 1.4 | 1.2 | 4.8299 |  | 12.4369 | 34.3601
46023.5431 | 0.5 | EHS MONO LOWTEMP | On | Off | On | Off | On | Stop | Heat | 0 | 0 | 0 | 0 | 1726 | 951.2 | 27.9 | 8.3 | 61.4 | 72.5 | 5.8 | 1009 | 0 | 0 | 168 | 53 | 7.8 | 7.8 | 38.5 | 45.3 | 44.6 | 0 | 0 | 0 | 25.1 | 25.5 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.7 | 44.95 | -0.7 | 1008.769 | 4089.5788 | -1333.2048 | 1009 | -1.3213 | 1.8146 | -0.5 | -10.6 | 1.9 | -11.11 |  | 12.4453 | 34.349
46023.5435 | 1 | EHS MONO LOWTEMP | On | Off | On | Off | On | Stop | Heat | 0 | 0 | 0 | 0 | 1019.9 | 990.5 | 10.4 | 9.5 | 58.8 | 71.4 | 5.8 | 1009 | 0 | 0 | 168 | 52 | 8.3 | 9.3 | 31.7 | 45.1 | 45.1 | 0 | 0 | 0 | 25.1 | 25.4 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.7 | 45.1 | 0 | 1008.6909 | 4089.7175 | 0 | 1009 | 0 | 1.0297 | -0.2 | -21.3 | 1.4 | 0 |  | 12.4537 | 34.349
46023.5438 | 1.5 | EHS MONO LOWTEMP | On | Off | On | Off | On | Stop | Heat | 0 | 0 | 0 | 0 | 961 | 990.5 | 8.6 | 9.5 | 56.1 | 69.5 | 5.9 | 166 | 0 | 0 | 168 | 51 | 9.1 | 10.4 | 28 | 42.4 | 45.1 | 0 | 0 | 0 | 25 | 25.2 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 0 | 43.75 | 2.7 | 1009.3894 | 4088.4688 | 0 | 166 | 0 | 0.97022 | 0.9 | -19.4 | 1.4 | 0 |  | 12.4551 | 34.349
46023.5442 | 2 | EHS MONO LOWTEMP | Off | Off | On | Off | On | Stop | Heat | 0 | 0 | 0 | 0 | 941.4 | 980.7 | 8 | 9.2 | 54.3 | 67.5 | 5.9 | 166 | 0 | 0 | 168 | 50 | 9.2 | 11 | 26.4 | 40 | 45.1 | 0 | 0 | 0 | 24.1 | 25 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 0 | 42.55 | 5.1 | 1010.0017 | 4087.3587 | 0 | 166 | 0 | 0.95993 | 1.8 | -18.4 | 1.4 | 0 |  | 12.4565 | 34.349
46023.5445 | 2.5 | EHS MONO LOWTEMP | Off | Off | On | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 921.8 | 951.2 | 7.4 | 8.3 | 53.2 | 66 | 6 | 91 | 0 | 0 | 168 | 50 | 8.7 | 11.6 | 25.5 | 39.4 | 45.1 | 0 | 0 | 0 | 22.6 | 24.7 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.4 | 0 | 42.25 | 5.7 | 1010.1535 | 4087.0813 | 0 | 91 | 0 | 0.96909 | 3.3 | -18.1 | 1.3 | 0 |  | 12.4572 | 34.349
46023.5449 | 3 | EHS MONO LOWTEMP | Off | Off | On | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 912 | 941.4 | 7 | 8 | 52.5 | 64.5 | 6.1 | 91 | 0 | 0 | 168 | 49 | 8.3 | 12 | 24.8 | 39 | 45.1 | 0 | 0 | 0 | 21 | 24.3 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.4 | 0 | 42.05 | 6.1 | 1010.2544 | 4086.8962 | 0 | 91 | 0 | 0.96877 | 4 | -17.8 | 1.3 | 0 |  | 12.458 | 34.349
46023.5452 | 3.5 | EHS MONO LOWTEMP | Off | Off | On | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 912 | 941.4 | 7 | 8 | 52 | 63.7 | 6.2 | 91 | 0 | 0 | 168 | 49 | 8.1 | 12.2 | 24.3 | 38.8 | 45.1 | 0 | 0 | 0 | 19.9 | 24.1 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.3 | 0 | 41.95 | 6.3 | 1010.3048 | 4086.8038 | 0 | 91 | 0 | 0.96877 | 4.2 | -17.3 | 1.2 | 0 |  | 12.4588 | 34.349
46023.5455 | 4 | EHS MONO LOWTEMP | Off | Off | On | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 902.2 | 941.4 | 6.7 | 8 | 50.8 | 62.4 | 6.2 | 91 | 0 | 0 | 168 | 49 | 8.1 | 12.7 | 23.6 | 38.7 | 45.1 | 0 | 0 | 0 | 18.5 | 23.6 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.3 | 0 | 41.9 | 6.4 | 1010.33 | 4086.7575 | 0 | 91 | 0 | 0.95836 | 4.7 | -16.9 | 1.2 | 0 |  | 12.4595 | 34.349
46023.5459 | 4.5 | EHS MONO LOWTEMP | Off | Off | On | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 892.4 | 921.8 | 6.4 | 7.4 | 50.3 | 61.4 | 6.2 | 91 | 0 | 0 | 168 | 48 | 8 | 13.1 | 23 | 38.7 | 45 | 0 | 0 | 0 | 17.1 | 23.3 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.3 | 0 | 41.85 | 6.3 | 1010.3551 | 4086.7112 | 0 | 91 | 0 | 0.96811 | 5.7 | -16.6 | 1.3 | 0 |  | 12.4603 | 34.349
46023.5462 | 5 | EHS MONO LOWTEMP | Off | Off | On | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 912 | 941.4 | 7 | 8 | 49.8 | 60.5 | 6.2 | 91 | 0 | 0 | 168 | 46 | 8.2 | 13.5 | 22.5 | 39 | 45 | 2000 | 0 | 0 | 16 | 22.8 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.3 | 0 | 42 | 6 | 1010.2796 | 4086.85 | 0 | 91 | 0 | 0.96877 | 5.5 | -15.5 | 1.3 | 0 |  | 12.461 | 34.349
46023.5466 | 5.5 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 892.4 | 931.6 | 6.4 | 7.7 | 49.1 | 59.7 | 6.3 | 91 | 0 | 0 | 168 | 44 | 8 | 13.8 | 22 | 39.2 | 44.8 | 2000 | 0 | 0 | 15.1 | 22.5 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.3 | 0 | 42 | 5.6 | 1010.2796 | 4086.85 | 0 | 91 | 0 | 0.95792 | 6.1 | -15.6 | 1.5 | 0 |  | 12.4618 | 34.349
46023.5469 | 6 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 892.4 | 921.8 | 6.4 | 7.4 | 48.8 | 59.1 | 6.3 | 91 | 0 | 0 | 168 | 44 | 7.9 | 14 | 21.8 | 39.5 | 44.8 | 2000 | 0 | 0 | 14.5 | 22.2 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.2 | 0 | 42.15 | 5.3 | 1010.204 | 4086.9887 | 0 | 91 | 0 | 0.96811 | 6.6 | -15.4 | 1.4 | 0 |  | 12.4626 | 34.349
46023.5473 | 6.5 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 892.4 | 921.8 | 6.4 | 7.4 | 48.1 | 58.4 | 6.3 | 91 | 0 | 0 | 168 | 44 | 7.8 | 14.2 | 21.6 | 40.3 | 44.6 | 2000 | 0 | 0 | 13.7 | 21.7 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.2 | 0 | 42.45 | 4.3 | 1010.0523 | 4087.2663 | 0 | 91 | 0 | 0.96811 | 6.8 | -15.2 | 1.6 | 0 |  | 12.4633 | 34.349
46023.5476 | 7 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 892.4 | 921.8 | 6.4 | 7.4 | 47.6 | 58 | 6.3 | 91 | 0 | 0 | 168 | 43 | 7.8 | 14.5 | 21.5 | 40.8 | 44.4 | 2000 | 0 | 0 | 13.1 | 21.4 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.2 | 0 | 42.6 | 3.6 | 1009.9763 | 4087.405 | 0 | 91 | 0 | 0.96811 | 7.1 | -15.1 | 1.8 | 0 |  | 12.4641 | 34.349
46023.548 | 7.5 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 882.6 | 912 | 6.1 | 7 | 47 | 57.3 | 6.3 | 91 | 0 | 0 | 168 | 43 | 7.8 | 14.7 | 21.5 | 41.3 | 44.2 | 2000 | 0 | 0 | 12.6 | 21 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.2 | 0 | 42.75 | 2.9 | 1009.9002 | 4087.5437 | 0 | 91 | 0 | 0.96776 | 7.7 | -15.4 | 2 | 0 |  | 12.4648 | 34.349
46023.5483 | 8 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 872.8 | 902.2 | 5.8 | 6.7 | 46.4 | 56.8 | 6.2 | 91 | 0 | 0 | 168 | 43 | 7.8 | 15 | 21.5 | 41.6 | 44 | 2000 | 0 | 0 | 12.2 | 20.6 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.2 | 0 | 42.8 | 2.4 | 1009.8748 | 4087.59 | 0 | 91 | 0 | 0.96741 | 8.3 | -15.7 | 2.2 | 0 |  | 12.4656 | 34.349
46023.5487 | 8.5 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 872.8 | 902.2 | 5.8 | 6.7 | 46 | 56.5 | 6.2 | 91 | 0 | 0 | 168 | 43 | 7.7 | 15.1 | 21.4 | 42 | 44 | 2000 | 0 | 0 | 12 | 20.4 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.2 | 0 | 43 | 2 | 1009.773 | 4087.775 | 0 | 91 | 0 | 0.96741 | 8.4 | -15.6 | 2.2 | 0 |  | 12.4663 | 34.349
46023.549 | 9 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 863 | 892.4 | 5.4 | 6.4 | 45.5 | 56.1 | 6.3 | 91 | 0 | 0 | 167 | 43 | 7.6 | 15.3 | 21.3 | 42.1 | 43.8 | 2000 | 0 | 0 | 11.7 | 20.1 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.3 | 0 | 42.95 | 1.7 | 1009.7985 | 4087.7288 | 0 | 91 | 0 | 0.96706 | 8.9 | -15.9 | 2.5 | 0 |  | 12.4671 | 34.349
46023.5494 | 9.5 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 863 | 892.4 | 5.4 | 6.4 | 45 | 55.8 | 6.3 | 91 | 0 | 0 | 167 | 42 | 7.6 | 15.4 | 21.1 | 42.4 | 43.6 | 2000 | 0 | 0 | 11.4 | 19.8 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.2 | 0 | 43 | 1.2 | 1009.773 | 4087.775 | 0 | 91 | 0 | 0.96706 | 9 | -15.7 | 2.6 | 0 |  | 12.4679 | 34.349
46023.5497 | 10 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 863 | 892.4 | 5.4 | 6.4 | 44.4 | 55.3 | 6.3 | 91 | 0 | 0 | 167 | 42 | 7.5 | 15.6 | 21 | 42.5 | 43.5 | 2000 | 0 | 0 | 11.3 | 19.5 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.2 | 0 | 43 | 1 | 1009.773 | 4087.775 | 0 | 91 | 0 | 0.96706 | 9.2 | -15.6 | 2.7 | 0 |  | 12.4686 | 34.349
46023.5501 | 10.5 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 863 | 892.4 | 5.4 | 6.4 | 43.8 | 55.1 | 6.2 | 91 | 0 | 0 | 167 | 42 | 7.4 | 15.8 | 20.7 | 42.7 | 43.3 | 2000 | 0 | 0 | 11.1 | 19.3 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.2 | 0 | 43 | 0.6 | 1009.773 | 4087.775 | 0 | 91 | 0 | 0.96706 | 9.4 | -15.3 | 2.9 | 0 |  | 12.4694 | 34.349
46023.5504 | 11 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 863 | 892.4 | 5.4 | 6.4 | 43.5 | 54.8 | 6.2 | 91 | 0 | 0 | 167 | 42 | 7.4 | 16 | 20.7 | 42.7 | 43.3 | 2000 | 0 | 0 | 11 | 19.1 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.3 | 0 | 43 | 0.6 | 1009.773 | 4087.775 | 0 | 91 | 0 | 0.96706 | 9.6 | -15.3 | 3 | 0 |  | 12.4701 | 34.349
46023.5508 | 11.5 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 863 | 892.4 | 5.4 | 6.4 | 43 | 54.5 | 6.2 | 91 | 0 | 0 | 167 | 42 | 7.3 | 16.2 | 20.5 | 42.8 | 43.1 | 2000 | 0 | 0 | 10.9 | 18.9 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.3 | 0 | 42.95 | 0.3 | 1009.7985 | 4087.7288 | 0 | 91 | 0 | 0.96706 | 9.8 | -15.1 | 3.2 | 0 |  | 12.4709 | 34.349
46023.5511 | 12 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 863 | 892.4 | 5.4 | 6.4 | 42.6 | 54.3 | 6.2 | 91 | 0 | 0 | 167 | 42 | 7.3 | 16.3 | 20.4 | 42.8 | 43 | 2000 | 0 | 0 | 10.8 | 18.7 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.3 | 0 | 42.9 | 0.2 | 1009.8239 | 4087.6825 | 0 | 91 | 0 | 0.96706 | 9.9 | -15 | 3.3 | 0 |  | 12.4717 | 34.349
46023.5514 | 12.5 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 863 | 892.4 | 5.4 | 6.4 | 42 | 54 | 6.3 | 91 | 0 | 0 | 167 | 41 | 7.3 | 16.5 | 20.2 | 42.8 | 42.7 | 2000 | 0 | 0 | 10.7 | 18.5 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.3 | 0 | 42.75 | -0.1 | 1009.9002 | 4087.5437 | 0 | 91 | 0 | 0.96706 | 10.1 | -14.8 | 3.6 | 0 |  | 12.4724 | 34.349
46023.5518 | 13 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 863 | 892.4 | 5.4 | 6.4 | 41.6 | 53.8 | 6.3 | 91 | 0 | 0 | 167 | 41 | 7.3 | 16.7 | 20.1 | 42.8 | 42.7 | 2000 | 0 | 0 | 10.7 | 18.3 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.2 | 0 | 42.75 | -0.1 | 1009.9002 | 4087.5437 | 0 | 91 | 0 | 0.96706 | 10.3 | -14.7 | 3.5 | 0 |  | 12.4732 | 34.349
46023.5521 | 13.5 | EHS MONO LOWTEMP | Off | Off | Off | Off | Off | Stop | Heat | 0 | 0 | 0 | 0 | 863 | 892.4 | 5.4 | 6.4 | 41.2 | 53.7 | 6.3 | 91 | 0 | 0 | 167 | 41 | 7.3 | 16.8 | 20.1 | 42.8 | 42.5 | 2000 | 0 | 0 | 10.6 | 18.2 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.2 | 0 | 42.65 | -0.3 | 1009.9509 | 4087.4513 | 0 | 91 | 0 | 0.96706 | 10.4 | -14.7 | 3.7 | 0 |  | 12.4739 | 34.349
46023.5525 | 0 | EHS MONO LOWTEMP | Off | Off | On | Off | On | Safety Start | Heat | 0 | 20 | 40 | 11 | 863 | 892.4 | 5.4 | 6.4 | 41 | 53.5 | 6.3 | 91 | 0 | 0 | 167 | 41 | 7.3 | 17 | 20.1 | 41.1 | 40.8 | 125 | 0 | 0 | 10.6 | 18 | 0 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.2 | 0 | 40.95 | -0.3 | 1010.8055 | 4085.8787 | 0 | 91 | 0 | 0.96706 | 10.6 | -14.7 | 5.4 | 3997.7664 |  | 12.4747 | 34.349
46023.5528 | 0.5 | EHS MONO LOWTEMP | Off | Off | On | Off | On | Safety Start | Heat | 0 | 40 | 40 | 40 | 2235.9 | 813.9 | 37.6 | 3.7 | 44.4 | 53.2 | 6.3 | 78 | 3.6 | 13 | 167 | 41 | 7.7 | 9.2 | 27.1 | 41.1 | 41.6 | 125 | 0 | 0 | 10.6 | 17.8 | 450 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.2 | 28.9 | 41.35 | 0.5 | 1010.6059 | 4086.2488 | 994.5422 | 78 | 12.7505 | 2.7471 | 5.5 | 10.5 | 4.6 | 3964.727 |  | 12.4753 | 34.3573
46023.5532 | 1 | EHS MONO LOWTEMP | Off | Off | On | Off | On | Safety Start | Heat | 0 | 40 | 40 | 40 | 2432 | 794.3 | 40.9 | 3 | 53.8 | 55.8 | 6.2 | 78 | 3.8 | 13 | 167 | 47 | 4 | 4.5 | 36.8 | 40 | 42 | 357 | 0 | 700 | 10.6 | 17.7 | 460 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.2 | 27.9 | 41 | 2 | 1010.7806 | 4085.925 | 3840.8756 | 78 | 49.242 | 3.0618 | 1.5 | 4.1 | 4.2 | 5.7554 |  | 12.476 | 34.3893
46023.5535 | 1.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Safety Start | Heat | 0 | 37 | 25 | 39 | 2441.8 | 804.1 | 40.6 | 4.1 | 57.5 | 58.7 | 6.1 | 1348 | 4.2 | 14 | 167 | 50 | 4.3 | 4.4 | 38.5 | 39.8 | 41.8 | 223 | 150 | 2000 | 14.7 | 24.1 | 460 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.3 | 28.1 | 40.8 | 2 | 1010.8801 | 4085.74 | 3868.6145 | 1348 | 2.8699 | 3.0367 | 0.3 | 2.1 | 4.5 | 15.7446 |  | 12.4872 | 34.4215 | 28.6989
46023.5539 | 2 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Safety Start | Heat | 0 | 25 | 25 | 25 | 2412.4 | 784.5 | 40.6 | 2.7 | 58.5 | 62 | 6 | 1348 | 3 | 15 | 183 | 53 | 2.8 | 3 | 39.8 | 39.1 | 42.1 | 223 | 155 | 2000 | 19.7 | 33.7 | 480 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.3 | 28.1 | 40.6 | 3 | 1010.9794 | 4085.555 | 5803.229 | 1348 | 4.3051 | 3.0751 | 0.3 | 0.8 | 4.2 | 253.913 |  | 12.4985 | 34.4699 | 43.0507
46023.5542 | 2.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Safety Start | Heat | 0 | 25 | 25 | 25 | 2432 | 784.5 | 40.9 | 2.7 | 57.8 | 63.2 | 6 | 1896 | 3 | 15 | 183 | 55 | 3.2 | 4.8 | 39.8 | 39.4 | 42 | 223 | 155 | 2000 | 25.8 | 36 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.4 | 27.5 | 40.7 | 2.6 | 1010.9298 | 4085.6475 | 4921.9442 | 1896 | 2.596 | 3.1001 | 2.1 | 1.1 | 4.4 | 16.9 |  | 12.5143 | 34.5109 | 25.9596
46023.5546 | 3 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Safety Start | Heat | 0 | 25 | 25 | 25 | 2441.8 | 794.3 | 41.1 | 3 | 56.8 | 63.4 | 6 | 1896 | 3 | 15 | 183 | 56 | 3.3 | 6.1 | 39.8 | 39.4 | 42.1 | 223 | 155 | 2000 | 26.5 | 36.7 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.4 | 27.7 | 40.75 | 2.7 | 1010.905 | 4085.6937 | 5148.3543 | 1896 | 2.7154 | 3.0742 | 3.1 | 1.3 | 4.3 | 4291.1303 |  | 12.5301 | 34.5538 | 27.1538
46023.5549 | 3.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Safety Start | Heat | 0 | 25 | 25 | 25 | 2441.8 | 794.3 | 41.1 | 3 | 56.7 | 63.2 | 6 | 1534 | 3 | 16 | 183 | 56 | 3.6 | 4.6 | 40 | 39.5 | 42.1 | 223 | 159 | 2000 | 26.8 | 37.2 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.4 | 27.5 | 40.8 | 2.6 | 1010.8801 | 4085.74 | 4921.8138 | 1534 | 3.2085 | 3.0742 | 1.6 | 1.1 | 4.3 |  |  | 12.5428 | 34.5948 | 32.0848
46023.5553 | 4 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2461.5 | 794.3 | 41.4 | 3 | 56.7 | 63.2 | 6 | 1534 | 3 | 16 | 180 | 57 | 3.6 | 3.9 | 40.1 | 39.7 | 42.2 | 222 | 159 | 2000 | 27.1 | 37.2 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.4 | 27.5 | 40.95 | 2.5 | 1010.8055 | 4085.8787 | 4732.3246 | 1534 | 3.085 | 3.099 | 0.9 | 1.3 | 4.2 |  |  | 12.5556 | 34.6342 | 30.8496
46023.5556 | 4.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 22 | 22 | 24 | 2461.5 | 794.3 | 41.4 | 3 | 56.8 | 63.2 | 6 | 1539 | 3 | 16 | 180 | 57 | 3.6 | 3.7 | 40.3 | 39.7 | 42.4 | 221 | 0 | 0 | 27.2 | 37.4 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.4 | 27.9 | 41.05 | 2.7 | 1010.7557 | 4085.9713 | 5185.1129 | 1539 | 3.3691 | 3.099 | 0.7 | 1.1 | 4 |  |  | 12.5684 | 34.6775 | 33.6914
46023.556 | 5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 22 | 22 | 22 | 2461.5 | 804.1 | 41.4 | 3.4 | 56.8 | 63.4 | 5.9 | 1539 | 2.3 | 13 | 180 | 57 | 3.8 | 3.8 | 40.3 | 40 | 42.4 | 220 | 0 | 0 | 25.4 | 37.1 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.4 | 27.9 | 41.2 | 2.4 | 1010.6808 | 4086.11 | 4608.8045 | 1539 | 2.9947 | 3.0612 | 0.4 | 1.1 | 4 |  |  | 12.5813 | 34.7159 | 29.9467
46023.5563 | 5.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 22 | 28 | 22 | 2471.3 | 804.1 | 41.5 | 3.4 | 56.8 | 63.5 | 5.9 | 1411 | 2.3 | 13 | 180 | 56 | 3.9 | 3.8 | 40.1 | 40 | 42.4 | 219 | 0 | 0 | 21.5 | 36 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.7 | 41.2 | 2.4 | 1010.6808 | 4086.11 | 4575.7665 | 1411 | 3.2429 | 3.0734 | 0.4 | 1.4 | 4.1 |  |  | 12.593 | 34.754 | 32.4292
46023.5567 | 6 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 28 | 28 | 28 | 2520.3 | 784.5 | 42.3 | 2.7 | 56.4 | 63.5 | 5.9 | 1317 | 2.9 | 14 | 180 | 56 | 3.3 | 3.3 | 40.3 | 40 | 43 | 220 | 0 | 0 | 18.4 | 34.8 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.7 | 41.5 | 3 | 1010.5308 | 4086.3875 | 5719.2473 | 1317 | 4.3426 | 3.2126 | 0.6 | 2 | 3.5 |  |  | 12.604 | 34.8016 | 43.4263 | 34.0687
46023.557 | 6.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 26 | 25 | 28 | 2520.3 | 774.7 | 42.3 | 2.3 | 56.5 | 63.7 | 5.9 | 1317 | 2.9 | 14 | 180 | 57 | 3.1 | 3 | 40.3 | 40 | 43 | 220 | 0 | 0 | 17.5 | 34.1 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.7 | 41.5 | 3 | 1010.5308 | 4086.3875 | 5719.2473 | 1317 | 4.3426 | 3.2533 | 0.7 | 2 | 3.5 |  |  | 12.615 | 34.8493 | 43.4263 | 36.584
46023.5574 | 7 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 25 | 25 | 2510.5 | 784.5 | 42.2 | 2.7 | 56.7 | 64.1 | 5.9 | 1452 | 2.7 | 14 | 180 | 57 | 3.2 | 3.1 | 40.3 | 40.1 | 43.1 | 219 | 0 | 0 | 17.1 | 33 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.7 | 41.6 | 3 | 1010.4807 | 4086.48 | 5719.093 | 1452 | 3.9388 | 3.2001 | 0.4 | 1.9 | 3.4 |  |  | 12.6271 | 34.897 | 39.3877 | 37.7233
46023.5577 | 7.5 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 25 | 30 | 25 | 2510.5 | 784.5 | 42.2 | 2.7 | 56.7 | 64.4 | 5.9 | 1452 | 2.6 | 14 | 180 | 57 | 3.4 | 3.2 | 40.1 | 40.3 | 43 | 219 | 0 | 0 | 17.3 | 31.8 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.9 | 41.65 | 2.7 | 1010.4556 | 4086.5262 | 5184.2775 | 1452 | 3.5704 | 3.2001 | 0.5 | 2.1 | 3.5 |  |  | 12.6392 | 34.9402 | 35.7044 | 38.8748
46023.558 | 8 | EHS MONO LOWTEMP | On | Off | Off | Off | On | Normal Operation | Heat | 0 | 30 | 30 | 30 | 2569.3 | 774.7 | 43.1 | 2.3 | 56.8 | 64.7 | 5.9 | 1460 | 3.1 | 14 | 180 | 57 | 3 | 3 | 40.1 | 40.5 | 43.6 | 219 | 0 | 0 | 18.2 | 30.7 | 490 | Off | Off | 70℃ | �������������������������������� | 0YDLPAFT900181M | DB91-02450A 220706 | DB91-02412A 100010 | DB82-07081A 220622 | 100% | Basic | Basic | Basic | Auto Addressing | Apply | Apply | 46.5 | 27.9 | 42.05 | 3.1 | 1010.2544 | 4086.8962 | 5951.6723 | 1460 | 4.0765 | 3.3165 | 0.7 | 3 | 2.9 |  |  | 12.6513 | 34.9898 | 40.7649 | 40.5419

## Indoor 20.00.00
Time | Combination Operation | Zone1 Normal Power | Zone2 Normal Power | Operation Mode | Error Code | Silence Mode | Outing Operation | DHW Power | DHW Mode | Zone1 Room Set Temp. ( ℃) | Zone2 Room Set Temp. ( ℃) | DHW Set Temp. ( ℃) | Water Law Set Temp. ( ℃) | Water Law Target Value ( ℃) | Water Outlet Set Temp. ( ℃) | Water Outlet2 Set Temp. ( ℃) | Ref. Temp. | Thermo | 2Way Valve1(Pump1) | 2Way Valve2(Pump2) | 3Way Valve | Water Pump | Backup Heater | Boost Heater | Solar Pump | PV Control | Smart Grid | Flow Switch | Flow Sensor | Eva In1 ( ℃) | Water In ( ℃) | Water Out ( ℃) | Heater Out(Tw3) ( ℃) | Mixing Valve Temp(Tw4) ( ℃) | DHW Tank ( ℃) | Room Temp. ( ℃) | Zone2 Room Temp. ( ℃) | Zone1 WaterOut Temp ( ℃) | Zone2 WaterOut Temp ( ℃) | Inverter Pump PWM | Thermostat1 | Thermostat2 | DHW Thermostat | Serial Number | Main Micom | Product Option
46023.2865 | - | - | - | - | - | - | - | - | - | - | - | - | 50.6 | - | - | - | Water Out | - | - | - | - | - | - | - | - | - | - | - | 27.5 | 21.2 | 18.5 | 23 | - | - | - | 20 | 20 | - | - | - | - | - | - | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2868 | - | - | - | - | - | - | - | - | - | - | - | - | 50.6 | - | - | - | Water Out | - | - | - | - | - | - | - | - | - | - | - | 27.7 | 21.2 | 18.6 | 23.1 | - | - | 22.3 | 20 | 20 | - | - | - | - | - | - | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2872 | - | - | - | - | - | - | - | - | - | - | - | - | 50.6 | - | - | - | Water Out | - | - | - | - | - | - | - | - | - | - | - | 27.7 | 21.2 | 18.6 | 23.1 | - | - | 22.3 | 20 | 20 | - | - | - | - | - | - | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2875 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | - | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 21.3 | 18.9 | 23.4 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2879 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | - | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 21.7 | 19.4 | 23.8 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2882 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | - | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 21.7 | 19.4 | 23.8 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2886 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | - | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 22.2 | 19.8 | 24.3 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2889 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | - | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 22.6 | 20.3 | 24.8 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2893 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 23 | 20.6 | 25.2 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2896 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 23 | 20.6 | 25.2 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.29 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 23.6 | 21.3 | 25.7 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2903 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 24.2 | 21.6 | 26.4 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2907 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 24.6 | 22.1 | 27 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.291 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 24.6 | 22.1 | 27 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2914 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 24.8 | 22.5 | 27.3 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2917 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 25.3 | 22.8 | 28 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2921 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 25.7 | 23.2 | 28.5 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2924 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 25.7 | 23.2 | 28.5 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2927 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 25.8 | 23.7 | 29.1 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2931 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 25.1 | 24 | 29.3 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2934 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.1 | 24.6 | 24.4 | 29.8 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2938 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.1 | 24.6 | 24.4 | 29.8 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2941 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 24.4 | 24.8 | 30.2 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2945 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 24.3 | 25.3 | 30.5 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2948 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 24.3 | 25.3 | 30.5 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2952 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 24.3 | 25.7 | 31 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2955 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 24.5 | 26.1 | 31.2 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2959 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 25 | 26.5 | 31.8 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2962 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 25 | 26.5 | 31.8 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2966 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 25.3 | 26.8 | 32.1 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2969 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 25.8 | 27.2 | 32.6 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2973 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 28.5 | 27.8 | 32.8 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2976 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 28.5 | 27.8 | 32.8 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.298 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 30.1 | 28.1 | 33.1 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2983 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 30.6 | 28.3 | 33.3 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2987 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 31.4 | 28.7 | 33.7 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.299 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 31.4 | 28.7 | 33.7 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2993 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 32 | 29.2 | 34 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.2997 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 32.3 | 29.6 | 34.2 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 32.5 | 29.8 | 34.4 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3004 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 32.5 | 29.8 | 34.4 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3007 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 32.8 | 30.1 | 34.8 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3011 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 33.1 | 30.4 | 35.2 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3014 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 33.5 | 30.7 | 35.5 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3018 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 33.5 | 30.7 | 35.5 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3021 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 33.6 | 31 | 35.8 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3025 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 33.8 | 31.2 | 36 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3028 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 33.8 | 31.2 | 36 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3032 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 34.1 | 31.7 | 36.4 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3035 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 34.4 | 32.1 | 36.5 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3039 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 34.7 | 32.3 | 36.8 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3042 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 34.7 | 32.3 | 36.8 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3046 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 34.8 | 32.6 | 37.1 | - | - | 22.3 | 20 | 20 | - | - | 99 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3049 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 35.1 | 32.8 | 37.4 | - | - | 22.3 | 20 | 20 | - | - | 99 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3052 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 35.2 | 33 | 37.5 | - | - | 22.3 | 20 | 20 | - | - | 99 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3056 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 35.2 | 33 | 37.5 | - | - | 22.3 | 20 | 20 | - | - | 99 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3059 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 35.4 | 33.2 | 37.7 | - | - | 22.3 | 20 | 20 | - | - | 99 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3063 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 51.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 35.5 | 33.5 | 37.8 | - | - | 22.3 | 20 | 20 | - | - | 99 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3066 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 51.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 35.8 | 33.7 | 38 | - | - | 22.3 | 20 | 20 | - | - | 98 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.307 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 51.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 35.8 | 33.7 | 38 | - | - | 22.3 | 20 | 20 | - | - | 98 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3073 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 51.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.1 | 35.8 | 33.8 | 38.2 | - | - | 22.3 | 20 | 20 | - | - | 98 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3077 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 51 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 36.1 | 34.1 | 38.4 | - | - | 22.3 | 20 | 20 | - | - | 98 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.308 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 36.2 | 34.4 | 38.5 | - | - | 22.3 | 20 | 20 | - | - | 98 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3084 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 36.2 | 34.4 | 38.5 | - | - | 22.3 | 20 | 20 | - | - | 98 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3087 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 51.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 36.5 | 34.7 | 38.8 | - | - | 22.3 | 20 | 20 | - | - | 97 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3091 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 51.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 36.5 | 34.7 | 38.8 | - | - | 22.3 | 20 | 20 | - | - | 97 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3094 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 51.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 36.5 | 34.7 | 38.8 | - | - | 22.3 | 20 | 20 | - | - | 97 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3098 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 51 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 36.7 | 34.8 | 39 | - | - | 22.3 | 20 | 20 | - | - | 97 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3101 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 36.7 | 35 | 39 | - | - | 22.3 | 20 | 20 | - | - | 97 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3105 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 37 | 35.4 | 39.4 | - | - | 22.3 | 20 | 20 | - | - | 97 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3108 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 37 | 35.4 | 39.4 | - | - | 22.3 | 20 | 20 | - | - | 95 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3112 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 37.1 | 35.5 | 39.5 | - | - | 22.3 | 20 | 20 | - | - | 95 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3115 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 37.2 | 35.7 | 39.7 | - | - | 22.3 | 20 | 20 | - | - | 95 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3118 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 37.4 | 35.8 | 39.8 | - | - | 22.3 | 20 | 20 | - | - | 95 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3122 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 37.4 | 35.8 | 39.8 | - | - | 22.3 | 20 | 20 | - | - | 95 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3125 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 37.5 | 36.1 | 40 | - | - | 22.3 | 20 | 20 | - | - | 95 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3129 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 37.7 | 36.2 | 40.1 | - | - | 22.3 | 20 | 20 | - | - | 93 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3132 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 37.8 | 36.4 | 40.3 | - | - | 22.3 | 20 | 20 | - | - | 93 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3136 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 37.8 | 36.4 | 40.3 | - | - | 22.3 | 20 | 20 | - | - | 93 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3139 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 37.8 | 36.5 | 40.3 | - | - | 22.3 | 20 | 20 | - | - | 93 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3143 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 38 | 36.5 | 40.5 | - | - | 22.3 | 20 | 20 | - | - | 93 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3146 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 38 | 36.7 | 39.7 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.315 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 38 | 36.7 | 39.7 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3153 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 31.4 | 36.7 | 37.1 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3157 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 4.6 | 36.2 | 32.6 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.316 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | -0.7 | 35.5 | 30.7 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3164 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | -0.7 | 35.5 | 30.7 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3167 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 0.8 | 34.2 | 28.6 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3171 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 2.3 | 33.3 | 26.4 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3174 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 2.3 | 33.3 | 26.4 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3177 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 6.6 | 31.8 | 22 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3181 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 28.5 | 30.2 | 35.4 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3184 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 31.5 | 30.3 | 34.7 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3188 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 31.5 | 30.3 | 34.7 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3191 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 32.5 | 30.6 | 35.5 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3195 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.1 | 34 | 31.4 | 36.4 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3198 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 35 | 32.1 | 37.2 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3202 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 35 | 32.1 | 37.2 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3205 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 35.7 | 32.6 | 37.7 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3209 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 36.5 | 33.2 | 38.5 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3212 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 37.1 | 33.7 | 39.2 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3216 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 37.1 | 33.7 | 39.2 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3219 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 37.7 | 34.2 | 39.8 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3223 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 38.1 | 34.5 | 40.5 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3226 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 37.7 | 34.7 | 40.8 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.323 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 37.7 | 34.7 | 40.8 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3233 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 35.4 | 35.1 | 41.3 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3237 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 34.2 | 35.4 | 41.6 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.324 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 34 | 35.8 | 41.8 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3243 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 34 | 35.8 | 41.8 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3247 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 34.1 | 36.2 | 42.1 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.325 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 34.5 | 36.5 | 42.7 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3254 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 34.5 | 36.5 | 42.7 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3257 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 35.1 | 37.1 | 43.5 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3261 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 35.8 | 37.7 | 44.2 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3264 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 36.8 | 38.1 | 44.6 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3268 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 36.8 | 38.1 | 44.6 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3271 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 39.7 | 38.5 | 45.1 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3275 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 42 | 39 | 45.3 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3278 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 42.8 | 39.4 | 45.8 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3282 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 42.8 | 39.4 | 45.8 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3285 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 43.5 | 39.8 | 46.1 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3289 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 43.8 | 40.3 | 46.3 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3292 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 44.2 | 40.6 | 46.5 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3296 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 44.2 | 40.6 | 46.5 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3299 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.1 | 44.2 | 41.1 | 46.6 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3303 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 44.4 | 41.6 | 46.8 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3306 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 44.6 | 42 | 47.1 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3309 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 44.6 | 42 | 47.1 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3313 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 45 | 42.1 | 47.3 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3316 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 45.1 | 42.4 | 47.3 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.332 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45.3 | 42.7 | 47.6 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3323 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45.3 | 42.7 | 47.6 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3327 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 45.6 | 42.8 | 47.8 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.333 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45.8 | 43.1 | 47.7 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3334 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45.8 | 43.1 | 47.7 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3337 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 45.8 | 43.3 | 48 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3341 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 46.1 | 43.5 | 48.6 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3344 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 46.3 | 44 | 48.6 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3348 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 46.3 | 44 | 48.6 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3351 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46.3 | 44 | 48.6 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3355 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46.1 | 44.2 | 48.3 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3358 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 46.3 | 44.4 | 49.2 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3362 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 46.3 | 44.4 | 49.2 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3365 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 46.5 | 44.6 | 49.2 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3369 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 46.5 | 44.8 | 49.2 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3372 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 46.5 | 45 | 49 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3375 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 46.5 | 45 | 49 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3379 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 46.5 | 45.3 | 49.4 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3382 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 46.6 | 45.3 | 49.4 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3386 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 46.6 | 45.5 | 49.4 | - | - | 22.3 | 20 | 20 | - | - | 92 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3389 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46.6 | 45.5 | 49.4 | - | - | 22.3 | 20 | 20 | - | - | 92 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3393 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 50 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46.8 | 45.5 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 92 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3396 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47 | 45.6 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 92 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.34 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47 | 45.6 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 92 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3403 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47 | 45.8 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 92 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3407 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 46.8 | 46 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 84 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.341 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46.8 | 46 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 84 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3414 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46.8 | 46 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 84 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3417 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47 | 46.1 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 84 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3421 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47 | 46.1 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 84 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3424 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47 | 46.3 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 84 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3428 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47 | 46.3 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 75 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3431 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47 | 46.3 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 75 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3434 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.1 | 46.3 | 50 | - | - | 22.3 | 20 | 20 | - | - | 75 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3438 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.1 | 46.3 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 75 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3441 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.1 | 46.3 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 75 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3445 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47.1 | 46.5 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 75 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3448 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 47.2 | 46.5 | 50 | - | - | 22.3 | 20 | 20 | - | - | 66 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3452 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.2 | 46.5 | 50 | - | - | 22.3 | 20 | 20 | - | - | 66 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3455 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.2 | 46.5 | 50 | - | - | 22.3 | 20 | 20 | - | - | 66 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3459 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47.2 | 46.6 | 50 | - | - | 22.3 | 20 | 20 | - | - | 66 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3462 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.2 | 46.6 | 50 | - | - | 22.3 | 20 | 20 | - | - | 66 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3466 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 47.2 | 46.6 | 50 | - | - | 22.3 | 20 | 20 | - | - | 66 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3469 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 47.2 | 46.6 | 50 | - | - | 22.3 | 20 | 20 | - | - | 58 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3473 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.2 | 46.6 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 58 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3476 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 47.2 | 46.8 | 50 | - | - | 22.3 | 20 | 20 | - | - | 58 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.348 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 47.2 | 46.8 | 50 | - | - | 22.3 | 20 | 20 | - | - | 58 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3483 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.2 | 46.8 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 58 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3487 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.3 | 46.8 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 58 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.349 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.3 | 46.8 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 49 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3494 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.3 | 46.8 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 49 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3497 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.3 | 46.8 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 49 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.35 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.3 | 46.8 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 49 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3504 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47.3 | 47 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 49 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3507 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47.3 | 47 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 49 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3511 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.3 | 47 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 40 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3514 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.3 | 47 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 40 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3518 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47.3 | 47 | 50.4 | - | - | 22.3 | 20 | 20 | - | - | 40 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3521 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47.3 | 47 | 50.4 | - | - | 22.3 | 20 | 20 | - | - | 40 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3525 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.3 | 47 | 50.4 | - | - | 22.3 | 20 | 20 | - | - | 40 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3528 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47.3 | 47 | 50.4 | - | - | 22.3 | 20 | 20 | - | - | 40 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3532 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47.3 | 47.1 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 31 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3535 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47.3 | 47.1 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 31 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3539 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.3 | 47.1 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 31 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3542 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47.3 | 47.1 | 50.4 | - | - | 22.3 | 20 | 20 | - | - | 31 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3546 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47.5 | 47.1 | 50.4 | - | - | 22.3 | 20 | 20 | - | - | 31 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3549 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 47.5 | 47.1 | 50.4 | - | - | 22.3 | 20 | 20 | - | - | 31 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3553 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.5 | 47.2 | 50.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3556 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 47.3 | 47.2 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3559 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 47.3 | 47.2 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3563 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47.3 | 47.2 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3566 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 47.3 | 47.2 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.357 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.3 | 47.2 | 50.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3573 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.3 | 47.2 | 50.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3577 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.3 | 47.2 | 50 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.358 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47.3 | 47.3 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3584 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.3 | 47.3 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3587 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.3 | 47.3 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3591 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.3 | 47.3 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3594 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.3 | 47.3 | 50.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3598 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.3 | 47.3 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3601 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.3 | 47.3 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3605 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.2 | 47.3 | 50 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3608 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.2 | 47.3 | 50 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3612 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.3 | 47.3 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3615 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.3 | 47.3 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3619 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 47.3 | 47.3 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3622 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 47.3 | 47.3 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3625 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 47.3 | 47.3 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3629 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.3 | 47.3 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3632 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.3 | 47.3 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3636 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.3 | 47.3 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3639 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.3 | 47.3 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3643 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.3 | 47.3 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3646 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.3 | 47.3 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.365 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.3 | 47.5 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3653 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.3 | 47.5 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3657 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.3 | 47.3 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.366 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.3 | 47.3 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3664 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.3 | 47.5 | 50.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3667 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.3 | 47.5 | 50.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3671 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.5 | 47.5 | 50.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3674 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.3 | 47.5 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3678 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.3 | 47.3 | 47.5 | 50.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3681 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.3 | 47.3 | 47.5 | 50.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3684 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.3 | 47.3 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3688 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.2 | 47.3 | 50 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3691 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.2 | 47.3 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3695 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.2 | 47.3 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3698 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.3 | 47.3 | 50.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3702 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 47.5 | 47.2 | 50.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3705 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 47.5 | 47.2 | 50.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3709 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47.2 | 47.1 | 50 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3712 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 47.2 | 47.2 | 50 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3716 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.5 | 47.1 | 47.2 | 50 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3719 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.5 | 47.1 | 47.2 | 50 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3723 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.1 | 47 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3726 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47 | 47 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.373 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47 | 46.8 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3733 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47 | 46.8 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3737 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47 | 46.8 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.374 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 47 | 46.8 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3744 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46.8 | 46.6 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3747 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46.8 | 46.6 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.375 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.1 | 46.8 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3754 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47 | 46.6 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3757 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47 | 46.8 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3761 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47 | 46.8 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3764 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.1 | 46.8 | 50 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3768 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.1 | 46.8 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3771 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.1 | 46.8 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3775 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.1 | 46.8 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3778 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 47 | 46.8 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3782 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47 | 46.8 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3785 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47 | 46.8 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3789 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.1 | 46.8 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3792 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.1 | 47 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3796 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.1 | 47 | 50 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3799 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.1 | 47 | 50 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3803 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.1 | 47 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3806 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 47.1 | 47 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.381 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.2 | 47 | 50 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3813 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.2 | 47 | 50 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3816 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.2 | 47 | 50 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.382 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.1 | 47 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3823 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.2 | 47 | 50 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3827 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.2 | 47 | 50 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.383 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.2 | 47 | 50 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3834 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47.1 | 47 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3837 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.1 | 47 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3841 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.1 | 47 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3844 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 47.2 | 47 | 50 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3848 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.3 | 47 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3851 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.3 | 47 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3855 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47.3 | 47 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3858 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.1 | 47 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3862 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47 | 47 | 49.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3865 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47 | 47 | 49.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3869 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47 | 46.8 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3872 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.1 | 47 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3875 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47.1 | 46.6 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3879 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47.1 | 46.6 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3882 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 47.1 | 46.8 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3886 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 47.1 | 46.6 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3889 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.1 | 46.6 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3893 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.1 | 46.6 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3896 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.2 | 46.6 | 50 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.39 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47.2 | 46.8 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3903 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.2 | 46.6 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3907 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.2 | 46.6 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.391 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 47.1 | 46.6 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3914 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47.1 | 46.5 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3917 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 47.1 | 46.5 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3921 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 47.1 | 46.5 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3924 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.2 | 46.5 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3928 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.2 | 46.5 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3931 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.2 | 46.5 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3935 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.2 | 46.5 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3938 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.1 | 46.5 | 49.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3941 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.1 | 46.5 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3945 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.1 | 46.5 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3948 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.1 | 46.5 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3952 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47.2 | 46.5 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3955 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47.2 | 46.6 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3959 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47.2 | 46.6 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3962 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.1 | 46.6 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3966 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.2 | 46.5 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3969 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.2 | 46.5 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3973 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.2 | 46.5 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3976 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.2 | 46.6 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.398 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.2 | 46.6 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3983 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.2 | 46.5 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3987 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.2 | 46.5 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.399 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47.2 | 46.6 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3994 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47.2 | 46.6 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.3997 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47.2 | 46.6 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 47.2 | 46.6 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4004 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 47.2 | 46.8 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4007 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.2 | 46.8 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4011 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.2 | 46.8 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4014 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 47.2 | 46.8 | 49.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4018 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 46.3 | 46.8 | 49.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4021 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 45.5 | 46.6 | 49.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4025 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 45.5 | 46.6 | 49.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4028 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 44.8 | 46.6 | 49.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4032 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 44.6 | 46.6 | 50 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4035 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.3 | 44.6 | 46.6 | 50.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4039 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.3 | 44.6 | 46.6 | 50.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4042 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 44.6 | 46.6 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4046 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 44.6 | 47 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4049 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45.1 | 47 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4053 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45.1 | 47 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4056 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 46.3 | 47 | 50.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.406 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45.6 | 47 | 49.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4063 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 45.1 | 47 | 49.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4066 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 45.1 | 47 | 49.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.407 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45 | 47 | 49.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4073 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 44.8 | 47 | 49.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4077 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 44.8 | 47 | 49.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.408 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 49 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 44.8 | 47 | 49.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4084 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 44.8 | 47 | 49.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4087 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 44.8 | 47 | 49.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4091 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 44.8 | 47 | 49.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4094 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 44.8 | 47 | 49.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4098 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 44.6 | 46.8 | 49.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4101 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 44.6 | 46.8 | 49.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4105 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 44.6 | 46.8 | 49.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4108 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 44.6 | 46.8 | 49.4 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4112 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 44.6 | 46.8 | 49.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4115 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 44.6 | 46.8 | 49.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4119 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 44.6 | 46.8 | 49.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4122 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 44.6 | 46.6 | 49 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4126 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45.6 | 46.6 | 49.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4129 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 46.1 | 46.6 | 49 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4132 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 46.1 | 46.6 | 49 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4136 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 46.1 | 46.6 | 49 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4139 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 46.1 | 46.5 | 49 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4143 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 46.1 | 46.5 | 49.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4146 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 46.1 | 46.5 | 49.2 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.415 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 46.1 | 46.5 | 48.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4153 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46 | 46.3 | 48.3 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4157 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46 | 46.3 | 48.3 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.416 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46 | 46.3 | 48.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4164 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 45.8 | 46.1 | 48.3 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4167 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 45.6 | 46.1 | 48 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4171 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 45.6 | 46.1 | 48 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4174 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 45.6 | 46 | 48.3 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4178 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45 | 46 | 48.3 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4181 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 44 | 45.8 | 48.3 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4185 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 44 | 45.8 | 48.3 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4188 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 43.6 | 45.6 | 48 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4191 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 43.5 | 45.6 | 47.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4195 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 43.3 | 45.6 | 48 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4198 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 43.3 | 45.6 | 48 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4202 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 43.3 | 45.5 | 47.8 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4205 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 43.1 | 45.3 | 48.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4209 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 43.1 | 45.5 | 49 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4212 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 43.1 | 45.5 | 49 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4216 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 43.6 | 45.5 | 49 | - | - | 22.3 | 20 | 20 | - | - | 100 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4219 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 44.4 | 46.5 | 46.6 | - | - | 22.3 | 20 | 20 | - | - | 100 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4223 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 32 | 47 | 47.1 | - | - | 22.3 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4226 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 32 | 47 | 47.1 | - | - | 22.3 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.423 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.3 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 12.3 | 45.5 | 47.1 | - | - | 22.3 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4233 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.2 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 10.9 | 43.3 | 47.1 | - | - | 22.3 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4237 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.2 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 11.4 | 42.5 | 47.1 | - | - | 22.3 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.424 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.2 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 11.4 | 42.5 | 47.1 | - | - | 22.3 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4244 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.1 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 11.9 | 42.4 | 47.1 | - | - | 22.3 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4247 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.1 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 12.3 | 42.4 | 47 | - | - | 22.3 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4251 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 0 | 12.3 | 42.4 | 47 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4254 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 29.7 | 12.1 | 42.7 | 46.8 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4257 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 18.7 | 44.6 | 45.1 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4261 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 36 | 43.3 | 44.6 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4264 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 36 | 43.3 | 44.6 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4268 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 41.6 | 42.5 | 45.8 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4271 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 41 | 42.4 | 44.8 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4275 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 40.5 | 42.4 | 44.6 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4278 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 40.5 | 42.4 | 44.6 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4282 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 40.3 | 42.1 | 44.4 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4285 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 40.1 | 42.2 | 44.4 | - | - | 22.3 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4289 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 40 | 42.1 | 44.4 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4292 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 40 | 42.1 | 44.4 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4296 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 40 | 42.1 | 44.6 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4299 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 40 | 42.1 | 44.4 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4303 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 40 | 42.1 | 44.2 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4306 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 40 | 42.1 | 44.2 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.431 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 40 | 42.1 | 44.6 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4313 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 40 | 42.1 | 44.8 | - | - | 22 | 20 | 20 | - | - | 96 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4316 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 40 | 42.1 | 44.8 | - | - | 22 | 20 | 20 | - | - | 96 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.432 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 40 | 42.1 | 44.8 | - | - | 22 | 20 | 20 | - | - | 96 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4323 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 40 | 42.2 | 44.8 | - | - | 22 | 20 | 20 | - | - | 96 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4327 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 40.1 | 42.2 | 45.1 | - | - | 22 | 20 | 20 | - | - | 96 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.433 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 40.1 | 42.2 | 45.1 | - | - | 22 | 20 | 20 | - | - | 96 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4334 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 40.1 | 42.2 | 45.8 | - | - | 22 | 20 | 20 | - | - | 94 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4337 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 40.3 | 42.4 | 46.3 | - | - | 22 | 20 | 20 | - | - | 94 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4341 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 40.8 | 42.4 | 46.1 | - | - | 22 | 20 | 20 | - | - | 94 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4344 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 40.8 | 42.4 | 46.1 | - | - | 22 | 20 | 20 | - | - | 94 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4348 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 43.1 | 42.7 | 46.3 | - | - | 22 | 20 | 20 | - | - | 94 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4351 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 43.6 | 42.7 | 46.1 | - | - | 22 | 20 | 20 | - | - | 94 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4355 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 43.8 | 42.7 | 46.1 | - | - | 22 | 20 | 20 | - | - | 91 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4358 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.3 | 43.8 | 42.7 | 46.1 | - | - | 22 | 20 | 20 | - | - | 91 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4362 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 44.2 | 42.8 | 46.6 | - | - | 22 | 20 | 20 | - | - | 91 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4365 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 44.6 | 43 | 47.1 | - | - | 22 | 20 | 20 | - | - | 91 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4369 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 44.6 | 43.1 | 47.1 | - | - | 22 | 20 | 20 | - | - | 91 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4372 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 44.6 | 43.1 | 47.1 | - | - | 22 | 20 | 20 | - | - | 91 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4376 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 44.8 | 43.3 | 47.1 | - | - | 22 | 20 | 20 | - | - | 89 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4379 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 44.8 | 43.6 | 47.1 | - | - | 22 | 20 | 20 | - | - | 89 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4382 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 44.8 | 43.6 | 47.1 | - | - | 22 | 20 | 20 | - | - | 89 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4386 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 45 | 43.6 | 47.1 | - | - | 22 | 20 | 20 | - | - | 89 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4389 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 45 | 43.6 | 47.1 | - | - | 22 | 20 | 20 | - | - | 89 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4393 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45.1 | 43.8 | 47.2 | - | - | 22 | 20 | 20 | - | - | 89 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4396 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45.1 | 43.8 | 47.2 | - | - | 22 | 20 | 20 | - | - | 86 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.44 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45.3 | 43.8 | 47.3 | - | - | 22 | 20 | 20 | - | - | 86 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4403 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 45.5 | 43.8 | 47.6 | - | - | 22 | 20 | 20 | - | - | 86 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4407 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45.6 | 44.2 | 47.8 | - | - | 22 | 20 | 20 | - | - | 86 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.441 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45.6 | 44.2 | 47.8 | - | - | 22 | 20 | 20 | - | - | 86 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4414 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.1 | 45.6 | 44.2 | 47.7 | - | - | 22 | 20 | 20 | - | - | 86 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4417 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 45.6 | 44.4 | 47.6 | - | - | 22 | 20 | 20 | - | - | 83 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4421 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 45.6 | 44.6 | 47.6 | - | - | 22 | 20 | 20 | - | - | 83 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4424 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 45.6 | 44.6 | 47.6 | - | - | 22 | 20 | 20 | - | - | 83 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4428 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 45.8 | 44.8 | 47.7 | - | - | 22 | 20 | 20 | - | - | 83 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4431 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46 | 44.8 | 47.8 | - | - | 22 | 20 | 20 | - | - | 83 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4435 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 46.1 | 44.8 | 47.8 | - | - | 22 | 20 | 20 | - | - | 83 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4438 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 46.1 | 44.8 | 47.8 | - | - | 22 | 20 | 20 | - | - | 79 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4442 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 46.1 | 44.8 | 47.7 | - | - | 22 | 20 | 20 | - | - | 79 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4445 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 46.1 | 45 | 48 | - | - | 22 | 20 | 20 | - | - | 79 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4448 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46.1 | 45.1 | 48 | - | - | 22 | 20 | 20 | - | - | 79 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4452 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46.1 | 45.1 | 48 | - | - | 22 | 20 | 20 | - | - | 79 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4455 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46 | 45.3 | 47.8 | - | - | 22 | 20 | 20 | - | - | 79 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4459 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46.1 | 45.3 | 48 | - | - | 22 | 20 | 20 | - | - | 69 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4462 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46.1 | 45.3 | 48 | - | - | 22 | 20 | 20 | - | - | 69 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4466 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46.3 | 45.3 | 48.3 | - | - | 22 | 20 | 20 | - | - | 69 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4469 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46.3 | 45.5 | 48.3 | - | - | 22 | 20 | 20 | - | - | 69 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4473 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 46.1 | 45.5 | 47.8 | - | - | 22 | 20 | 20 | - | - | 69 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4476 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 46.1 | 45.5 | 47.8 | - | - | 22 | 20 | 20 | - | - | 69 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.448 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 46 | 45.5 | 47.8 | - | - | 22 | 20 | 20 | - | - | 59 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4483 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 46.3 | 45.6 | 48.6 | - | - | 22 | 20 | 20 | - | - | 59 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4487 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 46.5 | 45.6 | 48.6 | - | - | 22 | 20 | 20 | - | - | 59 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.449 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 46.5 | 45.6 | 48.6 | - | - | 22 | 20 | 20 | - | - | 59 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4494 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 46.6 | 45.6 | 49 | - | - | 22 | 20 | 20 | - | - | 59 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4497 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 46.5 | 45.6 | 48.3 | - | - | 22 | 20 | 20 | - | - | 59 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4501 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46.3 | 45.8 | 48 | - | - | 22 | 20 | 20 | - | - | 48 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4504 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46.3 | 45.8 | 48 | - | - | 22 | 20 | 20 | - | - | 48 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4507 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 46.1 | 45.8 | 48 | - | - | 22 | 20 | 20 | - | - | 48 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4511 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46.5 | 45.8 | 48.6 | - | - | 22 | 20 | 20 | - | - | 48 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4514 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 46.6 | 45.8 | 49.2 | - | - | 22 | 20 | 20 | - | - | 48 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4518 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 46.6 | 45.8 | 49.2 | - | - | 22 | 20 | 20 | - | - | 48 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4521 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46.8 | 46 | 49.2 | - | - | 22 | 20 | 20 | - | - | 38 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4525 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46.6 | 46 | 49 | - | - | 22 | 20 | 20 | - | - | 38 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4528 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46.3 | 46.1 | 48.3 | - | - | 22 | 20 | 20 | - | - | 38 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4532 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46.3 | 46.1 | 48.3 | - | - | 22 | 20 | 20 | - | - | 38 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4535 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46.3 | 46 | 48.3 | - | - | 22 | 20 | 20 | - | - | 38 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4539 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 46.5 | 46.1 | 49 | - | - | 22 | 20 | 20 | - | - | 38 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4542 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 46.5 | 46.1 | 49 | - | - | 22 | 20 | 20 | - | - | 38 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4546 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46.6 | 46.3 | 49 | - | - | 22 | 20 | 20 | - | - | 28 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4549 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 46.6 | 46.1 | 49 | - | - | 22 | 20 | 20 | - | - | 28 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4553 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46.5 | 46.1 | 48.3 | - | - | 22 | 20 | 20 | - | - | 28 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4556 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46.5 | 46.1 | 48.3 | - | - | 22 | 20 | 20 | - | - | 28 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.456 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 46.5 | 46.1 | 48.6 | - | - | 22 | 20 | 20 | - | - | 28 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4563 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 46.5 | 46.1 | 48.6 | - | - | 22 | 20 | 20 | - | - | 28 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4567 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 46.5 | 46.1 | 48.6 | - | - | 22 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.457 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 46.5 | 46.1 | 48.6 | - | - | 22 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4573 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 48 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 46.5 | 46.3 | 48.6 | - | - | 22.3 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4577 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46.5 | 46.3 | 48.6 | - | - | 22 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.458 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 46.3 | 46.1 | 48.3 | - | - | 22 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4584 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 46.3 | 46.1 | 48.3 | - | - | 22 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4587 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 46 | 46.1 | 48.3 | - | - | 22 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4591 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 46 | 46.1 | 48.6 | - | - | 22 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4594 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 45.3 | 46.3 | 49 | - | - | 22 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4598 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 45.3 | 46.3 | 49 | - | - | 22 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4601 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.9 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 44.4 | 46.3 | 48.6 | - | - | 22 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4605 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 44.4 | 46.3 | 48.3 | - | - | 22 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4608 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 44.4 | 46.3 | 48.3 | - | - | 22 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4612 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.8 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 44.6 | 46.3 | 48.3 | - | - | 22 | 20 | 20 | - | - | 100 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4615 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.8 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 45 | 46.3 | 47.6 | - | - | 22 | 20 | 20 | - | - | 100 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4619 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.8 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 27.7 | 42 | 47.1 | 46.5 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4622 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.8 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 27.7 | 42 | 47.1 | 46.5 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4626 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.8 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 30.7 | 46.1 | 47 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4629 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.7 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 26.8 | 42.1 | 47.1 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4632 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.7 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 25.3 | 41.1 | 47.1 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4636 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.7 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 25.3 | 41.1 | 47.1 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4639 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.5 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 24.2 | 40.6 | 47.1 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4643 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.5 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 23.2 | 40.8 | 47 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4646 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.4 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 22.2 | 41.3 | 47 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.465 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.4 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 22.2 | 41.3 | 47 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4653 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.3 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 21.3 | 41.8 | 46.8 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4657 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.3 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 20.8 | 42.2 | 46.6 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.466 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.3 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 21 | 43.1 | 46.5 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4664 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.3 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 21 | 43.1 | 46.5 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4667 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.3 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 21 | 43.6 | 46.1 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4671 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.3 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 21 | 44.2 | 46 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4674 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.3 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 20.8 | 44.6 | 45.8 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4678 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.3 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 20.8 | 44.6 | 45.8 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4681 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 0 | 20.8 | 44.8 | 45.6 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4685 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 24.2 | 44.4 | 45 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4688 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 24.2 | 44.4 | 45 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4692 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 38.2 | 42.8 | 44.4 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4695 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 41.3 | 42 | 45 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4698 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 42 | 42 | 44.4 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4702 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 42 | 42 | 44.4 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4705 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 42 | 42 | 44.4 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4709 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 42.2 | 42 | 44.4 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4712 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 42.2 | 42.1 | 44.6 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4716 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 42.2 | 42.1 | 44.6 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4719 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 42.4 | 42.2 | 44.8 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4723 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 42.2 | 42.2 | 44.6 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4726 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 42.2 | 42.2 | 44.8 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.473 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 42.2 | 42.2 | 44.8 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4733 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 42.2 | 42.4 | 45 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4737 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 42.2 | 42.4 | 45.1 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.474 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 42.4 | 42.5 | 45.3 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4744 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 42.4 | 42.5 | 45.3 | - | - | 22 | 20 | 20 | - | - | 96 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4747 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 42 | 42.5 | 45.5 | - | - | 22 | 20 | 20 | - | - | 96 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4751 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 41.1 | 42.7 | 45.6 | - | - | 22 | 20 | 20 | - | - | 96 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4754 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 41 | 42.7 | 45.6 | - | - | 22 | 20 | 20 | - | - | 96 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4758 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 41 | 42.8 | 45.8 | - | - | 22 | 20 | 20 | - | - | 96 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4761 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 41 | 42.8 | 45.8 | - | - | 22 | 20 | 20 | - | - | 96 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4764 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 41 | 42.8 | 45.8 | - | - | 22 | 20 | 20 | - | - | 92 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4768 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 41 | 42.8 | 45.8 | - | - | 22 | 20 | 20 | - | - | 92 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4771 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 41 | 42.8 | 46 | - | - | 22 | 20 | 20 | - | - | 92 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4775 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 41 | 43.1 | 46.1 | - | - | 22.3 | 20 | 20 | - | - | 92 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4778 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 41.1 | 43 | 46 | - | - | 22 | 20 | 20 | - | - | 92 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4782 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 41.1 | 43 | 46 | - | - | 22 | 20 | 20 | - | - | 92 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4785 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 41.1 | 43.1 | 46.1 | - | - | 22 | 20 | 20 | - | - | 88 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4789 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 41.1 | 43.1 | 46.8 | - | - | 22 | 20 | 20 | - | - | 88 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4792 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 41.3 | 43.1 | 47.1 | - | - | 22 | 20 | 20 | - | - | 88 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4796 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 41.3 | 43.1 | 47.1 | - | - | 22 | 20 | 20 | - | - | 88 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4799 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 41.5 | 43.3 | 47.2 | - | - | 22 | 20 | 20 | - | - | 88 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4803 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 41.8 | 43.5 | 47.1 | - | - | 22 | 20 | 20 | - | - | 88 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4806 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 44.2 | 43.6 | 46.8 | - | - | 22 | 20 | 20 | - | - | 85 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.481 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 44.2 | 43.6 | 46.8 | - | - | 22 | 20 | 20 | - | - | 85 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4813 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 44.4 | 43.6 | 46.6 | - | - | 22 | 20 | 20 | - | - | 85 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4817 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 44.4 | 43.8 | 46.6 | - | - | 22 | 20 | 20 | - | - | 85 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.482 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 45 | 43.8 | 47.1 | - | - | 22 | 20 | 20 | - | - | 85 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4823 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 45 | 43.8 | 47.1 | - | - | 22 | 20 | 20 | - | - | 85 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4827 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 45.1 | 43.8 | 47.2 | - | - | 22 | 20 | 20 | - | - | 82 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.483 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45.1 | 44 | 47.2 | - | - | 22 | 20 | 20 | - | - | 82 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4834 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 45 | 44 | 47 | - | - | 22 | 20 | 20 | - | - | 82 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4837 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 45 | 44 | 47 | - | - | 22 | 20 | 20 | - | - | 82 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4841 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 45 | 44 | 47 | - | - | 22 | 20 | 20 | - | - | 82 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4844 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 44.8 | 44.2 | 47 | - | - | 22 | 20 | 20 | - | - | 82 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4848 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 44.8 | 44.2 | 47 | - | - | 22 | 20 | 20 | - | - | 78 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4851 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45.1 | 44.2 | 47.2 | - | - | 22 | 20 | 20 | - | - | 78 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4855 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 45.3 | 44.2 | 47.3 | - | - | 22 | 20 | 20 | - | - | 78 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4858 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45.3 | 44.2 | 47.3 | - | - | 22 | 20 | 20 | - | - | 78 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4862 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45.3 | 44.2 | 47.3 | - | - | 22 | 20 | 20 | - | - | 78 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4865 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 45.3 | 44.4 | 47.2 | - | - | 22 | 20 | 20 | - | - | 78 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4869 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 45.3 | 44.6 | 47.3 | - | - | 22 | 20 | 20 | - | - | 74 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4872 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45.3 | 44.6 | 47.3 | - | - | 22 | 20 | 20 | - | - | 74 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4876 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45.3 | 44.6 | 47.3 | - | - | 22 | 20 | 20 | - | - | 74 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4879 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 45.3 | 44.6 | 47.3 | - | - | 22 | 20 | 20 | - | - | 74 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4883 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 45.3 | 44.8 | 47.3 | - | - | 22 | 20 | 20 | - | - | 74 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4886 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45.5 | 44.8 | 47.5 | - | - | 22 | 20 | 20 | - | - | 74 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4889 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45.5 | 44.8 | 47.5 | - | - | 22 | 20 | 20 | - | - | 70 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4893 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 45.5 | 44.8 | 47.5 | - | - | 22 | 20 | 20 | - | - | 70 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4896 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45.5 | 45 | 47.3 | - | - | 22 | 20 | 20 | - | - | 70 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.49 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 45.5 | 45 | 47.3 | - | - | 22 | 20 | 20 | - | - | 70 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4903 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 45.5 | 45 | 47.3 | - | - | 22 | 20 | 20 | - | - | 70 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4907 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 45.5 | 45 | 47.5 | - | - | 22 | 20 | 20 | - | - | 70 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.491 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 45.6 | 45 | 47.6 | - | - | 22 | 20 | 20 | - | - | 66 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4914 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 45.6 | 45.1 | 47.6 | - | - | 22 | 20 | 20 | - | - | 66 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4917 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 45.6 | 45.1 | 47.6 | - | - | 22 | 20 | 20 | - | - | 66 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4921 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45.6 | 45.1 | 47.6 | - | - | 22 | 20 | 20 | - | - | 66 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4924 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 45.6 | 45.1 | 47.6 | - | - | 22 | 20 | 20 | - | - | 66 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4928 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 45.6 | 45.1 | 47.6 | - | - | 22 | 20 | 20 | - | - | 66 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4931 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 45.6 | 45.1 | 47.6 | - | - | 22 | 20 | 20 | - | - | 55 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4935 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 45.6 | 45.1 | 47.6 | - | - | 22 | 20 | 20 | - | - | 55 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4938 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 45.6 | 45.1 | 47.6 | - | - | 22 | 20 | 20 | - | - | 55 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4942 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 45.6 | 45.1 | 47.6 | - | - | 22 | 20 | 20 | - | - | 55 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4945 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 45.6 | 45.3 | 47.6 | - | - | 22 | 20 | 20 | - | - | 55 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4948 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 45.6 | 45.3 | 47.6 | - | - | 22 | 20 | 20 | - | - | 55 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4952 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.3 | 45.6 | 45.3 | 47.6 | - | - | 22 | 20 | 20 | - | - | 44 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4955 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.3 | 45.6 | 45.3 | 47.6 | - | - | 22 | 20 | 20 | - | - | 44 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4959 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 45.8 | 45.5 | 47.7 | - | - | 22 | 20 | 20 | - | - | 44 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4962 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 45.8 | 45.5 | 47.7 | - | - | 22 | 20 | 20 | - | - | 44 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4966 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.3 | 45.8 | 45.5 | 47.6 | - | - | 22 | 20 | 20 | - | - | 44 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4969 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.3 | 45.8 | 45.5 | 47.6 | - | - | 22 | 20 | 20 | - | - | 44 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4973 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 45.8 | 45.5 | 47.7 | - | - | 22 | 20 | 20 | - | - | 33 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4976 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45.8 | 45.5 | 47.7 | - | - | 22 | 20 | 20 | - | - | 33 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.498 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 45.8 | 45.5 | 47.7 | - | - | 22 | 20 | 20 | - | - | 33 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4983 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 45.8 | 45.5 | 47.7 | - | - | 22 | 20 | 20 | - | - | 33 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4987 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 45.5 | 45.5 | 47.6 | - | - | 22 | 20 | 20 | - | - | 33 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.499 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 45.5 | 45.5 | 47.7 | - | - | 22 | 20 | 20 | - | - | 33 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4994 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45.5 | 45.5 | 47.7 | - | - | 22 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.4997 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47.1 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45.5 | 45.5 | 47.7 | - | - | 22 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5001 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 45.5 | 45.6 | 47.7 | - | - | 22 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5004 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 45.1 | 45.6 | 47.7 | - | - | 22 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5008 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 45.1 | 45.6 | 47.7 | - | - | 22 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5011 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 45.1 | 45.6 | 47.6 | - | - | 22 | 20 | 20 | - | - | 25 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5014 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 45.1 | 45.6 | 47.6 | - | - | 22 | 20 | 20 | - | - | 100 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5018 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 43.8 | 46.3 | 46.5 | - | - | 22 | 20 | 20 | - | - | 100 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5021 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 28.1 | 43.8 | 46.3 | 46.5 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5025 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 34.8 | 46.5 | 46.5 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5028 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 47 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 28.7 | 43.8 | 46.5 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5032 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 26.6 | 42 | 46.5 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5035 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 26.6 | 42 | 46.5 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5039 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 25.4 | 41.1 | 46.5 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5042 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.7 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 24.3 | 40.8 | 46.5 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5046 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.6 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 23.6 | 40.8 | 46.5 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5049 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.6 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 23.6 | 40.8 | 46.5 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5053 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 22.7 | 41.3 | 46.3 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5056 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 22.2 | 41.6 | 46.1 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.506 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 22 | 42.4 | 46 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5063 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 22 | 42.4 | 46 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5067 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 22 | 42.8 | 45.8 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.507 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 21.7 | 43.3 | 45.6 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5073 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 21.7 | 43.3 | 45.6 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5077 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 21.4 | 43.6 | 45.5 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.508 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 21.3 | 44 | 45.3 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5084 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.4 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 21.3 | 44.2 | 45.1 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5087 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.4 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 21.3 | 44.2 | 45.1 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5091 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 21.3 | 44.4 | 45 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5094 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 21.3 | 44.4 | 44.8 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5098 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 21.2 | 44.4 | 44.4 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5101 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 21.2 | 44.4 | 44.4 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5105 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 0 | 21.1 | 44.4 | 44.2 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5108 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 21.5 | 43.5 | 44 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5112 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 37.2 | 41.8 | 43.3 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5115 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 37.2 | 41.8 | 43.3 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5119 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 40.3 | 40.8 | 43.8 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5122 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 41 | 40.8 | 43.1 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5126 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 41.1 | 40.6 | 43.3 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5129 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 41.1 | 40.6 | 43.3 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5133 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 41.3 | 40.8 | 43.3 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5136 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 41.5 | 41.1 | 43.5 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5139 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 41.5 | 41.1 | 43.5 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5143 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 41.5 | 41.1 | 43.5 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5146 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 41.5 | 41.1 | 43.5 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.515 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 41.5 | 41.3 | 44 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5153 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 41.5 | 41.3 | 44 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5157 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 41.5 | 41.5 | 44.2 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.516 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 41.3 | 41.5 | 44.2 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5164 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 41.3 | 41.6 | 44.2 | - | - | 22 | 20 | 20 | - | - | 96 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5167 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 41.3 | 41.6 | 44.2 | - | - | 22 | 20 | 20 | - | - | 96 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5171 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 41.3 | 41.6 | 44.6 | - | - | 22 | 20 | 20 | - | - | 96 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5174 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 40.5 | 41.8 | 44.8 | - | - | 22 | 20 | 20 | - | - | 96 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5178 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 40.1 | 41.8 | 44.8 | - | - | 22 | 20 | 20 | - | - | 96 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5181 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 40.1 | 41.8 | 44.8 | - | - | 22 | 20 | 20 | - | - | 96 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5185 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 40.1 | 42 | 44.6 | - | - | 22 | 20 | 20 | - | - | 96 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5188 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 40.1 | 42 | 44.6 | - | - | 22 | 20 | 20 | - | - | 92 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5192 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 40.3 | 42 | 44.8 | - | - | 22 | 20 | 20 | - | - | 92 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5195 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 40.3 | 42 | 44.8 | - | - | 22 | 20 | 20 | - | - | 92 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5198 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 40.3 | 42.1 | 45.1 | - | - | 22 | 20 | 20 | - | - | 92 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5202 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 40.3 | 42.2 | 45 | - | - | 22 | 20 | 20 | - | - | 92 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5205 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 40.5 | 42.4 | 45 | - | - | 22 | 20 | 20 | - | - | 92 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5209 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 40.5 | 42.4 | 45 | - | - | 22 | 20 | 20 | - | - | 88 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5212 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 40.5 | 42.4 | 45 | - | - | 22 | 20 | 20 | - | - | 88 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5216 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 40.8 | 42.2 | 45.1 | - | - | 22 | 20 | 20 | - | - | 88 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5219 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 40.6 | 42.4 | 45.3 | - | - | 22 | 20 | 20 | - | - | 88 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5223 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 40.6 | 42.4 | 45.3 | - | - | 22 | 20 | 20 | - | - | 88 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5226 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 40.6 | 42.4 | 45.5 | - | - | 22 | 20 | 20 | - | - | 88 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.523 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 40.6 | 42.5 | 45.5 | - | - | 22 | 20 | 20 | - | - | 84 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5233 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 40.6 | 42.5 | 45.5 | - | - | 22 | 20 | 20 | - | - | 84 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5237 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 40.6 | 42.5 | 45.3 | - | - | 22 | 20 | 20 | - | - | 84 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.524 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 40.6 | 42.5 | 45.5 | - | - | 22 | 20 | 20 | - | - | 84 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5244 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 40.6 | 42.7 | 45.6 | - | - | 22 | 20 | 20 | - | - | 84 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5247 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 40.6 | 42.7 | 45.6 | - | - | 22 | 20 | 20 | - | - | 84 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5251 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 40.8 | 42.8 | 45.6 | - | - | 22 | 20 | 20 | - | - | 80 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5254 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 41 | 42.8 | 45.8 | - | - | 22 | 20 | 20 | - | - | 80 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5258 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 41 | 42.8 | 45.8 | - | - | 22 | 20 | 20 | - | - | 80 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5261 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.8 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 41 | 42.8 | 45.8 | - | - | 22 | 20 | 20 | - | - | 80 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5264 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 41 | 42.8 | 45.8 | - | - | 22 | 20 | 20 | - | - | 80 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5268 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 41.1 | 43 | 46 | - | - | 22 | 20 | 20 | - | - | 80 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5271 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 41.3 | 43.1 | 46 | - | - | 22 | 20 | 20 | - | - | 76 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5275 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 41.3 | 43.1 | 46 | - | - | 22 | 20 | 20 | - | - | 76 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5278 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 41.3 | 43.1 | 46.1 | - | - | 22 | 20 | 20 | - | - | 76 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5282 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.7 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 41.5 | 43.1 | 46.1 | - | - | 22 | 20 | 20 | - | - | 76 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5285 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 41.5 | 43.3 | 46.3 | - | - | 22 | 20 | 20 | - | - | 76 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5289 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 41.5 | 43.3 | 46.3 | - | - | 22 | 20 | 20 | - | - | 76 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5292 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 41.5 | 43.3 | 46.5 | - | - | 22 | 20 | 20 | - | - | 73 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5296 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 41.6 | 43.5 | 46.5 | - | - | 22 | 20 | 20 | - | - | 73 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5299 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 41.8 | 43.5 | 46.5 | - | - | 22 | 20 | 20 | - | - | 73 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5303 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 41.8 | 43.5 | 46.3 | - | - | 22 | 20 | 20 | - | - | 73 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5306 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 41.8 | 43.6 | 46.3 | - | - | 22 | 20 | 20 | - | - | 73 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.531 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 41.8 | 43.6 | 46.5 | - | - | 22 | 20 | 20 | - | - | 73 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5313 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 41.8 | 43.6 | 46.5 | - | - | 22 | 20 | 20 | - | - | 69 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5317 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 42.1 | 43.6 | 46.5 | - | - | 22 | 20 | 20 | - | - | 69 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.532 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 43 | 43.8 | 46.5 | - | - | 22 | 20 | 20 | - | - | 69 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5324 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 43.6 | 43.8 | 46.5 | - | - | 22 | 20 | 20 | - | - | 69 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5327 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 43.6 | 43.8 | 46.5 | - | - | 22 | 20 | 20 | - | - | 69 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.533 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 43.6 | 43.8 | 46.5 | - | - | 22 | 20 | 20 | - | - | 69 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5334 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 43.8 | 43.8 | 46.6 | - | - | 22 | 20 | 20 | - | - | 65 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5337 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 43.8 | 43.8 | 46.5 | - | - | 22 | 20 | 20 | - | - | 65 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5341 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 43.8 | 43.8 | 46.5 | - | - | 22 | 20 | 20 | - | - | 65 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5344 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.6 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 43.8 | 43.8 | 46.5 | - | - | 22 | 20 | 20 | - | - | 65 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5348 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.3 | 43.8 | 43.8 | 46.6 | - | - | 22 | 20 | 20 | - | - | 65 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5351 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 43.8 | 43.8 | 46.6 | - | - | 22 | 20 | 20 | - | - | 65 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5355 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 43.8 | 43.8 | 46.6 | - | - | 22 | 20 | 20 | - | - | 61 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5358 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 43.8 | 44 | 46.6 | - | - | 22 | 20 | 20 | - | - | 61 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5362 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 43.8 | 44 | 46.6 | - | - | 22 | 20 | 20 | - | - | 61 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5365 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 44 | 44 | 46.6 | - | - | 22 | 20 | 20 | - | - | 61 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5369 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 44 | 44 | 46.6 | - | - | 22 | 20 | 20 | - | - | 61 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5372 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 44 | 44 | 46.6 | - | - | 22 | 20 | 20 | - | - | 61 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5376 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 44 | 44 | 46.6 | - | - | 22 | 20 | 20 | - | - | 57 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5379 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 44 | 44 | 46.6 | - | - | 22 | 20 | 20 | - | - | 57 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5383 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 44 | 44 | 46.6 | - | - | 22 | 20 | 20 | - | - | 57 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5386 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 44 | 43.8 | 46.6 | - | - | 22 | 20 | 20 | - | - | 57 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5389 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 43.8 | 44 | 46.6 | - | - | 22 | 20 | 20 | - | - | 57 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5393 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 43.8 | 44 | 46.6 | - | - | 22 | 20 | 20 | - | - | 57 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5396 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 43.8 | 44 | 46.8 | - | - | 22 | 20 | 20 | - | - | 53 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.54 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 43.6 | 43.8 | 46.5 | - | - | 22 | 20 | 20 | - | - | 53 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5403 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 43.6 | 43.8 | 46.5 | - | - | 22 | 20 | 20 | - | - | 53 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5407 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 43.6 | 43.8 | 46.5 | - | - | 22 | 20 | 20 | - | - | 53 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.541 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 43.8 | 43.8 | 46.6 | - | - | 22 | 20 | 20 | - | - | 53 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5414 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 43.5 | 43.8 | 46.6 | - | - | 22 | 20 | 20 | - | - | 53 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5417 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 43 | 44 | 46.8 | - | - | 22 | 20 | 20 | - | - | 49 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5421 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 43 | 44 | 46.8 | - | - | 22 | 20 | 20 | - | - | 49 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5424 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 42.8 | 44 | 46.8 | - | - | 22 | 20 | 20 | - | - | 49 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5428 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 42.8 | 44.6 | 46.1 | - | - | 22 | 20 | 20 | - | - | 100 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5431 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 41.6 | 45.1 | 44.8 | - | - | 22 | 20 | 20 | - | - | 100 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5435 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 27.7 | 41.6 | 45.1 | 44.8 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5438 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 30.1 | 44.8 | 45.1 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5442 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 26.8 | 40.5 | 45.1 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5445 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.4 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 25.5 | 39.4 | 45.1 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5449 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.4 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 25.5 | 39.4 | 45.1 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5452 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.3 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 24.8 | 39 | 45.1 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5455 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.3 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 23.8 | 38.7 | 45.1 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5459 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.3 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 23.8 | 38.7 | 45.1 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5462 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.3 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 23 | 38.7 | 45 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5466 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.3 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 22.3 | 39.1 | 45 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5469 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.2 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 21.8 | 39.5 | 44.8 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5473 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.2 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 21.8 | 39.5 | 44.8 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5476 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.2 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 21.6 | 40.3 | 44.6 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.548 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.2 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 21.5 | 41 | 44.4 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5483 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.2 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 21.5 | 41.5 | 44.2 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5487 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.2 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 21.5 | 41.5 | 44.2 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.549 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.3 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 21.4 | 42 | 43.8 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5494 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.2 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 21.2 | 42.2 | 43.6 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5497 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.2 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 21 | 42.4 | 43.5 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5501 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.2 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 21 | 42.4 | 43.5 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5504 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.3 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 20.7 | 42.7 | 43.3 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5508 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.3 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 20.6 | 42.8 | 43.1 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5511 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.3 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 20.4 | 42.8 | 43 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5514 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.3 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 20.4 | 42.8 | 43 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5518 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.2 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 20.2 | 42.8 | 42.7 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5521 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.2 | 0 | 30 | 30 | Water Out | Off | Off | Off | Room | Off | Off | Off | Off | - | 0 | Off | 0 | 20.1 | 42.8 | 42.5 | - | - | 22 | 20 | 20 | - | - | 0 | Off | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5525 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 0 | 20.1 | 42.8 | 42.5 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5528 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.9 | 20.1 | 41.1 | 40.8 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5532 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.2 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 31.7 | 40.1 | 41.5 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5535 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 38.5 | 39.8 | 41.8 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5539 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.3 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 28.1 | 38.5 | 39.8 | 41.8 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5542 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 39.8 | 39.1 | 42.1 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5546 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 39.8 | 39.2 | 42 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5549 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 40 | 39.5 | 42.1 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5553 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.5 | 40 | 39.5 | 42.1 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5556 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 40.1 | 39.7 | 42.4 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.556 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.4 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 40.3 | 39.8 | 42.4 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5563 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 40.3 | 40 | 42.4 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5567 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 40.3 | 40 | 42.4 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.557 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 40.3 | 40 | 43 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5574 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.7 | 40.3 | 40.1 | 43.1 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.5577 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 40.1 | 40.3 | 43 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000
46023.558 | - | On | Off | Heat | 0 | Off | 0 | Off | Eco | 30 | 30 | 32 | 46.5 | 0 | 30 | 30 | Water Out | On | Off | On | Room | On | Off | Off | Off | - | 0 | Off | 27.9 | 40.1 | 40.3 | 43 | - | - | 22 | 20 | 20 | - | - | 100 | On | Off | Off | - | DB91-02501A 240624 | [0]12300-[1]00000-[2]00000-[3]00000