## Sheet1
ASHP Test 01/02/2024
Glycol density | r | 1.0195 | kg/l | Fitted internet data for 20% glycol
Glycol specific heat | Cp | 3.9964 | kJ/kg/degC | Ditto
Surrounding room temp | TH | 11 | degC
Room heat losses (U.A):
Ext'l Walls |  | 14.88 | W/degC
Int'l walls |  | 54.56 | W/degC
Windows |  | 21 | W/degC
Floor |  | 37.15 | W/degC
Ceiling int'l |  | 31.93 | W/degC
Ceiling ext'l |  | 23.95 | W/degC
Time from start (08:57) | Heat Pump Temps |  | Primary | Calc ASHP | ASHP | Buffer Tank Temps |  |  |  |  | Calc CH | Heat loss | Lounge Rad Temp |  | Lounge | Ambient | Weather | Samsung Data @ 100% speed |  |  | Calc comp speed from: |  |  | Calc Rad | Heat loss | Est'd Room | Room
| Inlet | Outlet | Circuit Flow | Duty | Power | Prim In | Prim Out | Secy Out | Secy In | Secy Flow | Duty | prim loop | In | Out | Temp | Temp | Comp Temp | Duty | Power | CoPs | Duty | Power | CoPm | Output | sec'y loop | Heat Loss | Heating
(min) | (degC) | (degC) | (l/min) | (kW) | (kW) | (degC) | (degC) | (degC) | (degC) | (l/min) | (kW) | (kW) | (degC) | (degC) | (degC) | (degC) | (degC) | (kW) | (kW) |  |  |  |  | (kW) | (kW) | (kW) | (kW)
| Tw1 | Tw2 | V | Q (Note 1) | P | T1 | T2 | t1 | t2 | v (Note 2) | Q' (Note 3) |  | tr1 | tr2 | TL | TA | Note 4 | Note 5 | Note 5 | Note 5 | Note 6 | Note 6 | Note 6 | Note 7 |  | Note 8
0.37292 | 45 | 46.3 | 28.9 | 2.5511 | 0.2 | 45 | 41.7 | 44.9 | 43.1 | 52.9833 | 6.4759 | -3.9248 | 44.4 | 43 | 20.1 | 2.7 | 47.8629 | 8.442 | 2.4536 | 3.4407 | 30.22% | 8.151% | 12.7555 | 2.1201 | 4.3557 | 2.1662 | -0.046024
2 | 45 | 47.1 | 28.9 | 4.121 | 2.2 | 46.6 | 44.9 | 45.7 | 42.5 | 15.3531 | 3.3361 | 0.78496 | 45.2 | 42.7 | 20.2 | 2.8 | 47.8174 | 8.448 | 2.5025 | 3.3758 | 48.78% | 87.91% | 1.8732 | 2.1377 | 1.1984 | 2.1785 | -0.040854
5 | 45 | 47.1 | 28.7 | 4.0925 | 1.8 | 46.4 | 44.9 | 45.8 | 42.4 | 12.6618 | 2.9232 | 1.1693 | 45.3 | 42.7 | 20.2 | 2.8 | 47.8174 | 8.448 | 2.4958 | 3.3849 | 48.44% | 72.12% | 2.2736 | 2.1435 | 0.77968 | 2.1785 | -0.035001
7 | 45 | 47.3 | 28.5 | 4.451 | 1.5 | 46.8 | 45 | 46 | 42.5 | 14.6571 | 3.4834 | 0.96761 | 45.6 | 42.9 | 20.2 | 2.8 | 47.8174 | 8.448 | 2.5093 | 3.3667 | 52.69% | 59.78% | 2.9673 | 2.1728 | 1.3106 | 2.1785 | -0.0056845
10 | 45 | 47.5 | 28.5 | 4.8381 | 1.6 | 47.1 | 45.3 | 46.3 | 42.6 | 13.8649 | 3.4834 | 1.3547 | 45.8 | 43.1 | 20.2 | 2.8 | 47.8174 | 8.448 | 2.5195 | 3.3531 | 57.27% | 63.51% | 3.0238 | 2.1964 | 1.287 | 2.1785 | 0.017835
12 | 45 | 47.7 | 28.5 | 5.2251 | 1.7 | 47 | 45.4 | 46.3 | 42.7 | 12.6667 | 3.0964 | 2.1288 | 46.6 | 43.2 | 20.2 | 2.8 | 47.8174 | 8.448 | 2.5161 | 3.3576 | 61.85% | 67.57% | 3.0736 | 2.2495 | 0.84687 | 2.1785 | 0.070966
14 | 45 | 47.7 | 28.5 | 5.2251 | 1.7 | 47.4 | 45.6 | 46.7 | 42.9 | 13.5 | 3.4834 | 1.7417 | 46.2 | 43.4 | 20.3 | 2.8 | 47.8174 | 8.448 | 2.5296 | 3.3396 | 61.85% | 67.2% | 3.0736 | 2.2258 | 1.2576 | 2.1969 | 0.028969
16 | 45 | 47.8 | 28.7 | 5.4567 | 1.7 | 47.7 | 45.8 | 46.9 | 43.1 | 14.35 | 3.7027 | 1.7539 | 46.4 | 43.6 | 20.2 | 2.9 | 47.772 | 8.454 | 2.5359 | 3.3338 | 64.55% | 67.04% | 3.2098 | 2.2613 | 1.4414 | 2.1725 | 0.088796
20 | 45 | 48 | 28.9 | 5.8872 | 1.7 | 48 | 46 | 47.2 | 43.3 | 14.8205 | 3.9248 | 1.9624 | 46.5 | 43.9 | 20.3 | 2.9 | 47.772 | 8.454 | 2.5462 | 3.3203 | 69.64% | 66.77% | 3.463 | 2.2732 | 1.6516 | 2.1909 | 0.08231
22 | 46 | 48.3 | 28.3 | 4.4198 | 1.6 | 47.9 | 46.3 | 47.2 | 43.5 | 12.2378 | 3.0746 | 1.3452 | 46.7 | 44.6 | 20.3 | 2.9 | 47.772 | 8.454 | 2.5427 | 3.3248 | 52.28% | 62.92% | 2.7624 | 2.3268 | 0.74788 | 2.1909 | 0.13586
25 | 46 | 48 | 29.1 | 3.9519 | 1.6 | 47.7 | 46.3 | 47.2 | 43.7 | 11.64 | 2.7664 | 1.1856 | 46.7 | 44.2 | 20.3 | 3 | 47.7265 | 8.46 | 2.532 | 3.3413 | 46.71% | 63.19% | 2.47 | 2.3029 | 0.46344 | 2.1849 | 0.11801
27 | 46 | 48 | 28.9 | 3.9248 | 1.5 | 47.9 | 46.3 | 47.2 | 43.9 | 14.0121 | 3.1398 | 0.78496 | 46.7 | 44.2 | 20.3 | 3 | 47.7265 | 8.46 | 2.5389 | 3.3321 | 46.39% | 59.08% | 2.6165 | 2.3029 | 0.8369 | 2.1849 | 0.11801
29 | 46 | 48.6 | 28.9 | 5.1022 | 1.6 | 48.1 | 46.5 | 47.4 | 43.9 | 13.2114 | 3.1398 | 1.9624 | 46.9 | 44.1 | 20.3 | 3.1 | 47.6811 | 8.466 | 2.5422 | 3.3302 | 60.27% | 62.94% | 3.1889 | 2.3089 | 0.83095 | 2.1789 | 0.12994
32 | 46 | 48 | 28.7 | 3.8976 | 1.6 | 48 | 46.5 | 47.3 | 44 | 13.0455 | 2.9232 | 0.9744 | 46.8 | 44.2 | 20.4 | 3.2 | 47.6356 | 8.472 | 2.5349 | 3.3422 | 46.01% | 63.12% | 2.436 | 2.297 | 0.62624 | 2.1913 | 0.10568
34 | 46 | 48.3 | 28.9 | 4.5135 | 1.5 | 48.1 | 46.7 | 47.4 | 44.1 | 12.2606 | 2.7473 | 1.7662 | 47 | 44.3 | 20.4 | 3.2 | 47.6356 | 8.472 | 2.5385 | 3.3375 | 53.28% | 59.09% | 3.009 | 2.3148 | 0.43252 | 2.1913 | 0.12354
37 | 46 | 46.5 | 28.5 | 0.96761 | 0.2 | 45.7 | 45.6 | 45.4 | 44 | 2.0357 | 0.19352 | 0.77409 | 45.1 | 43.7 | 20.4 | 3.3 | 47.5902 | 8.478 | 2.4478 | 3.4636 | 11.41% | 8.171% | 4.8381 | 2.167 | -1.9735 | 2.1853 | -0.018334
40 | 45 | 45.3 | 28.5 | 0.58057 | 0.2 | 45.2 | 44.7 | 44.7 | 43.1 | 8.9062 | 0.96761 | -0.38705 | 44.2 | 42.8 | 20.4 | 3.4 | 47.5447 | 8.484 | 2.4245 | 3.4992 | 6.843% | 8.249% | 2.9028 | 2.0619 | -1.0943 | 2.1793 | -0.11739
42 | 44 | 46.8 | 28.5 | 5.4186 | 2.2 | 46.3 | 44.8 | 45.5 | 42.5 | 14.25 | 2.9028 | 2.5158 | 45.2 | 42.7 | 20.5 | 3.4 | 47.5447 | 8.484 | 2.4649 | 3.4419 | 63.87% | 89.25% | 2.463 | 2.1026 | 0.8002 | 2.1977 | -0.095033
45 | 44 | 46.8 | 28.7 | 5.4567 | 1.8 | 46.4 | 44.9 | 45.7 | 42.5 | 13.4531 | 2.9232 | 2.5335 | 45.3 | 42.7 | 20.5 | 3.5 | 47.4993 | 8.49 | 2.4641 | 3.4455 | 64.27% | 73.05% | 3.0315 | 2.1085 | 0.81474 | 2.1917 | -0.08322
47 | 45 | 47.1 | 28.9 | 4.121 | 1.4 | 46.6 | 45.1 | 45.9 | 42.7 | 13.5469 | 2.9436 | 1.1774 | 45.4 | 42.8 | 20.5 | 3.6 | 47.4538 | 8.496 | 2.4671 | 3.4437 | 48.51% | 56.75% | 2.9436 | 2.1201 | 0.82344 | 2.1857 | -0.065565
49 | 45 | 47.2 | 28.7 | 4.2874 | 1.4 | 47 | 45.4 | 46.2 | 42.8 | 13.5059 | 3.1181 | 1.1693 | 45.1 | 43.6 | 20.5 | 3.6 | 47.4538 | 8.496 | 2.4822 | 3.4228 | 50.46% | 56.4% | 3.0624 | 2.1494 | 0.96871 | 2.1857 | -0.036322
51 | 45 | 47.5 | 28.9 | 4.906 | 1.6 | 47.4 | 45.6 | 46.5 | 43 | 14.8629 | 3.5323 | 1.3737 | 45.8 | 43.6 | 20.5 | 3.7 | 47.4084 | 8.502 | 2.4932 | 3.4101 | 57.7% | 64.17% | 3.0662 | 2.1905 | 1.3418 | 2.1797 | 0.010756
55 | 45 | 47.7 | 28.7 | 5.2618 | 1.6 | 47.7 | 45.9 | 46.9 | 43.3 | 14.35 | 3.5079 | 1.7539 | 46.2 | 43.9 | 20.5 | 3.7 | 47.4084 | 8.502 | 2.5046 | 3.3945 | 61.89% | 63.88% | 3.2886 | 2.2318 | 1.2761 | 2.1797 | 0.052029
57 | 46 | 47.8 | 28.5 | 3.4834 | 1.8 | 47.8 | 46.1 | 47.1 | 43.6 | 13.8429 | 3.2899 | 0.19352 | 46.5 | 44.2 | 20.6 | 3.8 | 47.3629 | 8.508 | 2.5046 | 3.397 | 40.94% | 71.87% | 1.9352 | 2.2554 | 1.0345 | 2.1921 | 0.06333
59 | 46 | 48 | 28.9 | 3.9248 | 1.6 | 47.9 | 46.4 | 47.2 | 43.9 | 13.1364 | 2.9436 | 0.98119 | 46.4 | 44.5 | 20.6 | 3.9 | 47.3175 | 8.514 | 2.5046 | 3.3993 | 46.1% | 63.88% | 2.453 | 2.2673 | 0.67631 | 2.1861 | 0.081167
61 | 45 | 46 | 28.7 | 1.9488 | 0.2 | 45.2 | 45.3 | 45 | 43.8 | -2.3917 | -0.19488 | 2.1437 | 44.7 | 43.7 | 20.6 | 4 | 47.272 | 8.52 | 2.3939 | 3.559 | 22.87% | 8.354% | 9.744 | 2.1201 | -2.315 | 2.1801 | -0.05998
63 | 44 | 45.3 | 28.9 | 2.5511 | 0.2 | 45.2 | 44.5 | 44.5 | 43.1 | 14.45 | 1.3737 | 1.1774 | 44 | 42.9 | 20.6 | 4.1 | 47.2266 | 8.526 | 2.3888 | 3.5691 | 29.92% | 8.372% | 12.7555 | 2.033 | -0.6593 | 2.1741 | -0.14117
65 | 44 | 46.8 | 29.1 | 5.5327 | 2.2 | 46.3 | 44.6 | 45.5 | 42.4 | 15.9581 | 3.3591 | 2.1736 | 44.4 | 42.8 | 20.6 | 4.2 | 47.1811 | 8.532 | 2.4283 | 3.5135 | 64.85% | 90.6% | 2.5149 | 2.0503 | 1.3088 | 2.1682 | -0.11782
68 | 44 | 47 | 28.7 | 5.8464 | 1.8 | 46.5 | 44.9 | 45.8 | 42.3 | 13.12 | 3.1181 | 2.7283 | 45.2 | 43 | 20.7 | 4.3 | 47.1357 | 8.538 | 2.432 | 3.5107 | 68.48% | 74.01% | 3.248 | 2.0968 | 1.0213 | 2.1805 | -0.083706
71 | 44 | 47.1 | 28.7 | 6.0413 | 1.4 | 46.7 | 45.1 | 46 | 42.7 | 13.9152 | 3.1181 | 2.9232 | 44.9 | 43.7 | 20.7 | 4.4 | 47.0902 | 8.544 | 2.4358 | 3.5077 | 70.71% | 57.48% | 4.3152 | 2.1201 | 0.99795 | 2.1745 | -0.054395
Average | 45.2632 | 47.4263 | 28.6895 | 4.2148 | 1.4684 | 47.0158 | 45.4316 | 46.3579 | 43.1737 |  |  |  | 45.9263 | 43.4737 | 20.3 | 3.0158 | 47.7193 | 8.4609 | 2.5073 | 3.3753 |  |  |  | 2.2144 |  | 2.184
Std Dev | 0.71197 | 0.82074 | 0.2016 | 1.3809 | 0.5997 | 0.96326 | 0.95176 | 0.87207 | 0.58081 |  |  |  | 0.89015 | 0.61998 |  |  | 0.23593 | [6 empty] | 0.088014 |  | 0.0078606
Average excl stopped |  |  |  | 4.7755 | 1.684 |  |  |  |  | 13.6889 | 3.1993 | 1.5762 | [8 empty] | 56.31% | 67.34% | 2.8705 |  | 0.99099 |  | 0.024384
Std Dev excl stopped |  |  |  | 0.7387 | 0.22855 |  |  |  |  | 1.016 | 0.30087 | 0.679 | [8 empty] | 8.647% | 9.597% | 0.51361 |  | 0.31248 |  | 0.080979
Note 1 | From Q = V * r *Cp * (Tw2 - Tw1)
Note 2 | From heat balance on buffer tank: v = V * (T1 - T2) / (t1 - t2)
Note 3 | From Q' = v * r * Cp * (t1 - t2)
Note 4 | Linear interpolation of 40degC @ 20degC ambient, 50degC @ -2degC ambient
Note 5 | Curve fitted from Table 2-9 in Samsung EHS Data Book, then CoPs = ratio
Note 6 | Prorated duty/power from Samsung table values, then CoPm = ratio
Note 7 | From prorated radiator Vendor data: Q = design duty * (actual Dt / design Dt) ^ 1.3
Note 8 | From MCS U.A values and measured heat transfer areas
[15 empty] | 20.3 |  |  |  |  | 3.3753 | 58.37% | 49.82% | 3.4438