## Sheet1
Time Slice (#) | Time from Op'n start (min) | Inverter Frequency (Hz) | Discharge Pressure (bar) | Sat'n Temp at Disch Pres (degC) | Suction Pressure (bar) | Sat'n Temp at Suct'n Pres (degC) | Comp'r Discharge Temp (degC) | Comp'r Casing Temp (degC) | Outdoor Temp (degC) | Compressor Current (A) | OCT1 ( ℃) | Inverter DC Link Voltage (V) | IPM1 Temp ( ℃) | R32 Evap'r Inlet Temp (degC) | Comp'r Suction Temp (degC) | R32 Cond'r Exit Temp (degC) | RWT (degC) | LWT (degC) | Calc water DT (degC) | Main EEV Output (wide open = 2000) | Vap Injection EEV Output (wide open = 300) | Vap Injection Solenoid Valve Output (wide open = 2000) | Vap injection Intercooler Sidestream Inlet Temp (degC) | Vap injection Intercooler Sidestream Outlet Temp (degC) | Evaporator Fan Speed (RPM) | Water Law Target Temp (degC) | 3Way Valve | Water Pump | Water Flow Sensor (l/min) | Water In ( ℃) | Water Out ( ℃) | Aveerage Water Temp (degC) (for properties evaluation) | Calc Glycol density (kg/m3) | Calc Glycol Sp Ht (J/kg/K | HeCalc at Output (W) (from Q = m.Cp.DT) | Water Law Set Temp. ( ℃) | Water Law Target - LWT (degC) | Main EEV opening (%) | Comp'r Pressure Ratio x 10 | (LWT - RWT) (degC) x 10 | Water Law Target - LWT (DegC) | Calc subcool ex Cond'r (degC) | Calc superheat ex Evap'r (degC) | Outdoor Temp (degC) x 10 | Calc Heat Produced (kW) | Pure R32 Disch Satn Temp (degC) | Samsung discharge sat'n margin | Pure R32 subcool (degC) | Pure R32 Suctn Satn Temp (degC) | Samsung suction sat'n margin | Pure R32 superheat (degC)
-5 | -7.1935 | 3.75 | 7.65 | 2.25 | 7.775 | 3 | 18.3 | 29.6 | 1.825 | 0 | 0 | 0 | 31 | 2.225 | 8.2 | 7.1 | 19.75 | 20.025 | 0.275 | 1062.5 | 0 | 0 | 4.9 | 6.5 | 70 | 50.3 | #DIV/0! | #DIV/0! | 28.5 | 19.225 | 20.5 | 19.8875 | 1020.0508 | 4066.3959 | 541.8234 | 50.3 | 30.275 | 53.125 | 9.8392 | 2.75 | 30.275 | -4.85 | -5.2 | 18.25 | 0.54182 | -1.9604 | -4.2104 | -9.0604 | -1.457 | -4.457 | 9.657
-4 | -5.7548 | 38.4444 | 13.8 | 20.7778 | 7.1 | 0.44444 | 26.7889 | 30.6111 | 1.7556 | 2.2 | 7.1111 | 180 | 32.4444 | 0.54444 | 1.6222 | 14.5444 | 18.6111 | 20.5 | 1.8889 | 300 | 0 | 0 | 4.8667 | 6.5667 | 536.6667 | 50.3222 | #DIV/0! | #DIV/0! | 27.7222 | 19.1333 | 20.8667 | 19.5556 | 1020.1766 | 4066.0889 | 3620.2239 | 50.3222 | 29.8222 | 15 | 19.4366 | 18.8889 | 29.8222 | 6.2333 | -1.1778 | 17.5556 | 3.6202 | 17.7247 | -3.053 | 3.1803 | -4.2506 | -4.695 | 5.8728
-3 | -4.3161 | 50 | 15 | 23.75 | 6.4 | -2.25 | 30.8375 | 32.075 | 1.8 | 3.25 | 9 | 180 | 35.125 | -2 | -2.4375 | 20.175 | 18.325 | 22.6 | 4.275 | 500 | 0 | 0 | 6.025 | 7.275 | 547.5 | 50.3375 | #DIV/0! | #DIV/0! | 27.5 | 18.2875 | 21.9375 | 20.4625 | 1019.8314 | 4066.9278 | 8126.6657 | 50.3375 | 27.7375 | 25 | 23.4375 | 42.75 | 27.7375 | 3.575 | 0.1875 | 18 | 8.1267 | 20.7326 | -3.0174 | 0.55763 | -7.3622 | -5.1122 | 4.9247
-2 | -2.8774 | 50 | 15.3778 | 24.5556 | 6.4 | -2 | 29.4 | 32.0222 | 1.8 | 3.3222 | 9 | 181 | 36.5556 | -2.3778 | -3.0444 | 21.3778 | 18.9889 | 23.5556 | 4.5667 | 500 | 0 | 0 | 8.1222 | 8.4444 | 547.7778 | 50.3 | #DIV/0! | #DIV/0! | 27.5444 | 18.7444 | 23.2444 | 21.2722 | 1019.5193 | 4067.6768 | 8694.0864 | 50.3 | 26.7444 | 25 | 24.0278 | 45.6667 | 26.7444 | 3.1778 | 1.0444 | 18 | 8.6941 | 21.6407 | -2.9148 | 0.26295 | -7.3622 | -5.3622 | 4.3177
-1 | -1.4387 | 50 | 15.75 | 25.25 | 6.375 | -2.25 | 29.6 | 33.0625 | 1.8 | 3.4 | 9 | 180.625 | 37.5 | -2.425 | -3.175 | 22.3125 | 19.875 | 24.4625 | 4.5875 | 500 | 0 | 0 | 9.9 | 9.5 | 548.75 | 50.3 | #DIV/0! | #DIV/0! | 27.65 | 19.7 | 24.25 | 22.1687 | 1019.1694 | 4068.5061 | 8765.9969 | 50.3 | 25.8375 | 25 | 24.7059 | 45.875 | 25.8375 | 2.9375 | 0.925 | 18 | 8.766 | 22.5186 | -2.7314 | 0.2061 | -7.4778 | -5.2278 | 4.3028
0 | 0 | 50.4444 | 16.2556 | 26.5556 | 6.3667 | -2.3333 | 30.5 | 35.0667 | 1.8889 | 3.5222 | 9.2222 | 180 | 38.4444 | -2.4111 | -3.2 | 23.2778 | 20.9667 | 25.4889 | 4.5222 | 499.5556 | 0 | 0 | 11.1 | 10.4111 | 548.8889 | 50.3 | #DIV/0! | #DIV/0! | 27.5667 | 20.7111 | 25.2556 | 23.2278 | 1018.7503 | 4069.4857 | 8613.7487 | 50.3 | 24.8111 | 24.9778 | 25.5323 | 45.2222 | 24.8111 | 3.2778 | 0.86667 | 18.8889 | 8.6137 | 23.6853 | -2.8702 | 0.40755 | -7.5164 | -5.1831 | 4.3164
1 | 1.4387 | 53.1111 | 16.8667 | 27.7778 | 6.2556 | -3 | 31.8556 | 37.1556 | 1.9778 | 3.8556 | 10 | 180 | 39.5556 | -2.6444 | -3.5111 | 24.4667 | 22.0889 | 26.7333 | 4.6444 | 497.4444 | 0 | 0 | 11.9222 | 11.2111 | 548.8889 | 50.2111 | #DIV/0! | #DIV/0! | 27.5222 | 21.9111 | 26.4556 | 24.4111 | 1018.2746 | 4070.5803 | 8830.5403 | 50.2111 | 23.4778 | 24.8722 | 26.9627 | 46.4444 | 23.4778 | 3.3111 | 0.51111 | 19.7778 | 8.8305 | 25.0583 | -2.7195 | 0.59165 | -8.0349 | -5.0349 | 4.5238
2 | 2.8774 | 55.875 | 17.5375 | 29.375 | 6.125 | -3.75 | 34 | 39.8625 | 1.8375 | 4.1875 | 10.125 | 180.75 | 40.75 | -3.025 | -3.9375 | 25.6 | 23.2 | 28.1 | 4.9 | 452 | 0 | 0 | 12.5125 | 11.85 | 548.75 | 50.3 | #DIV/0! | #DIV/0! | 27.9 | 22.85 | 27.7 | 25.65 | 1017.7682 | 4071.7263 | 9442.2717 | 50.3 | 22.2 | 22.6 | 28.6327 | 49 | 22.2 | 3.775 | 0.1875 | 18.375 | 9.4423 | 26.5212 | -2.8538 | 0.92124 | -8.6527 | -4.9027 | 4.7152
3 | 4.3161 | 57 | 18.0778 | 30.3333 | 6.1 | -4 | 35.5556 | 42.6667 | 1.8 | 4.4222 | 11 | 183 | 42 | -3.1889 | -4.1444 | 26.6111 | 24.2889 | 29.3778 | 5.0889 | 430.7778 | 0 | 0 | 13.0222 | 12.3222 | 548.8889 | 50.3 | #DIV/0! | #DIV/0! | 27.7889 | 24.1111 | 29.1667 | 26.8333 | 1017.2765 | 4072.8208 | 9765.1117 | 50.3 | 20.9222 | 21.5389 | 29.6357 | 50.8889 | 20.9222 | 3.7222 | 0.14444 | 18 | 9.7651 | 27.6678 | -2.6655 | 1.0567 | -8.7721 | -4.7721 | 4.6276
4 | 5.7548 | 57 | 18.6889 | 31.4444 | 6.0778 | -4 | 37.4556 | 45.4556 | 1.8 | 4.5444 | 11 | 182.3333 | 43.2222 | -3.1333 | -4.1222 | 27.7889 | 25.4667 | 30.5444 | 5.0778 | 416.1111 | 0 | 0 | 13.5 | 12.9111 | 550 | 50.3 | #DIV/0! | #DIV/0! | 27.7889 | 25.2222 | 30.3 | 28.0056 | 1016.7816 | 4073.9051 | 9741.6434 | 50.3 | 19.7556 | 20.8056 | 30.7495 | 50.7778 | 19.7556 | 3.6556 | 0.12222 | 18 | 9.7416 | 28.9326 | -2.5119 | 1.1437 | -8.8785 | -4.8785 | 4.7563
5 | 7.1935 | 57 | 19.3125 | 32.875 | 6.0875 | -4 | 39.25 | 47.7 | 1.825 | 4.65 | 11 | 182 | 44.25 | -3.0875 | -4.0875 | 28.8 | 26.55 | 31.7125 | 5.1625 | 398.875 | 0 | 0 | 13.9625 | 13.475 | 546.25 | 50.3 | #DIV/0! | #DIV/0! | 27.95 | 26.375 | 31.5 | 29.1312 | 1016.2992 | 4074.9464 | 9959.4213 | 50.3 | 18.5875 | 19.9438 | 31.7248 | 51.625 | 18.5875 | 4.075 | 0.0875 | 18.25 | 9.9594 | 30.19 | -2.685 | 1.39 | -8.8319 | -4.8319 | 4.7444
6 | 8.6321 | 55 | 19.7667 | 33.4444 | 6.1333 | -3.6667 | 40.7889 | 49.6222 | 2 | 4.6111 | 11.6667 | 182 | 45 | -2.9556 | -4 | 29.3333 | 27.5556 | 32.6444 | 5.0889 | 386 | 0 | 0 | 14.3778 | 13.9667 | 548.8889 | 50.2333 | #DIV/0! | #DIV/0! | 27.7667 | 27.4222 | 32.4889 | 30.1 | 1015.8783 | 4075.8425 | 9751.121 | 50.2333 | 17.5889 | 19.3 | 32.2283 | 50.8889 | 17.5889 | 4.1111 | 0.33333 | 20 | 9.7511 | 31.0857 | -2.3587 | 1.7524 | -8.613 | -4.9463 | 4.613
7 | 10.0708 | 54.6667 | 20.3333 | 34.6667 | 6.2 | -3 | 42.2889 | 51.0667 | 1.9111 | 4.6667 | 12.1111 | 182 | 45.7778 | -2.8 | -3.8 | 30.5 | 28.7111 | 33.5222 | 4.8111 | 368.6667 | 34.4444 | 600 | 14.3667 | 14.6222 | 550 | 50.2778 | #DIV/0! | #DIV/0! | 27.8556 | 28.3333 | 33.1778 | 31.1167 | 1015.431 | 4076.7829 | 9246.4272 | 50.2778 | 16.7556 | 18.4333 | 32.7957 | 48.1111 | 16.7556 | 4.1667 | 0.8 | 19.1111 | 9.2464 | 32.1807 | -2.486 | 1.6807 | -8.2966 | -5.2966 | 4.4966
8 | 11.5095 | 56.625 | 21.05 | 36 | 6.1 | -4 | 45.3 | 53.7875 | 1.8625 | 5.4625 | 14 | 182 | 44.375 | -3.025 | -3.9625 | 32.6875 | 29.7125 | 34.9625 | 5.25 | 357.125 | 150 | 2000 | 11.15 | 25.325 | 548.75 | 50.3 | #DIV/0! | #DIV/0! | 27.875 | 29.3875 | 34.675 | 32.3375 | 1014.8861 | 4077.9122 | 10094.3445 | 50.3 | 15.3375 | 17.8562 | 34.5082 | 52.5 | 15.3375 | 3.3125 | -0.0375 | 18.625 | 10.0943 | 33.5314 | -2.4686 | 0.84393 | -8.7721 | -4.7721 | 4.8096
9 | 12.9482 | 57 | 21.5222 | 37 | 6.1 | -4 | 48.9111 | 57.4889 | 1.7 | 5.6222 | 14.1111 | 179.3333 | 43.6667 | -3.0444 | -4 | 33.7889 | 30.6444 | 35.9 | 5.2556 | 353 | 150 | 2000 | 11.7333 | 30.0778 | 550 | 50.3889 | #DIV/0! | #DIV/0! | 27.8333 | 30.3667 | 35.6667 | 33.2722 | 1014.4634 | 4078.7768 | 10087.8569 | 50.3889 | 14.4889 | 17.65 | 35.2823 | 52.5556 | 14.4889 | 3.2111 | 0 | 17 | 10.0879 | 34.4016 | -2.5984 | 0.61272 | -8.7721 | -4.7721 | 4.7721
10 | 14.3869 | 57 | 22.1 | 38 | 6.1 | -4 | 51.375 | 60.175 | 1.625 | 5.75 | 14.875 | 179.5 | 45.625 | -3.075 | -4.0375 | 34.8 | 31.7375 | 36.9875 | 5.25 | 351 | 153.375 | 2000 | 12.7 | 31.75 | 547.5 | 50.4 | #DIV/0! | #DIV/0! | 27.8 | 31.4 | 36.7 | 34.3625 | 1013.964 | 4079.7853 | 10062.658 | 50.4 | 13.4125 | 17.55 | 36.2295 | 52.5 | 13.4125 | 3.2 | 0.0375 | 16.25 | 10.0627 | 35.4459 | -2.5541 | 0.64586 | -8.7721 | -4.7721 | 4.7346
11 | 15.8256 | 57 | 22.6556 | 38.8889 | 6.1 | -4 | 53.5111 | 62.0778 | 1.6111 | 5.9222 | 15 | 181 | 46.8889 | -3.0333 | -4 | 35.7 | 32.6889 | 37.9222 | 5.2333 | 349 | 168.7778 | 2000 | 13.7556 | 32.2667 | 550 | 50.4 | #DIV/0! | #DIV/0! | 28.0111 | 32.4778 | 37.7556 | 35.3056 | 1013.5268 | 4080.6576 | 10104.6871 | 50.4 | 12.4778 | 17.45 | 37.1403 | 52.3333 | 12.4778 | 3.1889 | 0 | 16.1111 | 10.1047 | 36.4296 | -2.4592 | 0.72964 | -8.7721 | -4.7721 | 4.7721
12 | 17.2643 | 57 | 23.1778 | 39.7778 | 6.1111 | -3.8889 | 55.6889 | 63.9111 | 1.5333 | 6.0778 | 15.5556 | 180.2222 | 48.8889 | -2.9 | -3.9444 | 36.5889 | 33.6556 | 38.8556 | 5.2 | 347.2222 | 186.2222 | 2000 | 14.7222 | 32.9222 | 548.8889 | 50.4222 | #DIV/0! | #DIV/0! | 28.1 | 33.4778 | 38.6222 | 36.2556 | 1013.0813 | 4081.5364 | 10069.928 | 50.4222 | 11.5667 | 17.3611 | 37.9273 | 52 | 11.5667 | 3.1889 | 0.055556 | 15.3333 | 10.0699 | 37.337 | -2.4408 | 0.74812 | -8.719 | -4.8301 | 4.7745
13 | 18.703 | 57 | 23.75 | 40.625 | 6.1625 | -3.375 | 57.55 | 65.5375 | 1.5625 | 6.2 | 16 | 179.875 | 50.5 | -2.7875 | -3.8625 | 37.4625 | 34.625 | 39.7125 | 5.0875 | 346.5 | 201.25 | 2000 | 15.7125 | 33.1875 | 550 | 50.475 | #DIV/0! | #DIV/0! | 28.1 | 34.325 | 39.5 | 37.1688 | 1012.6482 | 4082.3811 | 9849.896 | 50.475 | 10.7625 | 17.325 | 38.5396 | 50.875 | 10.7625 | 3.1625 | 0.4875 | 15.625 | 9.8499 | 38.3127 | -2.3123 | 0.85019 | -8.4743 | -5.0993 | 4.6118
14 | 20.1417 | 57 | 24.1667 | 41.3333 | 6.2 | -3 | 59.0889 | 67.0889 | 1.6 | 6.3444 | 16.3333 | 179 | 52 | -2.6778 | -3.7667 | 38.1889 | 35.4444 | 40.5556 | 5.1111 | 346.3333 | 216.2222 | 2000 | 16.4 | 33.7 | 550 | 50.4 | #DIV/0! | #DIV/0! | 28.0556 | 35.3444 | 40.4222 | 38 | 1012.25 | 4083.15 | 9877.9327 | 50.4 | 9.8444 | 17.3167 | 38.9785 | 51.1111 | 9.8444 | 3.1444 | 0.76667 | 16 | 9.8779 | 39.0114 | -2.3219 | 0.8225 | -8.2966 | -5.2966 | 4.53
15 | 21.5804 | 57 | 24.6667 | 42.2222 | 6.2 | -3 | 60.4333 | 68.6 | 1.7 | 6.5111 | 17 | 179 | 53.6667 | -2.5444 | -3.6222 | 38.9778 | 36.4111 | 41.3778 | 4.9667 | 344.3333 | 231.7778 | 2000 | 17.2222 | 34.2222 | 547.7778 | 50.4 | #DIV/0! | #DIV/0! | 28.0333 | 36.1111 | 41.1667 | 38.8944 | 1011.8172 | 4083.9774 | 9589.0123 | 50.4 | 9.0222 | 17.2167 | 39.7849 | 49.6667 | 9.0222 | 3.2444 | 0.62222 | 17 | 9.589 | 39.8372 | -2.385 | 0.85942 | -8.2966 | -5.2966 | 4.6744
16 | 23.019 | 57 | 25.2 | 43 | 6.2 | -3 | 61.325 | 69.525 | 1.7 | 6.6625 | 17.125 | 179 | 55.375 | -2.5 | -3.55 | 39.725 | 37.2875 | 42.2875 | 5 | 342.25 | 246.375 | 2000 | 18.1875 | 34.725 | 550 | 50.4 | #DIV/0! | #DIV/0! | 28.05 | 37.075 | 42.1375 | 39.7875 | 1011.3806 | 4084.8034 | 9656.8921 | 50.4 | 8.1125 | 17.1125 | 40.6452 | 50 | 8.1125 | 3.275 | 0.55 | 17 | 9.6569 | 40.7034 | -2.2966 | 0.97842 | -8.2966 | -5.2966 | 4.7466
17 | 24.4577 | 57 | 25.7 | 43.8889 | 6.2222 | -3 | 62.1889 | 70.3667 | 1.7111 | 6.8333 | 18 | 179 | 56.5556 | -2.3778 | -3.4444 | 40.5111 | 38.1444 | 43 | 4.8556 | 341.8889 | 259.4444 | 2000 | 19.0556 | 35.0222 | 550 | 50.4 | #DIV/0! | #DIV/0! | 27.7222 | 37.8444 | 42.7111 | 40.5722 | 1010.9932 | 4085.5293 | 9266.4265 | 50.4 | 7.4 | 17.0944 | 41.3036 | 48.5556 | 7.4 | 3.3778 | 0.44444 | 17.1111 | 9.2664 | 41.5023 | -2.3866 | 0.99115 | -8.1917 | -5.1917 | 4.7473
18 | 25.8964 | 57 | 25.5444 | 43.5556 | 6.2333 | -3 | 63.1333 | 71.3444 | 1.7778 | 6.8222 | 17.7778 | 180.7778 | 57.5556 | -2.3556 | -3.4 | 40.8556 | 37.8667 | 43.0111 | 5.1444 | 339.8889 | 273.5556 | 2000 | 19.7778 | 34.6222 | 548.8889 | 50.3444 | #DIV/0! | #DIV/0! | 27.9 | 38.3111 | 43.4 | 40.4389 | 1011.0593 | 4085.406 | 9881.0539 | 50.3444 | 7.3333 | 16.9944 | 40.9804 | 51.4444 | 7.3333 | 2.7 | 0.4 | 17.7778 | 9.8811 | 41.2551 | -2.3005 | 0.39952 | -8.1394 | -5.1394 | 4.7394
19 | 27.3351 | 57 | 25.2625 | 43.125 | 6.2 | -3 | 62.7125 | 70.8 | 1.8 | 6.775 | 17.875 | 183 | 55.875 | -2.475 | -3.4875 | 40.075 | 37.2 | 42.375 | 5.175 | 336 | 279.125 | 2000 | 20.2125 | 31.2 | 550 | 50.3 | #DIV/0! | #DIV/0! | 27.9 | 37.075 | 42.275 | 39.7875 | 1011.3806 | 4084.8034 | 9941.4348 | 50.3 | 7.925 | 16.8 | 40.746 | 51.75 | 7.925 | 3.05 | 0.4875 | 18 | 9.9414 | 40.804 | -2.321 | 0.72897 | -8.2966 | -5.2966 | 4.8091
20 | 28.7738 | 57 | 26.1778 | 44.5556 | 6.2444 | -3 | 63.2778 | 70.7889 | 1.8 | 7.0222 | 18 | 180.3333 | 55.8889 | -2.3889 | -3.4222 | 41.1111 | 38.7667 | 43.7 | 4.9333 | 338.1111 | 289 | 2000 | 20.5778 | 33.2889 | 551.1111 | 50.3 | #DIV/0! | #DIV/0! | 28.0333 | 38.3556 | 43.2889 | 41.2333 | 1010.6642 | 4086.1408 | 9518.843 | 50.3 | 6.6 | 16.9056 | 41.9217 | 49.3333 | 6.6 | 3.4444 | 0.42222 | 18 | 9.5188 | 42.254 | -2.3015 | 1.1429 | -8.0871 | -5.0871 | 4.6649
21 | 30.2125 | 57 | 26.9333 | 45.6667 | 6.2778 | -3 | 64.9556 | 72.4778 | 1.8889 | 7.2333 | 18.7778 | 180 | 57.8889 | -2.2222 | -3.3 | 42.3111 | 40 | 45.0556 | 5.0556 | 337.4444 | 299.1111 | 2000 | 21.2667 | 35.1333 | 547.7778 | 50.3 | #DIV/0! | #DIV/0! | 28.0333 | 39.6778 | 44.7889 | 42.5278 | 1010.0129 | 4087.3382 | 9751.2408 | 50.3 | 5.2444 | 16.8722 | 42.9027 | 50.5556 | 5.2444 | 3.3556 | 0.3 | 18.8889 | 9.7512 | 43.4206 | -2.246 | 1.1095 | -7.9307 | -4.9307 | 4.6307
22 | 31.6512 | 57 | 27.6125 | 46.625 | 6.3 | -3 | 66.75 | 74.375 | 1.875 | 7.4375 | 19.25 | 180 | 59.75 | -2.1625 | -3.1875 | 43.2125 | 40.925 | 46.0375 | 5.1125 | 318.875 | 300 | 2000 | 21.725 | 36 | 548.75 | 50.3 | #DIV/0! | #DIV/0! | 28.05 | 40.85 | 45.85 | 43.4813 | 1009.5272 | 4088.2202 | 9864.3219 | 50.3 | 4.2625 | 15.9437 | 43.8294 | 51.125 | 4.2625 | 3.4125 | 0.1875 | 18.75 | 9.8643 | 44.4471 | -2.1779 | 1.2346 | -7.8267 | -4.8267 | 4.6392
23 | 33.0899 | 55 | 28.6111 | 48.3333 | 6.2 | -3 | 67.6556 | 75.4222 | 1.9778 | 7.4333 | 20 | 182.3333 | 57.7778 | -2.5667 | -3.4667 | 44.7111 | 41.7667 | 47.1222 | 5.3556 | 288 | 296.8889 | 2000 | 22.3111 | 26.2556 | 548.8889 | 50.2667 | #DIV/0! | #DIV/0! | 27.9444 | 41.5556 | 46.8556 | 44.4444 | 1009.0314 | 4089.1111 | 10291.5866 | 50.2667 | 3.1444 | 14.4 | 46.147 | 53.5556 | 3.1444 | 3.6222 | 0.46667 | 19.7778 | 10.2916 | 45.9199 | -2.4134 | 1.2088 | -8.2966 | -5.2966 | 4.83
24 | 34.5286 | 51.75 | 28.8375 | 48.75 | 6.2875 | -3 | 66.125 | 73.1375 | 2 | 7.1125 | 20 | 182.5 | 55.5 | -2.425 | -3.1875 | 45.4 | 42.5 | 47.5375 | 5.0375 | 286 | 281 | 2000 | 22.6125 | 23.325 | 550 | 50.2 | #DIV/0! | #DIV/0! | 27.975 | 42.3375 | 47.4625 | 45.0188 | 1008.7332 | 4089.6423 | 9689.3705 | 50.2 | 2.6625 | 14.3 | 45.8648 | 50.375 | 2.6625 | 3.35 | 0.1875 | 20 | 9.6894 | 46.2481 | -2.5019 | 0.84807 | -7.8851 | -4.8851 | 4.6976
25 | 35.9673 | 52.6667 | 29.2556 | 49.2222 | 6.3 | -3 | 68.6333 | 74.7889 | 2 | 7.3778 | 20.3333 | 179 | 55.6667 | -2.3 | -3.1 | 45.7333 | 43.1778 | 47.9111 | 4.7333 | 286 | 278.6667 | 2000 | 22.7667 | 25.6778 | 548.8889 | 50.2 | #DIV/0! | #DIV/0! | 27.9222 | 42.9222 | 47.6778 | 45.5444 | 1008.4587 | 4090.1286 | 9085.7527 | 50.2 | 2.2889 | 14.3 | 46.4374 | 47.3333 | 2.2889 | 3.4889 | 0.1 | 20 | 9.0858 | 46.8486 | -2.3737 | 1.1152 | -7.8267 | -4.8267 | 4.7267
26 | 37.406 | 50.6667 | 28.7667 | 48.5556 | 6.3333 | -2.6667 | 70.4667 | 77.4111 | 2 | 6.9889 | 20 | 177.8889 | 56 | -2.2444 | -3 | 45.7333 | 42.6889 | 47.6556 | 4.9667 | 281.3333 | 275.3333 | 2000 | 22.8111 | 24.5444 | 548.8889 | 50.2 | #DIV/0! | #DIV/0! | 27.7222 | 43.0778 | 48.0111 | 45.1722 | 1008.6533 | 4089.7843 | 9466.3837 | 50.2 | 2.5444 | 14.0667 | 45.4211 | 49.6667 | 2.5444 | 2.8222 | 0.33333 | 20 | 9.4664 | 46.1456 | -2.4099 | 0.41229 | -7.6713 | -5.0046 | 4.6713
27 | 38.8446 | 53.5 | 28.6125 | 48.125 | 6.2375 | -3 | 69.6375 | 76.475 | 1.975 | 7.2125 | 20 | 177 | 55 | -2.4 | -3.1625 | 45.0375 | 42.05 | 47.225 | 5.175 | 280 | 272.25 | 2000 | 21.9375 | 22.65 | 550 | 50.2125 | #DIV/0! | #DIV/0! | 27.9 | 42.2375 | 47.2 | 44.6375 | 1008.9313 | 4089.2897 | 9928.2522 | 50.2125 | 2.9875 | 14 | 45.8717 | 51.75 | 2.9875 | 3.0875 | 0.1625 | 19.75 | 9.9283 | 45.922 | -2.203 | 0.88446 | -8.1198 | -5.1198 | 4.9573
28 | 40.2833 | 55.7778 | 29.1667 | 49.1111 | 6.1778 | -3.2222 | 67.1556 | 73.8 | 1.9556 | 7.5778 | 20 | 180 | 54.1111 | -2.7444 | -3.5444 | 45.5333 | 42.1667 | 47.6 | 5.4333 | 280 | 271.2222 | 2000 | 21.4333 | 21.8333 | 550 | 50.2778 | #DIV/0! | #DIV/0! | 27.8556 | 42.2 | 47.5 | 44.8833 | 1008.8037 | 4089.5171 | 10406.5222 | 50.2778 | 2.6778 | 14 | 47.2122 | 54.3333 | 2.6778 | 3.5778 | 0.32222 | 19.5556 | 10.4065 | 46.7215 | -2.3896 | 1.1881 | -8.4018 | -5.1796 | 4.8574
29 | 41.722 | 54.1111 | 29.5111 | 49.7778 | 6.2222 | -3 | 64.3333 | 70.0889 | 2 | 7.4778 | 20 | 179.1111 | 53.2222 | -2.6222 | -3.3889 | 46.1 | 42.6889 | 47.9111 | 5.2222 | 280 | 271 | 2000 | 21.6556 | 22.1 | 550 | 50.2 | #DIV/0! | #DIV/0! | 28.2556 | 42.5111 | 47.7778 | 45.3 | 1008.5866 | 4089.9025 | 10144.5803 | 50.2 | 2.2889 | 14 | 47.4286 | 52.2222 | 2.2889 | 3.6778 | 0.38889 | 20 | 10.1446 | 47.2123 | -2.5655 | 1.1123 | -8.1917 | -5.1917 | 4.8028
30 | 43.1607 | 51.5 | 29.8 | 50 | 6.2875 | -3 | 64.7375 | 70.4125 | 2 | 7.3 | 20.375 | 178 | 54 | -2.425 | -3.175 | 46.5875 | 43.525 | 48.8 | 5.275 | 280 | 271 | 2000 | 22.3375 | 22.75 | 550 | 50.2 | #DIV/0! | #DIV/0! | 28.125 | 43.35 | 48.675 | 46.1625 | 1008.134 | 4090.7003 | 10197.1704 | 50.2 | 1.4 | 14 | 47.3956 | 52.75 | 1.4 | 3.4125 | 0.175 | 20 | 10.1972 | 47.6203 | -2.3797 | 1.0328 | -7.8851 | -4.8851 | 4.7101
31 | 44.5994 | 46.7778 | 29.4778 | 49.6667 | 6.4444 | -2.1111 | 67.3889 | 73.2333 | 2.0111 | 6.6778 | 20 | 182.6667 | 55.2222 | -1.9889 | -2.6 | 46.4556 | 44.3333 | 48.6444 | 4.3111 | 278 | 262.8889 | 2000 | 23.2556 | 29.3333 | 550 | 50.2 | #DIV/0! | #DIV/0! | 28.1 | 44.1333 | 48.6444 | 46.4889 | 1007.9617 | 4091.0022 | 8325.6475 | 50.2 | 1.5556 | 13.9 | 45.7414 | 43.1111 | 1.5556 | 3.2111 | 0.48889 | 20.1111 | 8.3256 | 47.165 | -2.5017 | 0.7094 | -7.1574 | -5.0463 | 4.5574
32 | 46.0381 | 43.8889 | 29.5889 | 49.8889 | 6.5778 | -1.3333 | 71.0667 | 78.1444 | 1.9778 | 6.2889 | 20 | 183.1111 | 60 | -1.5444 | -2.0556 | 46.3 | 45.1889 | 49.1333 | 3.9444 | 274.6667 | 252.6667 | 2000 | 23.5 | 39.4111 | 550 | 50.2 | #DIV/0! | #DIV/0! | 27.5889 | 45.0444 | 49.0889 | 47.1611 | 1007.6048 | 4091.624 | 7477.4716 | 50.2 | 1.0667 | 13.7333 | 44.9831 | 39.4444 | 1.0667 | 3.5889 | 0.72222 | 19.7778 | 7.4775 | 47.3224 | -2.5665 | 1.0224 | -6.5492 | -5.2159 | 4.4937
33 | 47.4768 | 39.875 | 29.525 | 49.75 | 6.75 | -1 | 71.3 | 79.575 | 2 | 5.7 | 20 | 180 | 62.5 | -1.0375 | -1.45 | 46.325 | 45.6125 | 49.075 | 3.4625 | 271.25 | 236.75 | 2000 | 23.6875 | 41.4375 | 550 | 50.25 | #DIV/0! | #DIV/0! | 28.2 | 45.55 | 49.1 | 47.3438 | 1007.5075 | 4091.793 | 6708.8729 | 50.25 | 1.175 | 13.5625 | 43.7407 | 34.625 | 1.175 | 3.425 | 0.45 | 20 | 6.7089 | 47.2319 | -2.5181 | 0.90694 | -5.7768 | -4.7768 | 4.3268
34 | 48.9155 | 40.3333 | 29.7111 | 50 | 6.7 | -1 | 71.0889 | 79.5 | 2 | 5.8222 | 20 | 178.6667 | 63.3333 | -0.96667 | -1.4 | 46.5444 | 45.8 | 49.3333 | 3.5333 | 271.4444 | 236.3333 | 2000 | 23.7889 | 41.8 | 550 | 50.2 | #DIV/0! | #DIV/0! | 28.1 | 45.8 | 49.3111 | 47.5667 | 1007.3883 | 4091.9992 | 6821.3784 | 50.2 | 0.86667 | 13.5722 | 44.3449 | 35.3333 | 0.86667 | 3.4556 | 0.4 | 20 | 6.8214 | 47.4951 | -2.5049 | 0.95066 | -5.9996 | -4.9996 | 4.5996
35 | 50.3542 | 39.3333 | 29.8111 | 50 | 6.7556 | -1 | 71.1889 | 79.5333 | 2 | 5.6444 | 20 | 178.6667 | 64 | -0.93333 | -1.3333 | 46.7556 | 46.0333 | 49.4667 | 3.4333 | 269 | 231.4444 | 2000 | 24.0556 | 42.0444 | 550 | 50.2 | #DIV/0! | #DIV/0! | 28.0556 | 45.9556 | 49.4444 | 47.75 | 1007.2902 | 4092.1687 | 6617.4661 | 50.2 | 0.73333 | 13.45 | 44.1283 | 34.3333 | 0.73333 | 3.2444 | 0.33333 | 20 | 6.6175 | 47.6359 | -2.3641 | 0.88039 | -5.7522 | -4.7522 | 4.4188
36 | 51.7929 | 38.75 | 29.925 | 50 | 6.7375 | -1 | 71.6125 | 79.8625 | 1.975 | 5.6125 | 20.125 | 184 | 64 | -0.925 | -1.35 | 46.95 | 46.175 | 49.675 | 3.5 | 267 | 233 | 2000 | 24.1375 | 42.2 | 550 | 50.225 | #DIV/0! | #DIV/0! | 28.05 | 46.1 | 49.7 | 47.925 | 1007.1963 | 4092.3306 | 6744.2629 | 50.225 | 0.55 | 13.35 | 44.4156 | 35 | 0.55 | 3.05 | 0.35 | 19.75 | 6.7443 | 47.7959 | -2.2041 | 0.8459 | -5.8324 | -4.8324 | 4.4824
37 | 53.2315 | 37.3333 | 29.9556 | 50.1111 | 6.8 | -1 | 71.5333 | 80.0667 | 1.9 | 5.4111 | 20 | 182.3333 | 64 | -0.8 | -1.1556 | 47 | 46.3667 | 49.6667 | 3.3 | 265 | 223 | 2000 | 24.5111 | 42.3556 | 550 | 50.3 | #DIV/0! | #DIV/0! | 28.0111 | 46.3222 | 49.6667 | 48.0167 | 1007.147 | 4092.4154 | 6349.8815 | 50.3 | 0.63333 | 13.25 | 44.0523 | 33 | 0.63333 | 3.1111 | 0.15556 | 19 | 6.3499 | 47.8387 | -2.2724 | 0.83872 | -5.5553 | -4.5553 | 4.3997
38 | 54.6702 | 36.5 | 30.05 | 50 | 6.8 | -1 | 71.6 | 80.125 | 1.9 | 5.35 | 20.25 | 181 | 64.625 | -0.75 | -1.0875 | 47.0875 | 46.55 | 49.8 | 3.25 | 263.375 | 221 | 2000 | 24.7375 | 42.525 | 550 | 50.3 | #DIV/0! | #DIV/0! | 28.025 | 46.5375 | 49.8 | 48.175 | 1007.0619 | 4092.5619 | 6256.4667 | 50.3 | 0.5 | 13.1687 | 44.1912 | 32.5 | 0.5 | 2.9125 | 0.0875 | 19 | 6.2565 | 47.9709 | -2.0291 | 0.88338 | -5.5553 | -4.5553 | 4.4678
39 | 56.1089 | 37.6667 | 30.1889 | 50.6667 | 6.8 | -1 | 72 | 80.3667 | 1.9556 | 5.5222 | 20.4444 | 181.8889 | 65 | -0.75556 | -1.1222 | 47.1222 | 46.6667 | 49.9556 | 3.2889 | 263.3333 | 225.6667 | 2000 | 24.5444 | 42.7 | 550 | 50.2556 | #DIV/0! | #DIV/0! | 28.0778 | 46.6 | 49.8889 | 48.3111 | 1006.9885 | 4092.6878 | 6342.9871 | 50.2556 | 0.3 | 13.1667 | 44.3954 | 32.8889 | 0.3 | 3.5444 | 0.12222 | 19.5556 | 6.343 | 48.1646 | -2.502 | 1.0424 | -5.5553 | -4.5553 | 4.4331
40 | 57.5476 | 36.5556 | 30.2444 | 51 | 6.8 | -1 | 72.2667 | 80.7889 | 1.9667 | 5.3889 | 20.8889 | 181 | 65 | -0.62222 | -1.0111 | 47.2 | 46.8444 | 50.1111 | 3.2667 | 259.6667 | 222.1111 | 2000 | 24.9667 | 42.7111 | 550 | 50.2556 | #DIV/0! | #DIV/0! | 28.0111 | 46.8 | 50.1111 | 48.4778 | 1006.8986 | 4092.8419 | 6284.8457 | 50.2556 | 0.14444 | 12.9833 | 44.4771 | 32.6667 | 0.14444 | 3.8 | 0.011111 | 19.6667 | 6.2848 | 48.2419 | -2.7581 | 1.0419 | -5.5553 | -4.5553 | 4.5442
41 | 58.9863 | 35.75 | 30.275 | 51 | 6.825 | -0.75 | 72.45 | 81 | 2 | 5.3625 | 20.875 | 179 | 65 | -0.6625 | -0.975 | 47.3 | 47 | 50.2 | 3.2 | 257.75 | 220 | 2000 | 25.075 | 42.8 | 547.5 | 50.2 | #DIV/0! | #DIV/0! | 28.1 | 47 | 50.2 | 48.6 | 1006.8326 | 4092.955 | 6175.8859 | 50.2 | 0 | 12.8875 | 44.359 | 32 | 0 | 3.7 | 0.225 | 20 | 6.1759 | 48.2844 | -2.7156 | 0.98438 | -5.445 | -4.695 | 4.47
42 | 60.425 | 35 | 30.3333 | 51 | 6.8111 | -0.88889 | 72.4 | 81.1 | 1.9444 | 5.2444 | 20.7778 | 182.1111 | 65 | -0.62222 | -0.91111 | 47.3 | 47.1 | 50.3111 | 3.2111 | 257.4444 | 215 | 2000 | 25.3778 | 43.0111 | 550 | 50.2556 | #DIV/0! | #DIV/0! | 28.0111 | 47.0556 | 50.2889 | 48.7056 | 1006.7754 | 4093.0526 | 6177.5229 | 50.2556 | -0.055556 | 12.8722 | 44.5351 | 32.1111 | -0.055556 | 3.7 | 0.022222 | 19.4444 | 6.1775 | 48.3653 | -2.6347 | 1.0653 | -5.5062 | -4.6173 | 4.5951
43 | 61.8637 | 35 | 30.4556 | 51 | 6.9 | 0 | 72.5778 | 81.1667 | 1.9556 | 5.3 | 20.6667 | 182.7778 | 65 | -0.51111 | -0.83333 | 47.3889 | 47.1 | 50.4 | 3.3 | 256.5556 | 215 | 2000 | 25.4667 | 43.0889 | 550 | 50.2778 | #DIV/0! | #DIV/0! | 27.9667 | 47.1 | 50.3333 | 48.75 | 1006.7514 | 4093.0938 | 6338.3661 | 50.2778 | -0.12222 | 12.8278 | 44.1385 | 33 | -0.12222 | 3.6111 | 0.83333 | 19.5556 | 6.3384 | 48.5346 | -2.4654 | 1.1457 | -5.1158 | -5.1158 | 4.2825
44 | 63.3024 | 34.75 | 30.5125 | 51 | 6.9 | 0 | 72.7625 | 81.3375 | 2 | 5.2875 | 21 | 182 | 65.875 | -0.4125 | -0.7375 | 47.55 | 47.2125 | 50.525 | 3.3125 | 256 | 214.5 | 2000 | 25.575 | 43.2 | 548.75 | 50.2 | #DIV/0! | #DIV/0! | 28.05 | 47.175 | 50.45 | 48.8688 | 1006.687 | 4093.2036 | 6381.0966 | 50.2 | -0.325 | 12.8 | 44.221 | 33.125 | -0.325 | 3.45 | 0.7375 | 20 | 6.3811 | 48.6133 | -2.3867 | 1.0633 | -5.1158 | -5.1158 | 4.3783
45 | 64.7411 | 33 | 30.5333 | 51 | 6.9 | 0 | 73.1 | 81.5 | 2 | 5.0111 | 20.7778 | 180 | 66 | -0.37778 | -0.63333 | 47.6 | 47.2778 | 50.5778 | 3.3 | 255.4444 | 208.3333 | 2000 | 26.1333 | 43.4444 | 550 | 50.2 | #DIV/0! | #DIV/0! | 28.1889 | 47.2333 | 50.6 | 48.9278 | 1006.655 | 4093.2582 | 6388.3756 | 50.2 | -0.37778 | 12.7722 | 44.2512 | 33 | -0.37778 | 3.4 | 0.63333 | 20 | 6.3884 | 48.642 | -2.358 | 1.042 | -5.1158 | -5.1158 | 4.4825
46 | 66.1798 | 34.3333 | 30.7444 | 51 | 6.9 | 0 | 73.2 | 81.5778 | 2 | 5.2111 | 21 | 179.4444 | 66 | -0.36667 | -0.63333 | 47.6222 | 47.4556 | 50.7778 | 3.3222 | 256.7778 | 211.4444 | 2000 | 25.8556 | 43.7111 | 550 | 50.2 | #DIV/0! | #DIV/0! | 28.0111 | 47.3889 | 50.6889 | 49.1167 | 1006.5524 | 4093.4329 | 6390.4558 | 50.2 | -0.57778 | 12.8389 | 44.5572 | 33.2222 | -0.57778 | 3.3778 | 0.63333 | 20 | 6.3905 | 48.9324 | -2.0676 | 1.3102 | -5.1158 | -5.1158 | 4.4825
47 | 67.6185 | 30.625 | 30.0819 | 51 | 6.975 | 0 | 73.475 | 82 | 2 | 4.8 | 21 | 183 | 66 | -0.325 | -0.5625 | 47.7 | 47.6 | 50.9 | 3.3 | 256.625 | 202.375 | 2000 | 26.4875 | 43.875 | 547.5 | 50.2 | #DIV/0! | #DIV/0! | 27.9 | 47.6 | 50.9 | 49.25 | 1006.4799 | 4093.5563 | 6322.2658 | 50.2 | -0.7 | 12.8313 | 43.1282 | 33 | -0.7 | 3.3 | 0.5625 | 20 | 6.3223 | 48.0154 | -2.9846 | 0.31544 | -4.7892 | -4.7892 | 4.2267
48 | 69.0571 | 27.1111 | 29.943 | 51 | 7.0889 | 0 | 73.2333 | 81.7222 | 2 | 4.2111 | 20.2222 | 182.5556 | 66 | -0.022222 | -0.1 | 47.6111 | 47.6556 | 50.6 | 2.9444 | 254.3333 | 185.3333 | 2000 | 27.5111 | 45.3667 | 547.7778 | 50.2 | #DIV/0! | #DIV/0! | 27.9889 | 47.6556 | 50.6 | 49.1278 | 1006.5464 | 4093.4432 | 5659.2689 | 50.2 | -0.4 | 12.7167 | 42.2393 | 29.4444 | -0.4 | 3.3889 | 0.1 | 20 | 5.6593 | 47.8211 | -3.1789 | 0.20998 | -4.2982 | -4.2982 | 4.1982
49 | 70.4958 | 27 | 29.9225 | 51 | 7.1 | 0 | 72.8125 | 81.1125 | 2 | 4.2 | 20.625 | 182 | 66 | 0 | 0 | 47.6 | 47.7 | 50.6 | 2.9 | 251.125 | 184 | 2000 | 27.975 | 45.6 | 548.75 | 50.2 | #DIV/0! | #DIV/0! | 28 | 47.7 | 50.6 | 49.15 | 1006.5343 | 4093.4637 | 5576.0197 | 50.2 | -0.4 | 12.5563 | 42.1444 | 29 | -0.4 | 3.4 | 0 | 20 | 5.576 | 47.7924 | -3.2076 | 0.19245 | -4.2506 | -4.2506 | 4.2506
50 | 71.9345 | 27 | 30.0083 | 51 | 7.1 | 0 | 72.6111 | 80.8 | 2 | 4.2 | 20.7778 | 180.2222 | 66 | 0 | -0.033333 | 47.6 | 47.7222 | 50.6 | 2.8778 | 249.4444 | 184 | 2000 | 28.0556 | 45.6 | 548.8889 | 50.2 | #DIV/0! | #DIV/0! | 28.2333 | 47.7444 | 50.6 | 49.1611 | 1006.5282 | 4093.474 | 5579.3829 | 50.2 | -0.4 | 12.4722 | 42.2653 | 28.7778 | -0.4 | 3.4 | 0.033333 | 20 | 5.5794 | 47.9126 | -3.0874 | 0.31264 | -4.2506 | -4.2506 | 4.2172
51 | 73.3732 | 27 | 30.0628 | 51 | 7.1 | 0 | 72.7 | 80.9778 | 2 | 4.2 | 20.6667 | 180 | 66 | 0.044444 | -0.011111 | 47.6 | 47.8 | 50.6 | 2.8 | 248.4444 | 184 | 2000 | 28.1 | 45.6 | 550 | 50.2 | #DIV/0! | #DIV/0! | 28.1444 | 47.7667 | 50.6 | 49.2 | 1006.5071 | 4093.51 | 5411.4314 | 50.2 | -0.4 | 12.4222 | 42.342 | 28 | -0.4 | 3.4 | 0.011111 | 20 | 5.4114 | 47.9888 | -3.0112 | 0.38881 | -4.2506 | -4.2506 | 4.2395
52 | 74.8119 | 26 | 30.0329 | 51 | 7.1 | 0 | 72.75 | 81.1 | 2 | 4.1125 | 20.5 | 180 | 66 | 0.0375 | 0 | 47.6625 | 47.775 | 50.725 | 2.95 | 246.625 | 182 | 2000 | 28.3375 | 45.6 | 550 | 50.2 | #DIV/0! | #DIV/0! | 27.95 | 47.775 | 50.7 | 49.25 | 1006.4799 | 4093.5563 | 5661.851 | 50.2 | -0.525 | 12.3313 | 42.2998 | 29.5 | -0.525 | 3.3375 | 0 | 20 | 5.6619 | 47.9469 | -3.0531 | 0.28443 | -4.2506 | -4.2506 | 4.2506
53 | 76.2506 | 26.4444 | 30.0628 | 51 | 7.1 | 0 | 72.4778 | 80.8556 | 2.1111 | 4.1333 | 20.7778 | 182 | 66 | 0.16667 | 0.055556 | 47.6111 | 47.7889 | 50.6 | 2.8111 | 244.6667 | 180.4444 | 2000 | 29.0667 | 45.4889 | 550 | 50.2 | #DIV/0! | #DIV/0! | 27.8111 | 47.7778 | 50.6 | 49.1944 | 1006.5101 | 4093.5049 | 5368.5692 | 50.2 | -0.4 | 12.2333 | 42.342 | 28.1111 | -0.4 | 3.3889 | -0.055556 | 21.1111 | 5.3686 | 47.9888 | -3.0112 | 0.3777 | -4.2506 | -4.2506 | 4.3061
54 | 77.6893 | 25 | 29.9648 | 51 | 7.1333 | 0.33333 | 72.5333 | 80.7889 | 2.2 | 4 | 20.6667 | 182.5556 | 66 | 0.23333 | 0.12222 | 47.7 | 47.8667 | 50.6667 | 2.8 | 243.7778 | 177.7778 | 2000 | 29.5444 | 45.6 | 550 | 50.1111 | #DIV/0! | #DIV/0! | 28.0778 | 47.8889 | 50.6889 | 49.2667 | 1006.4708 | 4093.5717 | 5398.4998 | 50.1111 | -0.55556 | 12.1889 | 42.0067 | 28 | -0.55556 | 3.3 | 0.21111 | 22 | 5.3985 | 47.8516 | -3.1484 | 0.15162 | -4.1081 | -4.4415 | 4.2303
55 | 79.128 | 26.375 | 30.0451 | 51 | 7.125 | 0.25 | 72.3875 | 80.525 | 2.2 | 4.1375 | 20.375 | 181 | 66 | 0.3 | 0.2 | 47.6125 | 47.7625 | 50.625 | 2.8625 | 242.625 | 180 | 2000 | 29.15 | 45.5375 | 548.75 | 50.1 | #DIV/0! | #DIV/0! | 28.1 | 47.75 | 50.5 | 49.1938 | 1006.5105 | 4093.5042 | 5523.4969 | 50.1 | -0.525 | 12.1312 | 42.1686 | 28.625 | -0.525 | 3.3875 | 0.05 | 22 | 5.5235 | 47.9641 | -3.0359 | 0.35157 | -4.1437 | -4.3937 | 4.3437
56 | 80.5667 | 25.5556 | 30.0519 | 51 | 7.1333 | 0.33333 | 72.6222 | 80.9 | 2.2 | 4.0556 | 20.6667 | 179.8889 | 66 | 0.3 | 0.2 | 47.6556 | 47.8 | 50.6667 | 2.8667 | 242.4444 | 178.6667 | 2000 | 29.2556 | 45.6889 | 547.7778 | 50.1 | #DIV/0! | #DIV/0! | 28.1 | 47.8 | 50.6889 | 49.2333 | 1006.4889 | 4093.5408 | 5531.468 | 50.1 | -0.56667 | 12.1222 | 42.1289 | 28.6667 | -0.56667 | 3.3444 | 0.13333 | 22 | 5.5315 | 47.9736 | -3.0264 | 0.31803 | -4.1081 | -4.4415 | 4.3081
57 | 82.0054 | 25.2222 | 29.9757 | 51 | 7.1 | 0 | 72.6333 | 80.9333 | 2.0667 | 4.0222 | 20.5556 | 179 | 66 | 0.15556 | 0.044444 | 47.6 | 47.8 | 50.6 | 2.8 | 240.6667 | 177.7778 | 2000 | 29.4 | 45.5667 | 547.7778 | 50.1667 | #DIV/0! | #DIV/0! | 28.2111 | 47.8 | 50.6 | 49.2 | 1006.5071 | 4093.51 | 5424.2496 | 50.1667 | -0.43333 | 12.0333 | 42.2192 | 28 | -0.43333 | 3.4 | -0.044444 | 20.6667 | 5.4242 | 47.8669 | -3.1331 | 0.26689 | -4.2506 | -4.2506 | 4.295
58 | 83.444 | 26.375 | 30.1309 | 51 | 7.1 | 0 | 73 | 81.1875 | 2 | 4.15 | 20.75 | 179 | 66 | 0.2 | 0.0625 | 47.6375 | 47.875 | 50.8 | 2.925 | 241.375 | 180.5 | 2000 | 28.8625 | 45.6125 | 548.75 | 50.2 | #DIV/0! | #DIV/0! | 28.15 | 47.825 | 50.75 | 49.3375 | 1006.4322 | 4093.6372 | 5653.8841 | 50.2 | -0.6 | 12.0687 | 42.4379 | 29.25 | -0.6 | 3.3625 | -0.0625 | 20 | 5.6539 | 48.0839 | -2.9161 | 0.44636 | -4.2506 | -4.2506 | 4.3131
59 | 84.8827 | 25 | 30.0846 | 51 | 7.1 | 0 | 73.1667 | 81.5333 | 2 | 4 | 20.8889 | 179 | 66 | 0.23333 | 0.16667 | 47.7 | 48 | 50.8222 | 2.8222 | 240.5556 | 177.3333 | 2000 | 29.6889 | 45.6667 | 550 | 50.2 | #DIV/0! | #DIV/0! | 28.1222 | 48 | 50.8667 | 49.4111 | 1006.3921 | 4093.7053 | 5449.7099 | 50.2 | -0.62222 | 12.0278 | 42.3727 | 28.2222 | -0.62222 | 3.3 | -0.16667 | 20 | 5.4497 | 48.0192 | -2.9808 | 0.31924 | -4.2506 | -4.2506 | 4.4172
60 | 86.3214 | 24.875 | 30.1432 | 51 | 7.2 | 1 | 73.05 | 81.325 | 2.15 | 3.775 | 19.5 | 179 | 66 | 0.35 | 0.275 | 47.7 | 48.15 | 50.8 | 2.65 | 240.375 | 110 | 1250 | 29.725 | 45.5625 | 548.75 | 50.175 | #DIV/0! | #DIV/0! | 28.05 | 48.15 | 50.8 | 49.475 | 1006.3572 | 4093.7644 | 5103.9041 | 50.175 | -0.625 | 12.0188 | 41.8655 | 26.5 | -0.625 | 3.3 | 0.725 | 21.5 | 5.1039 | 48.101 | -2.899 | 0.40095 | -3.8247 | -4.8247 | 4.0997
61 | 87.7601 | 23.4444 | 30.2481 | 51 | 7.2 | 1 | 71.9444 | 81.2556 | 2.2222 | 3.1556 | 17 | 179 | 64.4444 | 0.46667 | 0.36667 | 47.7 | 48.1667 | 50.8 | 2.6333 | 240 | 0 | 0 | 21.8889 | 42.1778 | 550 | 50.1 | #DIV/0! | #DIV/0! | 27.9667 | 48.1 | 50.8 | 49.4833 | 1006.3527 | 4093.7721 | 5056.723 | 50.1 | -0.7 | 12 | 42.0112 | 26.3333 | -0.7 | 3.3 | 0.63333 | 22.2222 | 5.0567 | 48.247 | -2.753 | 0.54695 | -3.8247 | -4.8247 | 4.1913
62 | 89.1988 | 22 | 30.1827 | 51 | 7.2111 | 1 | 70.3667 | 80.2444 | 2.3889 | 3.0111 | 17 | 180.3333 | 64 | 0.62222 | 0.5 | 47.7 | 48.3 | 50.8 | 2.5 | 239 | 0 | 0 | 19.8556 | 36.6 | 550 | 50.0556 | #DIV/0! | #DIV/0! | 28.0111 | 48.3 | 50.8 | 49.55 | 1006.3163 | 4093.8337 | 4808.2142 | 50.0556 | -0.74444 | 11.95 | 41.8558 | 25 | -0.74444 | 3.3 | 0.5 | 23.8889 | 4.8082 | 48.156 | -2.844 | 0.45599 | -3.7776 | -4.7776 | 4.2776
63 | 90.6375 | 21.5 | 30.1554 | 51 | 7.3 | 1 | 68.975 | 78.9 | 2.4 | 2.9375 | 17 | 183 | 64 | 0.75 | 0.625 | 47.6625 | 48.3 | 50.6 | 2.3 | 237.375 | 0 | 0 | 22.0875 | 32.7 | 550 | 50 | #DIV/0! | #DIV/0! | 28 | 48.3 | 50.6 | 49.45 | 1006.3709 | 4093.7413 | 4421.9423 | 50 | -0.6 | 11.8688 | 41.3088 | 23 | -0.6 | 3.3375 | 0.375 | 24 | 4.4219 | 48.118 | -2.882 | 0.45554 | -3.4031 | -4.4031 | 4.0281
64 | 92.0762 | 20.7778 | 30.0846 | 51 | 7.3111 | 1.1111 | 68.0556 | 77.7778 | 2.4333 | 2.8889 | 17 | 181 | 64 | 0.82222 | 0.73333 | 47.6 | 48.2333 | 50.6444 | 2.4111 | 235.3333 | 0 | 0 | 23.9667 | 30.1778 | 548.8889 | 50 | #DIV/0! | #DIV/0! | 28.1889 | 48.2667 | 50.5778 | 49.4389 | 1006.3769 | 4093.731 | 4666.8507 | 50 | -0.64444 | 11.7667 | 41.1492 | 24.1111 | -0.64444 | 3.4 | 0.37778 | 24.3333 | 4.6669 | 48.0192 | -2.9808 | 0.41924 | -3.3565 | -4.4676 | 4.0899
65 | 93.5149 | 21.3333 | 30.1064 | 51 | 7.3333 | 1.3333 | 67.1444 | 76.7667 | 2.5 | 2.9333 | 17 | 180.1111 | 64 | 1.0333 | 0.92222 | 47.6 | 48.2667 | 50.5556 | 2.2889 | 233.2222 | 0 | 0 | 25.1333 | 28.3556 | 547.7778 | 50 | #DIV/0! | #DIV/0! | 28.1889 | 48.2 | 50.5333 | 49.4111 | 1006.3921 | 4093.7053 | 4430.3211 | 50 | -0.55556 | 11.6611 | 41.0542 | 22.8889 | -0.55556 | 3.4 | 0.41111 | 25 | 4.4303 | 48.0497 | -2.9503 | 0.44966 | -3.2635 | -4.5969 | 4.1858
66 | 94.9536 | 21.125 | 30.0329 | 51 | 7.375 | 1.75 | 66.6125 | 76.3625 | 2.5625 | 2.9 | 17 | 181 | 64 | 1.2 | 1.1375 | 47.6 | 48.0375 | 50.425 | 2.3875 | 231.125 | 0 | 0 | 25.65 | 27.3125 | 550 | 50 | #DIV/0! | #DIV/0! | 28.075 | 48.1125 | 50.475 | 49.2313 | 1006.4901 | 4093.5389 | 4602.7811 | 50 | -0.425 | 11.5563 | 40.7225 | 23.875 | -0.425 | 3.4 | 0.6125 | 25.625 | 4.6028 | 47.9469 | -3.0531 | 0.34693 | -3.0897 | -4.8397 | 4.2272
67 | 96.3923 | 21.6667 | 30.1173 | 51 | 7.3778 | 1.7778 | 66.4 | 76.4222 | 2.5 | 2.9889 | 16.7778 | 180.4444 | 64 | 1.0778 | 1 | 47.6 | 48 | 50.5333 | 2.5333 | 231 | 0 | 0 | 25.9778 | 26.5556 | 550 | 50 | #DIV/0! | #DIV/0! | 28.2111 | 48 | 50.4444 | 49.2667 | 1006.4708 | 4093.5717 | 4907.5514 | 50 | -0.53333 | 11.55 | 40.8217 | 25.3333 | -0.53333 | 3.4 | 0.77778 | 25 | 4.9076 | 48.0649 | -2.9351 | 0.46487 | -3.0782 | -4.8559 | 4.0782
68 | 97.831 | 21 | 29.9866 | 51 | 7.4 | 2 | 66.1778 | 76.5667 | 2.5 | 2.9 | 16.8889 | 180 | 64 | 1.3 | 1.2111 | 47.5222 | 47.8889 | 50.4222 | 2.5333 | 229.7778 | 0 | 0 | 26.1 | 26.1222 | 548.8889 | 50 | #DIV/0! | #DIV/0! | 28.1 | 47.9333 | 50.3778 | 49.1556 | 1006.5313 | 4093.4689 | 4888.3936 | 50 | -0.42222 | 11.4889 | 40.5224 | 25.3333 | -0.42222 | 3.4778 | 0.78889 | 25 | 4.8884 | 47.8821 | -3.1179 | 0.35992 | -2.9858 | -4.9858 | 4.1969
69 | 99.2696 | 20.5 | 29.9103 | 51 | 7.45 | 2 | 65.8125 | 76.375 | 2.5875 | 2.85 | 16.75 | 182 | 63.375 | 1.3 | 1.2625 | 47.5 | 47.85 | 50.375 | 2.525 | 227.875 | 0 | 0 | 26.1375 | 25.85 | 547.5 | 50 | #DIV/0! | #DIV/0! | 28.2 | 47.875 | 50.375 | 49.1125 | 1006.5547 | 4093.4291 | 4889.7188 | 50 | -0.375 | 11.3938 | 40.148 | 25.25 | -0.375 | 3.5 | 0.7375 | 25.875 | 4.8897 | 47.7753 | -3.2247 | 0.27525 | -2.7787 | -4.7787 | 4.0412
70 | 100.7083 | 21.5556 | 29.9212 | 51 | 7.4111 | 2 | 65.5333 | 76.1333 | 2.7667 | 2.9444 | 16.7778 | 181.5556 | 63 | 1.4222 | 1.3556 | 47.4778 | 47.7778 | 50.2889 | 2.5111 | 226.6667 | 0 | 0 | 26.2 | 25.6444 | 548.8889 | 49.9111 | #DIV/0! | #DIV/0! | 28.1 | 47.8222 | 50.3111 | 49.0333 | 1006.5977 | 4093.3558 | 4845.699 | 49.9111 | -0.37778 | 11.3333 | 40.3734 | 25.1111 | -0.37778 | 3.5222 | 0.64444 | 27.6667 | 4.8457 | 47.7905 | -3.2095 | 0.31276 | -2.9397 | -4.9397 | 4.2952
71 | 102.147 | 22.375 | 29.9348 | 51 | 7.4 | 2 | 65.4 | 76.2 | 2.7125 | 3.025 | 16.875 | 181 | 63 | 1.3 | 1.275 | 47.3 | 47.7625 | 50.3 | 2.5375 | 225 | 0 | 0 | 26.1375 | 25.55 | 550 | 49.9 | #DIV/0! | #DIV/0! | 28.2 | 47.75 | 50.3 | 49.0312 | 1006.5988 | 4093.3539 | 4914.0506 | 49.9 | -0.4 | 11.25 | 40.4524 | 25.375 | -0.4 | 3.7 | 0.725 | 27.125 | 4.9141 | 47.8096 | -3.1904 | 0.50963 | -2.9858 | -4.9858 | 4.2608
72 | 103.5857 | 21 | 29.834 | 51 | 7.4667 | 2 | 65.4444 | 76.4667 | 2.7111 | 2.8889 | 16.2222 | 181.7778 | 63 | 1.3667 | 1.3111 | 47.3 | 47.7 | 50.2444 | 2.5444 | 223.3333 | 0 | 0 | 26.0667 | 25.4889 | 550 | 49.9 | #DIV/0! | #DIV/0! | 28.1 | 47.7 | 50.2889 | 48.9722 | 1006.6309 | 4093.2993 | 4910.1165 | 49.9 | -0.34444 | 11.1667 | 39.9563 | 25.4444 | -0.34444 | 3.7 | 0.68889 | 27.1111 | 4.9101 | 47.6681 | -3.3319 | 0.36815 | -2.7099 | -4.7099 | 4.021
73 | 105.0244 | 22 | 29.8558 | 51 | 7.4556 | 2 | 65.2444 | 76.2444 | 2.8222 | 3 | 16.4444 | 181.5556 | 63 | 1.4667 | 1.3778 | 47.3 | 47.7 | 50.2 | 2.5 | 222.5556 | 0 | 0 | 26 | 25.4 | 550 | 49.8778 | #DIV/0! | #DIV/0! | 28.1 | 47.7 | 50.2 | 48.95 | 1006.6429 | 4093.2787 | 4824.3838 | 49.8778 | -0.32222 | 11.1278 | 40.045 | 25 | -0.32222 | 3.7 | 0.62222 | 28.2222 | 4.8244 | 47.6988 | -3.3012 | 0.39877 | -2.7557 | -4.7557 | 4.1335
74 | 106.4631 | 22 | 29.8245 | 51 | 7.5 | 2 | 65.4 | 76.375 | 2.9875 | 3 | 16.5 | 180 | 63 | 1.5375 | 1.4625 | 47.3 | 47.6625 | 50.2 | 2.5375 | 222.375 | 0 | 0 | 25.975 | 25.4 | 548.75 | 49.8 | #DIV/0! | #DIV/0! | 28.1 | 47.6875 | 50.2 | 48.9313 | 1006.6531 | 4093.2614 | 4896.7783 | 49.8 | -0.4 | 11.1188 | 39.766 | 25.375 | -0.4 | 3.7 | 0.5375 | 29.875 | 4.8968 | 47.6547 | -3.3453 | 0.35474 | -2.5726 | -4.5726 | 4.0351
75 | 107.9018 | 23 | 29.7686 | 51 | 7.5 | 2 | 65.2667 | 76.4889 | 3 | 3.0778 | 16.3333 | 180 | 63 | 1.5444 | 1.4111 | 47.2111 | 47.5667 | 50.0444 | 2.4778 | 219.7778 | 0 | 0 | 25.8 | 25.4 | 547.7778 | 49.8 | #DIV/0! | #DIV/0! | 28.0556 | 47.5778 | 50.0667 | 48.8056 | 1006.7213 | 4093.1451 | 4774.1534 | 49.8 | -0.24444 | 10.9889 | 39.6915 | 24.7778 | -0.24444 | 3.7889 | 0.58889 | 30 | 4.7742 | 47.5762 | -3.4238 | 0.36505 | -2.5726 | -4.5726 | 3.9837
76 | 109.3405 | 22.6667 | 29.6706 | 50.7778 | 7.5 | 2 | 65.3111 | 76.7 | 3.0222 | 3 | 16.2222 | 180 | 63 | 1.5111 | 1.4 | 47.1667 | 47.4889 | 49.9778 | 2.4889 | 217.8889 | 0 | 0 | 25.7111 | 25.4 | 548.8889 | 49.8 | #DIV/0! | #DIV/0! | 28.0556 | 47.4778 | 50.0222 | 48.7333 | 1006.7604 | 4093.0783 | 4795.6702 | 49.8 | -0.17778 | 10.8944 | 39.5608 | 24.8889 | -0.17778 | 3.6111 | 0.6 | 30.2222 | 4.7957 | 47.4379 | -3.3399 | 0.27122 | -2.5726 | -4.5726 | 3.9726
77 | 110.7792 | 24 | 29.6651 | 51 | 7.45 | 2 | 65.225 | 76.775 | 3.1 | 3.1125 | 16 | 180 | 63 | 1.4375 | 1.375 | 47.1 | 47.425 | 49.925 | 2.5 | 218.375 | 0 | 0 | 25.7 | 25.4 | 548.75 | 49.7125 | #DIV/0! | #DIV/0! | 28.025 | 47.475 | 49.875 | 48.675 | 1006.792 | 4093.0244 | 4811.9207 | 49.7125 | -0.2125 | 10.9187 | 39.8189 | 25 | -0.2125 | 3.9 | 0.625 | 31 | 4.8119 | 47.4302 | -3.5698 | 0.33019 | -2.7787 | -4.7787 | 4.1537
78 | 112.2179 | 24.1111 | 29.6052 | 50.7778 | 7.4444 | 2 | 65.3556 | 77.0333 | 3.0667 | 3.1111 | 16.1111 | 180.8889 | 63 | 1.4111 | 1.3111 | 47.0444 | 47.2667 | 49.8 | 2.5333 | 216 | 0 | 0 | 25.6222 | 25.4 | 550 | 49.7444 | #DIV/0! | #DIV/0! | 27.9889 | 47.3222 | 49.8222 | 48.5333 | 1006.8686 | 4092.8933 | 4870.0113 | 49.7444 | -0.055556 | 10.8 | 39.7682 | 25.3333 | -0.055556 | 3.7333 | 0.68889 | 30.6667 | 4.87 | 47.3455 | -3.4323 | 0.30105 | -2.8016 | -4.8016 | 4.1128
79 | 113.6565 | 26 | 29.5834 | 50.6667 | 7.4 | 2 | 65.6111 | 77.2333 | 3.1 | 3.3 | 16 | 182 | 63 | 1.3444 | 1.1778 | 46.9556 | 47.1333 | 49.8 | 2.6667 | 213 | 0 | 0 | 25.6 | 25.4 | 551.1111 | 49.7 | #DIV/0! | #DIV/0! | 28.1 | 47.1444 | 49.8 | 48.4667 | 1006.9046 | 4092.8317 | 5146.7848 | 49.7 | -0.1 | 10.65 | 39.9776 | 26.6667 | -0.1 | 3.7111 | 0.82222 | 31 | 5.1468 | 47.3147 | -3.352 | 0.3591 | -2.9858 | -4.9858 | 4.1636
80 | 115.0952 | 26 | 29.567 | 50.625 | 7.4 | 2 | 66.0375 | 77.75 | 3.1625 | 3.3 | 16 | 181 | 63 | 1.375 | 1.1875 | 46.8 | 47.1 | 49.8 | 2.7 | 210.125 | 0 | 0 | 25.5125 | 25.3375 | 550 | 49.7 | #DIV/0! | #DIV/0! | 28 | 47.1 | 49.8 | 48.45 | 1006.9136 | 4092.8162 | 5192.6016 | 49.7 | -0.1 | 10.5062 | 39.9555 | 27 | -0.1 | 3.825 | 0.8125 | 31.625 | 5.1926 | 47.2915 | -3.3335 | 0.49152 | -2.9858 | -4.9858 | 4.1733
81 | 116.5339 | 26.5556 | 29.4962 | 50.2222 | 7.3889 | 1.8889 | 66.2889 | 78.1222 | 3.2 | 3.3333 | 16 | 181 | 63 | 1.3222 | 1.1444 | 46.7111 | 47.0667 | 49.6 | 2.5333 | 209.1111 | 0 | 0 | 25.4222 | 25.3 | 550 | 49.7 | #DIV/0! | #DIV/0! | 28.2333 | 47.0778 | 49.6667 | 48.3333 | 1006.9766 | 4092.7083 | 4912.8488 | 49.7 | 0.1 | 10.4556 | 39.9197 | 25.3333 | 0.1 | 3.5111 | 0.74444 | 32 | 4.9128 | 47.1911 | -3.0311 | 0.48003 | -3.032 | -4.9208 | 4.1764
82 | 117.9726 | 26.875 | 29.4935 | 50.375 | 7.325 | 1.25 | 66.7875 | 78.8125 | 3.125 | 3.4 | 16 | 181 | 63 | 1 | 0.825 | 46.25 | 46.9625 | 49.65 | 2.6875 | 206.5 | 0 | 0 | 25.3125 | 25.2875 | 550 | 49.7 | #DIV/0! | #DIV/0! | 27.95 | 47 | 49.7 | 48.3063 | 1006.9912 | 4092.6833 | 5159.5619 | 49.7 | 0.05 | 10.325 | 40.2642 | 26.875 | 0.05 | 4.125 | 0.425 | 31.25 | 5.1596 | 47.1873 | -3.1877 | 0.93727 | -3.2984 | -4.5484 | 4.1234
83 | 119.4113 | 27.8889 | 29.5071 | 50.4444 | 7.3444 | 1.4444 | 67.1222 | 79.2556 | 3.2222 | 3.4778 | 16 | 180.2222 | 62.2222 | 1.1556 | 0.94444 | 45.6222 | 46.8889 | 49.5556 | 2.6667 | 204.6667 | 0 | 0 | 25.1889 | 25.1333 | 550 | 49.6667 | #DIV/0! | #DIV/0! | 28.0111 | 46.9333 | 49.6 | 48.2222 | 1007.0364 | 4092.6056 | 5130.8922 | 49.6667 | 0.11111 | 10.2333 | 40.1761 | 26.6667 | 0.11111 | 4.8222 | 0.5 | 32.2222 | 5.1309 | 47.2066 | -3.2379 | 1.5844 | -3.2171 | -4.6616 | 4.1616
84 | 120.85 | 27 | 29.3873 | 50 | 7.3 | 1 | 67.5 | 79.7 | 3.3 | 3.4 | 16 | 180 | 62.6667 | 0.96667 | 0.73333 | 45.1667 | 46.7333 | 49.5333 | 2.8 | 204 | 0 | 0 | 25.0333 | 25 | 550 | 49.6 | #DIV/0! | #DIV/0! | 28.0333 | 46.8 | 49.6 | 48.1333 | 1007.0843 | 4092.5233 | 5391.8588 | 49.6 | 0.066667 | 10.2 | 40.2565 | 28 | 0.066667 | 4.8333 | 0.26667 | 33 | 5.3919 | 47.0363 | -2.9637 | 1.8697 | -3.4031 | -4.4031 | 4.1364
[42 empty] | 3.4702 | 0.38952 |  |  |  | -2.7515 | 0.71872 |  | -4.8165 | 4.427