## Calculations
Primary F.Rate = or > Secondary F.Rate
Primary
3.32 | kw | Boiler Output
13 | LPM | Flowrate
3.6605 | DegC | dT rise
49.5 | DegC | Flowtemp
45.8395 | DegC | Return Temp
6.5 | LPM | Prim Recirc
|  |  |  | Primary |  |  |  | Secondary
|  |  |  | KW | dT |  |  | KW | dT
Secondary |  |  |  | 3.32 | 3.6605 | DegC |  | 3.32 | 7.321 | DegC
3.32 | kw | Rad Output |  | LPM | DegC |  |  | LPM | DegC
6.5 | LPM | Flowrate |  | 13 | 49.5 |  |  | 6.5 | 49.5
42.179 | DegC | Returntemp |  |  |  | Recirc
7.321 | DegC | dT |  | LPM | DegC | 6.5 | LPM | LPM | DegC
|  |  |  | 13 | 45.8395 |  |  | 6.5 | 42.179
|  |  | Check (kw) | 3.32 |  |  |  | Check (kw) | 3.32 |  | T50 Stated Output is
|  |  | Mean Blr | 47.6697 | DegC |  | T50 | Output | 7.8312 | kw | 19.5 | kW
|  |  | Mean Rad | 45.8395 | DegC |  |  | Rad Output | 42.39% | 3.32 | kw
Secondary F.Rate = or > Primary F.Rate
Primary
3.496 | kw | Boiler Output |  | Primary |  |  |  | Secondary
13 | LPM | Flowrate |  | KW | dT |  |  | KW | dT
3.8546 | DegC | dT rise |  | 3.496 | 3.8546 | DegC |  | 3.496 | 2.5055 | DegC
49.5 | DegC | Flowtemp |  | LPM | DegC |  |  | LPM | DegC
45.6454 | DegC | Return Temp |  | 13 | 49.5 |  |  | 20 | 48.1509
Recirc
Secondary |  |  |  | LPM | DegC |  | 7 | LPM | DegC
3.496 | kw | Rad Output |  | 13 | 45.6454 |  |  | 20 | 45.6454
20 | LPM | Flowrate
48.1509 | DegC | Flowtemp | Check (kw) | 3.496 |  |  |  | Check (kw) | 3.496 |  | T50 Stated Output is
45.6454 | DegC | Returntemp | Mean Blr | 47.5727 | DegC |  | T50 | Output | 7.827 | kw | 19.5 | kW
2.5055 | DegC | Rad dT | Mean Rad | 46.8982 | DegC |  |  | Rad Output | 44.67% | 3.496 | kw
7 | LPM | Sec. Recirc